## Complete Building Method (hidden)
2013 NACM | People | Occupancy Vent Factor | Sensible heat | Latent heat | Receptacle | Hot water | Lighting | Min. Vent per Area | Ventilation | Cooling UMLH Limit | Heating UMLH Limit | Gas Appl Load | Refrig Load | Schedule
| # per 1000 ft² |  | Btu/h per person | Btu/h per person | Load W/ft² | Gal/h per person | W/ft² | CFM/ft² | CFM/ft² | Hrs | Hrs | Btu/h-ft2 | W/ft2
Auditorium Building | 143 | 1 | 245 | 105 | 1 | 0.09 | 1.5 | 0.15 | 1.07 | 150 | 150 | 0 | 0 | Assembly
Classroom Building | 40 | 0.5 | 246 | 171 | 1 | 0.162 | 1.1 | 0.15 | 0.32 | 150 | 150 | 0 | 0 | School
Commercial and Industrial Storage Building | 5 | 0.5 | 268 | 403 | 0.43 | 0.162 | 0.6 | 0.15 | 0.15 | 150 | 150 | 0 | 0.28 | Warehouse
Convention Center Building | 136 | 0.5 | 245 | 112 | 0.96 | 0.086 | 1.2 | 0.15 | 1.02 | 150 | 150 | 0.04 | 0.03 | Assembly
Data Center Buildings (Note 9) | 5 | 0.5 | 268 | 403 | note 9 | 0.162 | 0.8 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | Data
Financial Institution Building | 10 | 0.5 | 250 | 250 | 1.5 | 0.18 | 1.1 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | Office
General Commercia' or Industrial Work Building | 7 | 0.5 | 375 | 625 | 1 | 0.18 | 1 | 0.15 | 0.15 | 150 | 150 | 0 | 0.28 | Manufacturing
Grocery Store Buildings | 29 | 0.5 | 252 | 225 | 0.91 | 0.17 | 1.5 | 0.15 | 0.22 | 150 | 150 | 0.03 | 0.14 | Retail
Library Building | 10 | 0.5 | 250 | 250 | 1.5 | 0.18 | 1.3 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | Office
Medical Building/Clinic Building | 10 | 0.5 | 250 | 213 | 1.18 | 0.165 | 1.1 | 0.15 | 0.15 | 150 | 150 | 0.33 | 1.12 | Health
Office Building | 10 | 0.5 | 250 | 206 | 1.34 | 0.159 | 0.8 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | Office
Parking Garage Building | 10 | 0.5 | 250 | 200 | 0 | 0 | 0.2 | 0.15 | 0.15 | 150 | 150 | 0 | 0 | Parking
Religious Facility Building | 136 | 0.5 | 245 | 112 | 0.96 | 0.086 | 1.6 | 0.15 | 1.03 | 150 | 150 | 0.04 | 0 | Assembly
Restaurant Building | 45 | 0.5 | 274 | 334 | 0.79 | 0.549 | 1.2 | 0.15 | 0.38 | 150 | 150 | 5.14 | 0.06 | Restaurant
School Building | 40 | 0.5 | 246 | 171 | 1 | 0.162 | 1 | 0.15 | 0.32 | 150 | 150 | 0.04 | 0.03 | School
Theater Building | 130 | 1 | 268 | 403 | 0.54 | 0.09 | 1.3 | 0.15 | 0.98 | 150 | 150 | 0.04 | 0 | Assembly
All Other Buildings | 10 | 0.5 | 250 | 200 | 1 | 0.18 | 0.6 | 0.15 | 0.15 | 150 | 150 | 0.04 | 0.03 | Office
Note 9 - Receptacle Load shall be specified by the user.

## 2022 Stds Ltg Table (hidden)
| Primary Function Area | Allowed Lighting Power Density (W/ft2) | Additional Lighting Power (Note 1) | [6 empty] | 2019 Values
|  |  | Qualified Lighting Systems | Additional Allowance (W/ft2, unless noted otherwise) | Qualified Lighting Systems | Additional Allowance (W/ft2, unless noted otherwise) | Qualified Lighting Systems | Additional Allowance (W/ft2, unless noted otherwise)
| Aging Eye/Low-vision (Corridor Area) (Note 11) | 0.7 | Decorative/Display | 0.3 | None |  | None |  |  | 0.8 | Decorative (Note 4) | 0.15
| Aging Eye/Low-vision (Dining) (Note 11) | 0.8 | Decorative/Display | 0.3 | TunableWhiteOrDimToWarm (Note 10) | 0.1 | None |  |  | 0.8 | Ornamental | 0.3
| Aging Eye/Low-vision (Lobby, Main Entry) (Note 11) | 0.85 | Decorative/Display | 0.3 | TransitionLightingOffAtNight (Note 12) | 0.95 | TunableWhiteOrDimToWarm (Note 10) | 0.1 |  | 0.85 | Ornamental | 0.3 | Transition Lighitng OFF at night (Note 12) | 0.95
| Aging Eye/Low-vision (Lounge/Waiting Area) (Note 11) | 0.8 | Decorative/Display | 0.3 | TunableWhiteOrDimToWarm (Note 10) | 0.1 | None |  |  | 0.75 | Ornamental | 0.3
| Aging Eye/Low-vision (Multipurpose Room) (Note 11) | 0.85 | Decorative/Display | 0.3 | TunableWhiteOrDimToWarm (Note 10) | 0.1 | None |  |  | 0.95 | Ornamental | 0.3
| Aging Eye/Low-vision (Religious Worship Area) (Note 11) | 1 | Decorative/Display | 0.3 | TunableWhiteOrDimToWarm (Note 10) | 0.1 | None |  |  | 1 | Ornamental | 0.3
| Aging Eye/Low-vision (Restroom) (Note 11) | 1 | Decorative/Display | 0.2 | None |  | None |  |  | 0.8 | Accent, display and feature (Note 3) | 0.2
| Aging Eye/Low-vision (Stairwell) (Note 11) | 0.8 | Decorative/Display | 0.3 | None |  | None |  |  | 0.8
| Audience Seating Area | 0.5 | Decorative/Display | 0.25 | None |  | None |  |  | 0.6 | Ornamental | 0.3
| Auditorium Area | 0.7 | Decorative/Display | 0.45 | None |  | None |  |  | 0.7 | Ornamental | 0.3 | Accent, display and feature (Note 3) | 0.2
| Auto Repair / Maintenance Area | 0.55 | DetailedTaskWork (Note 7) | 0.2 | None |  | None |  |  | 0.55 | Detailed Task Work (Note 7) | 0.2
| Barber, Beauty Salon, Spa Area | 0.7 | DetailedTaskWork (Note 7) | 0.3 | Decorative/Display | 0.25 | None |  |  | 0.8 | Detailed Task Work (Note 7) | 0.2 | Ornamental | 0.3
| Civic Meeting Place Area | 0.9 | Decorative/Display | 0.25 | None |  | None |  |  | 1 | Ornamental | 0.3
| Classroom, Lecture, Training, Vocational Areas | 0.6 | WhiteOrChalkBoard (W/ft) (Note 1) | 7 | None |  | None |  |  | 0.7 | White or Chalk Board (W/ft) (Note 1) | 4.5
| Concourse and Atria Area | 0.6 | Decorative/Display | 0.25 | None |  | None |  |  | 0.9 | Ornamental | 0.3
| Convention, Conference, Multipurpose and Meeting Area | 0.75 | Decorative/Display | 0.25 | None |  | None |  |  | 0.85 | Ornamental | 0.3
| Copy Room | 0.5 | None |  | None |  | None |  |  | 0.5
| Corridor Area | 0.4 | Decorative/Display | 0.25 | None |  | None |  |  | 0.6
| Dining Area (Bar/Lounge and Fine Dining) | 0.45 | Decorative/Display | 0.35 | None |  | None |  |  | 0.55 | Ornamental | 0.3
| Dining Area (Cafeteria/Fast Food) | 0.45 | Decorative/Display | 0.25 | None |  | None |  |  | 0.4 | Ornamental | 0.3
| Dining Area (Family and Leisure) | 0.4 | Decorative/Display | 0.25 | None |  | None |  |  | 0.5 | Ornamental | 0.3
| Electrical, Mechanical, Telephone Rooms | 0.4 | DetailedTaskWork (Note 7) | 0.2 | None |  | None |  |  | 0.4 | Detailed Task Work (Note 7) | 0.2
| Exercise/Fitness Center and Gymnasium Areas | 0.5 | None |  | None |  | None |  |  | 0.5
| Financial Transaction Area | 0.7 | Decorative/Display | 0.25 | None |  | None |  |  | 0.8 | Ornamental | 0.3
| Healthcare Facility and Hospitals (Exam/Treatment Room) | 1.15 | None |  | None |  | None |  |  | 1.15
| Healthcare Facility and Hospitals (Imaging Room) | 0.6 | Decorative/Display | 0.2 | TunableWhiteOrDimToWarm (Note 10) | 0.1 | None |  |  | 1
| Healthcare Facility and Hospitals (Medical Supply Room) | 0.55 | None |  | None |  | None |  |  | 0.55
| Healthcare Facility and Hospitals (Nursery) | 0.8 | TunableWhiteOrDimToWarm (Note 10) | 0.1 | None |  | None |  |  | 0.95 | Tunable while or dim-to-warm (Note 10) | 0.1
| Healthcare Facility and Hospitals (Nurse's Station) | 0.85 | TunableWhiteOrDimToWarm (Note 10) | 0.1 | DetailedTaskWork (Note 7) | 0.2 | None |  |  | 0.75 | Tunable while or dim-to-warm (Note 10) | 0.1
| Healthcare Facility and Hospitals (Operating Room) | 1.9 | None |  | None |  | None |  |  | 1.9
| Healthcare Facility and Hospitals (Patient Room) | 0.7 | Decorative/Display | 0.15 | TunableWhiteOrDimToWarm (Note 10) | 0.1 | None |  |  | 0.55 | Decorative | 0.15 | Tunable while or dim-to-warm (Note 10) | 0.1
| Healthcare Facility and Hospitals (Physical Therapy Room) | 0.75 | TunableWhiteOrDimToWarm (Note 10) | 0.1 | None |  | None |  |  | 0.85 | Tunable while or dim-to-warm (Note 10) | 0.1
| Healthcare Facility and Hospitals (Recovery Room) | 0.9 | TunableWhiteOrDimToWarm (Note 10) | 0.1 | None |  | None |  |  | 0.9 | Tunable while or dim-to-warm (Note 10) | 0.1
| Hotel Function Area | 0.85 | Decorative/Display | 0.25 | None |  | None |  |  | 0.85 | Ornamental | 0.3
| Kitchen/Food Preparation Area | 0.95 | None |  | None |  | None |  |  | 0.95
| Laboratory, Scientific | 0.9 | SpecializedTaskWork (Note 8) | 0.35 | None |  | None |  |  | 1 | Specialized Task Work (Note 8) | 0.35
| Laundry Area | 0.45 | None |  | None |  | None |  |  | 0.45
| Library (Reading Area) | 0.8 | Decorative/Display | 0.25 | None |  | None |  |  | 0.8 | Ornamental | 0.3
| Library (Stacks Area) | 1 | None |  | None |  | None |  |  | 1.1
| Lobby, Main Entry | 0.7 | Decorative/Display | 0.25 | None |  | None |  |  | 0.85 | Ornamental | 0.3
| Locker Room | 0.45 | None |  | None |  | None |  |  | 0.45
| Lounge, Breakroom, or Waiting Area | 0.55 | Decorative/Display | 0.25 | None |  | None |  |  | 0.65 | Ornamental | 0.3
| Manufacturing, Commercial & Industrial Work Area (Low Bay) | 0.6 | DetailedTaskWork (Note 7) | 0.2 | None |  | None |  |  | 0.6 | Detailed Task Work (Note 7) | 0.2
| Manufacturing, Commercial & Industrial Work Area (High Bay) | 0.65 | DetailedTaskWork (Note 7) | 0.2 | None |  | None |  |  | 0.65 | Detailed Task Work (Note 7) | 0.2
| Manufacturing, Commercial & Industrial Work Area (Precision) | 0.85 | PrecisionWork (Note 9) | 0.7 | None |  | None |  |  | 0.85 | Precision Work (Note 9) | 0.7
| Museum Area (Exhibition/Display) | 0.6 | Decorative/Display | 0.45 | None |  | None |  |  | 0.6 | Accent, display and feature (Note 3) | 0.5
| Museum Area (Restoration Room) | 0.7 | DetailedTaskWork (Note 7) | 0.35 | None |  | None |  |  | 0.75 | Detailed Task Work (Note 7) | 0.2
| Office Area (>250 square feet) | 0.6 | Decorative/Display&PortableLightingForOffice (Note 6) | 0.2 | None |  | None |  |  | 0.65 | Portable lighting for office areas (Note 6) | 0.2
| Office Area (<250 square feet) | 0.65 | Decorative/Display&PortableLightingForOffice (Note 6) | 0.2 | None |  | None |  |  | 0.7 | Portable lighting for office areas (Note 6) | 0.2
| Parking Garage Area (Parking Zone and Ramps) | 0.1 | FirstATM/TicketMachine (W) | 100 | AdditionalATM/TicketMachine (50 W each) | 50 | None |  |  | 0.1 | First ATM (W) | 100 | Additional ATM (50 W each) | 50
| Parking Garage Area (Daylight Adaptation Zones) (Note 2) | 1 | None |  | None |  | None |  |  | 0.5
| Pharmacy Area | 1 | SpecializedTaskWork (Note 8) | 0.35 | None |  | None |  |  | 1.1 | Specialized Task Work (Note 8) | 0.35
| Retail Sales Area (Grocery Sales) | 1 | Decorative/Display | 0.35 | None |  | None |  |  | 1.05 | Accent, display and feature (Note 3) | 0.2 | Decorative | 0.15
| Retail Sales Area (Retail Merchandise Sales) | 0.95 | Decorative/Display | 0.35 | None |  | None |  |  | 1 | Accent, display and feature (Note 3) | 0.2 | Decorative | 0.15
| Retail Sales Area (Fitting Room) | 0.6 | ExternalIlluminatedMirror (Note5) | 40 | InternalIlluminatedMirror (Note 5) | 120 | None |  |  | 0.6 | External Illuminated Mirror (Note5) | 40 | Internal Illuminated Mirror (Note 5) | 120
| Religious Worship Area | 0.95 | Decorative/Display | 0.25 | None |  | None |  |  | 0.95 | Ornamental | 0.3
| Restrooms | 0.65 | Decorative/Display | 0.35 | None |  | None |  |  | 0.65 | Accent, display and feature (Note 3) | 0.2 | Decorative | 0.15
| Stairwell | 0.6 | Decorative/Display | 0.35 | None |  | None |  |  | 0.5 | Accent, display and feature (Note 3) | 0.2 | Decorative (Note 4) | 0.15
| Storage, Commercial/Industrial (Warehouse) | 0.4 | None |  | None |  | None |  |  | 0.45
| Storage, Commercial/Industrial (Shipping & Handling) | 0.6 | None |  | None |  | None |  |  | 0.6 |  |  |  |  | Original Designations:
| Sports Arena - Playing Area (> 5,000 Spectators) | 2.25 | None |  | None |  | None |  |  | 2.25 |  |  |  |  | Sports Arena - Playing Area (Class I Facility)
| Sports Arena - Playing Area (2,000 - 5,000 Spectators) | 1.45 | None |  | None |  | None |  |  | 1.45 |  |  |  |  | Sports Arena - Playing Area (Class II Facility)
| Sports Arena - Playing Area (< 2,000 Spectators) | 1.1 | None |  | None |  | None |  |  | 1.1 |  |  |  |  | Sports Arena - Playing Area (Class III Facility)
| Sports Arena - Playing Area (Recreational) | 0.75 | None |  | None |  | None |  |  | 0.75 |  |  |  |  | Sports Arena - Playing Area (Class IV Facility)
| Theater Area (Motion Picture) | 0.5 | Decorative/Display | 0.25 | None |  | None |  |  | 0.6 | Ornamental | 0.3
| Theater Area (Performance) | 0.8 | Decorative/Display | 0.25 | None |  | None |  |  | 1 | Ornamental | 0.3
| Transportation Function (Baggage Area) | 0.4 | None |  | None |  | None |  |  | 0.4
| Transportation Function (Ticketing Area) | 0.45 | Decorative/Display | 0.2 | None |  | None |  |  | 0.45 | Accent, display and feature (Note 3) | 0.2
| Videoconferencing Studio | 0.9 | Videoconferencing (Note 14) | 1 | None |  | None |  |  | 0.9 | Videoconferencing | 1
| All other | 0.4 | None |  | None |  | None |  |  | 0.4 |  |  |  |  | why listed below as not called out and set to 0.85?
vvv - Additional Space Types not specifically called out - vvv
| High-Rise Residential Living Spaces | na | None |  | None |  | None |  | Handled in Rules
| Hotel/Motel Guest Room | na | None |  | None |  | None |  | Handled in Rules
| Kitchenette or Residential Kitchen | 0.95 | None |  | None |  | None |  | Same as Kitchen/Food Preparation Area
| Unleased Tenant Area | 0.6 | None |  | None |  | None |  | Same as Open Office
| Unoccupied-Exclude from Gross Floor Area | 0 | None |  | None |  | None
| Unoccupied-Include in Gross Floor Area | 0 | None |  | None |  | None
| All other | 0.75 | None |  | None |  | None |  | Same as Open Office
| Storage, Commercial/Industrial (Refrigerated) | 0.4 | None |  | None |  | None |  | Same as Storage, Commercial/Industrial (Warehouse)
| Computer Room | 0.5 | None |  | None |  | None |  | Same as Copy Room
| Storage, General | 0.4 | None |  | None |  | None |  | Same as Storage, Commercial/Industrial (Warehouse)
vvv - Multifamily only - vvv
| Conference, Multipurpose and Meeting Area | 0.75 | Decorative/Display | 0.3 | None |  | None
| Storage | 0.45 | None |  | None |  | None
| Health Care / Assisted Living (Nurse's Station) | 0.75 | TunableWhiteOrDimToWarm (Note 10) | 0.1 | None |  | None
| Health Care / Assisted Living (Physical Therapy Room) | 0.85 | TunableWhiteOrDimToWarm (Note 10) | 0.1 | None |  | None
Notes:
1. White board or chalk board. - Directional Llighting shall be dedicated to thea white board or chalk board.
2. Daylight Adaptation Zones shall be no longer than 66 feet from the entrance to the parking garage.
3. Accent, display and feature lighting - luminaires shall be adjustable or directional.
4. Decorative lighting - primary function shall be decorative and to provide general lighting.
5. Illuminated mirrors. Lighting shall be dedicated to the mirror.
6. Portable lighting in office areas includes under shelf or furniture-mounted supplemental task lighting.
7. Detailed task work - Lighting provides high level of visual acuity required for activities with close attention to small elements and/or
extreme close up work.
8. Specialized task work - Lighting provides for small-scale, cognitive or fast performance visual tasks; lighting required for operating
specialized equipment associated with pharmaceutical/laboratorial activities.
9. Precision specialized work - Lighting for work performed within a commercial or industrial environment that entails working with low
contrast, finely detailed, or fast moving objects.
10. Tunable white or dim-to-warm luminaires as specified in Section 140.6(a)4B.
11. Aging Eye/Low-vision areas can be documented as being designed to comply with the light levels in ANSI/IES RP-28 and are or will be
licensed by local or state authorities for either senior long-term care, adult day care, senior support, and/or people with special visual needs.
12. Transition lighting OFF at night. Lighting power controlled by astronomical time clock or other control to shut off lighting at night.
Additional LPD only applies to area within 30 feet of an exit. Not applicable to lighting in daylit zones.
13. Class I Facility is used for competition play for 5000 or more spectators. Class II Facility is used for competition play for up to 5000
spectators. Class III Facility is used for competition play for up to 2000 spectators. Class IV Facility is normally used for recreational play and
there is limited or no provision for spectators.
14. The additional videoconferencing lighting power shall be allowed provided the videoconferencing studio meets all the requirements of
Section 140.6(c)2Gvii.
Note on B6: Jireh Peng: Was "Aging Eye/Low-vision (Main Entry Lobby)"
Note on B15: Jireh Peng: Was "Beauty Salon Area"
Note on B39: Jireh Peng: Was "Scientific Laboratory Area"
Note on B43: Jireh Peng: Was "Main Entry Lobby"
Note on B46: Jireh Peng: Was "General/Commercial & Industrial Work Area"
Note on B53: Jireh Peng: Combination of "Parking Garage Area (Parking Zone)" & "Parking Garage Area (Dedicated Ramp)"
Note on B62: Jireh Peng: Was "Commercial/Industrial Storage"

## 2025 Stds Ltg Table
| Primary Function Area | Allowed Lighting Power Density (W/ft2) | Additional Lighting Power Additional Allowance (Note 1)
|  |  | Enclosed Space Of Ceiling Hight > 10' (W/ft2) | Detailed Task Work (W/ft2) | Specialized Task Work (W/ft2) | Decorative/Display (W/ft2) | Precision Work (W/ft2) | White Or Chalk Board (W/ft) | Video Conferencing Studio Lighting (W/ft2) | ATM/Ticket Machine (W) | Decorative/Display And Portable Lighting Office (W/ft2) | External Iluminate Mirror (W/ft2) | Internal Iluminate Mirror (W/ft2) | Transition Lighting Off At Night (W/ft2) | Tunable White Or Dim To Warm (W/ft2) | Wall Display MH <= 10'6" (W/ft) | Wall Display MH 10'7" - 14' (W/ft) | Wall Display MH > 14' (W/ft) | Floor Display And Task MH <= 10'6" (W/ft2) | Floor Display And Task MH 10'7" - 14' (W/ft2) | Floor Display And Task MH > 14' (W/ft2) | Valuable Display Case (W/ft2)
| Aging Eye/Low-vision (Corridor Area) (Note 11) | 0.7 |  |  |  | 0.3
| Aging Eye/Low-vision (Dining) (Note 11) | 0.8 |  |  |  | 0.3 | [8 empty] | 0.1
| Aging Eye/Low-vision (Lobby, Main Entry) (Note 11) | 0.85 |  |  |  | 0.3 | [7 empty] | 0.95 | 0.1
| Aging Eye/Low-vision (Lounge/Waiting Area) (Note 11) | 0.8 |  |  |  | 0.3 | [8 empty] | 0.1
| Aging Eye/Low-vision (Multipurpose Room) (Note 11) | 0.85 |  |  |  | 0.3 | [8 empty] | 0.1
| Aging Eye/Low-vision (Religious Worship Area) (Note 11) | 1 |  |  |  | 0.3 | [8 empty] | 0.1
| Aging Eye/Low-vision (Restroom) (Note 11) | 1 |  |  |  | 0.2
| Aging Eye/Low-vision (Stairwell) (Note 11) | 0.8 |  |  |  | 0.3
| Audience Seating Area | 0.5 |  |  |  | 0.25
| Auditorium Area | 0.7 |  |  |  | 0.45
| Auto Repair / Maintenance Area | 0.55 |  | 0.2
| Barber, Beauty Salon, Spa Area | 0.7 |  | 0.3 |  | 0.25
| Civic Meeting Place Area | 0.9 |  |  |  | 0.25
| Classroom, Lecture, Training, Vocational Areas | 0.6 | [5 empty] | 7
| Concourse and Atria Area | 0.6 |  |  |  | 0.25
| Convention, Conference, Multipurpose and Meeting Area | 0.75 |  |  |  | 0.25 | [9 empty] | 2 | 2.35 | 2.66 | 0.3 | 0.35 | 0.4
| Copy Room | 0.5
| Corridor Area | 0.4 |  |  |  | 0.25
| Dining Area (Bar/Lounge and Fine Dining) | 0.45 | 0.25 |  |  | 0.35 | [9 empty] | 1.25 | 1.5 | 1.7 | 0.45 | 0.52 | 0.6
| Dining Area (Cafeteria/Fast Food) | 0.45 |  |  |  | 0.25
| Dining Area (Family and Leisure) | 0.4 |  |  |  | 0.25
| Electrical, Mechanical, Telephone Rooms | 0.4 |  | 0.2
| Exercise/Fitness Center and Gymnasium Areas | 0.5
| Financial Transaction Area | 0.7 |  |  |  | 0.25
| Healthcare Facility and Hospitals (Exam/Treatment Room) | 1.15
| Healthcare Facility and Hospitals (Imaging Room) | 0.6 |  |  |  | 0.2 | [8 empty] | 0.1
| Healthcare Facility and Hospitals (Medical Supply Room) | 0.55
| Healthcare Facility and Hospitals (Nursery) | 0.8 | [12 empty] | 0.1
| Healthcare Facility and Hospitals (Nurse's Station) | 0.85 |  | 0.2 | [10 empty] | 0.1
| Healthcare Facility and Hospitals (Operating Room) | 1.9
| Healthcare Facility and Hospitals (Patient Room) | 0.7 |  |  |  | 0.15 | [8 empty] | 0.1
| Healthcare Facility and Hospitals (Physical Therapy Room) | 0.75 | [12 empty] | 0.1
| Healthcare Facility and Hospitals (Recovery Room) | 0.9 | [12 empty] | 0.1
| Hotel Function Area | 0.85 |  |  |  | 0.25
| Kitchen/Food Preparation Area | 0.95
| Laboratory, Scientific | 0.9 |  |  | 0.35
| Laundry Area | 0.45
| Library (Reading Area) | 0.8 |  |  |  | 0.25
| Library (Stacks Area) | 1
| Lobby, Main Entry | 0.7 |  |  |  | 0.25 | [9 empty] | 3 | 3.5 | 4
| Locker Room | 0.45
| Lounge, Breakroom, or Waiting Area | 0.55 |  |  |  | 0.25
| Manufacturing, Commercial & Industrial Work Area (Low Bay) | 0.6 |  | 0.2
| Manufacturing, Commercial & Industrial Work Area (High Bay) | 0.65 |  | 0.2
| Manufacturing, Commercial & Industrial Work Area (Precision) | 0.85 |  |  |  |  | 0.7
| Museum Area (Exhibition/Display) | 0.6 |  |  |  | 0.45
| Museum Area (Restoration Room) | 0.7 |  | 0.35
| Office Area (>250 square feet) | 0.6 | [8 empty] | 0.2
| Office Area (<250 square feet) | 0.65 | [8 empty] | 0.2
| Parking Garage Area (Parking Zone and Ramps) | 0.1 | [7 empty] | First 100 + 50 for each additional one
| Parking Garage Area (Daylight Adaptation Zones) (Note 2) | 1
| Pharmacy Area | 1 |  |  | 0.35
| Retail Sales Area (Grocery Sales) | 1 | 0.1 |  |  | 0.35 | [9 empty] | 6.6 | 7.76 | 8.8 | 0.6 | 0.7 | 0.8
| Retail Sales Area (Retail Merchandise Sales) | 0.95 | 0.1 |  |  | 0.35 | [9 empty] | 9.5 | 11.2 | 12.7 | 0.45 | 0.52 | 0.6 | 0.5
| Retail Sales Area (Fitting Room) | 0.6 | [9 empty] | 40 | 120
| Religious Worship Area | 0.95 |  |  |  | 0.25
| Restrooms | 0.65 |  |  |  | 0.35
| Stairwell | 0.6 |  |  |  | 0.35
| Storage, Commercial/Industrial (Warehouse) | 0.4
| Storage, Commercial/Industrial (Shipping & Handling) | 0.6
| Sports Arena - Playing Area (> 5,000 Spectators) | 2.25
| Sports Arena - Playing Area (2,000 - 5,000 Spectators) | 1.45
| Sports Arena - Playing Area (< 2,000 Spectators) | 1.1
| Sports Arena - Playing Area (Recreational) | 0.75
| Theater Area (Motion Picture) | 0.5 |  |  |  | 0.25
| Theater Area (Performance) | 0.8 |  |  |  | 0.25
| Transportation Function (Baggage Area) | 0.4
| Transportation Function (Ticketing Area) | 0.45 |  |  |  | 0.2
| Videoconferencing Studio | 0.9 | [6 empty] | 1
| All other | 0.4
vvv - Additional Space Types not specifically called out - vvv
| High-Rise Residential Living Spaces | na | [20 empty] | Handled in Rules
| Hotel/Motel Guest Room | na | [20 empty] | Handled in Rules
| Kitchenette or Residential Kitchen | 0.95 | [20 empty] | Same as Kitchen/Food Preparation Area
| Unleased Tenant Area | 0.6 | [20 empty] | Same as Open Office
| Unoccupied-Exclude from Gross Floor Area | 0
| Unoccupied-Include in Gross Floor Area | 0
| All other | 0.4 | [20 empty] | Same as Open Office
| Storage, Commercial/Industrial (Refrigerated) | 0.4 | [20 empty] | Same as Storage, Commercial/Industrial (Warehouse)
| Computer Room | 0.5 | [20 empty] | Same as Copy Room
| Storage, General | 0.4 | [20 empty] | Same as Storage, Commercial/Industrial (Warehouse)
vvv - Multifamily only - vvv
| Conference, Multipurpose and Meeting Area | 0.75 |  |  |  | 0.25 | [9 empty] | 2 | 2.35 | 2.66 | 0.3 | 0.35 | 0.4
| Storage | 0.4
| Health Care / Assisted Living (Nurse's Station) | 0.85 | [12 empty] | 0.1
| Health Care / Assisted Living (Physical Therapy Room) | 0.75 | [12 empty] | 0.1
Notes:
1. White board or chalk board. - Directional Llighting shall be dedicated to thea white board or chalk board.
2. Daylight Adaptation Zones shall be no longer than 66 feet from the entrance to the parking garage.
3. MH denotes the luminaire mounting height of the qualified lighting systems.
4. Reserved
5. Illuminated mirrors. Lighting shall be dedicated to the mirror.
6. Portable lighting in office areas includes under shelf or furniture-mounted supplemental task lighting.
7. Detailed task work - Lighting provides high level of visual acuity required for activities with close attention to small elements and/or extreme close up work.
8. Specialized task work - Lighting provides for small-scale, cognitive or fast performance visual tasks; lighting required for operating specialized equipment associated with pharmaceutical/laboratorial activities.
9. Precision specialized work - Lighting for work performed within a commercial or industrial environment that entails working with low contrast, finely detailed, or fast moving objects.
10. Tunable white luminaires capable of color change greater than or equal to 2000K CCT, or dim-to-warm luminaires capable of color change greater than or equal to 500K CCT, connected to controls that allows color
11. Aging Eye/Low-vision areas can be documented as being designed to comply with the light levels in ANSI/IES RP-28 and are or will be licensed by local or state authorities for either senior long-term care, adult day care, senior support, and/or people with special visual needs.
12. Transition lighting OFF at night. Lighting power controlled by astronomical time clock or other control to shut off lighting at night. Additional LPD only applies to area within 30 feet of an exit. Not applicable to lighting in daylit zones.
13. Class I Facility is used for competition play for 5000 or more spectators. Class II Facility is used for competition play for up to 5000 spectators. Class III Facility is used for competition play for up to 2000 spectators. Class IV Facility is normally used for recreational play and there is limited or no provision for spectators.
14. The additional videoconferencing lighting power shall be allowed provided the videoconferencing studio meets all the requirements of Section 140.6(c)2Gvii.

## 2022 SpaceFuncData-Input
2022 NACM Space Type | Default Ventilation Space Function | People | Occupancy Vent Factor | Sensible heat | Latent heat | Receptacle | Hot water | Baseline WtrHtr Type | Lighting | Qualified Lighting Systems | Additional Allowance | Qualified Lighting Systems | Additional Allowance | Qualified Lighting Systems | Additional Allowance | Cooling UMLH Limit | Heating UMLH Limit | Gas Equipment Power | Refrig Load | Illuminance Setpoint for Daylighting |  | Primary Sidelit Daylighting Zone Setpoint Adjustment Factor | Secondary Sidelit Daylighting Zone Setpoint Adjustment Factor | Schedule | Eligible for Healthcare | Excluded From Predominant Calculation | FuncSchGrp is Editable | SpcFuncIdx (For Perf Reporting) | Notes
|  | # per 1000 ft² |  | per person | per person | Load W/ft² | Gal/h per person |  | W/ft² |  | W/ft², unless noted otherwise |  | W/ft², unless noted otherwise |  | W/ft², unless noted otherwise | Hrs | Hrs | Btu/h-ft2 | W/ft2 | Min (lux) | Max (lux)
Aging Eye/Low-vision (Corridor Area) (Note 11) | General - Corridors | 10 | 0.5 | 250 | 250 | 0 | 0 | Electric | 0.7 | Decorative/Display | 0.3 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 50 | 100 | 1.5 | 2 | Office | 1 | 1 | 0 | 302
Aging Eye/Low-vision (Dining) (Note 11) | Food Service - Cafeteria/fast-food dining | 66.6667 | 0.5 | 275 | 275 | 0.5 | 0.578 | Gas | 0.8 | Decorative/Display | 0.3 | TunableWhiteOrDimToWarm (Note 10) | 0.1 | None | 0 | 150 | 150 | 0 | 0.25 | 50 | 200 | 1.5 | 2 | Restaurant | 1 | 0 | 0 | 303
Aging Eye/Low-vision (Lobby, Main Entry) (Note 11) | Office - Main entry lobbies | 66.6667 | 0.5 | 250 | 250 | 0.5 | 0.09 | Electric | 0.85 | Decorative/Display | 0.3 | TransitionLightingOffAtNight (Note 12) | 0.95 | TunableWhiteOrDimToWarm (Note 10) | 0.1 | 150 | 150 | 0 | 0 | 50 | 200 | 1.5 | 2 | Assembly | 1 | 0 | 0 | 304
Aging Eye/Low-vision (Lounge/Waiting Area) (Note 11) | General - Break rooms | 66.6667 | 0.5 | 275 | 275 | 1 | 0.09 | Gas | 0.8 | Decorative/Display | 0.3 | TunableWhiteOrDimToWarm (Note 10) | 0.1 | None | 0 | 150 | 150 | 0 | 0 | 40 | 300 | 1.5 | 2 | Assembly | 1 | 0 | 0 | 305
Aging Eye/Low-vision (Multipurpose Room) (Note 11) | General - Conference/meeting | 66.6667 | 0.5 | 245 | 155 | 1 | 0.09 | Electric | 0.85 | Decorative/Display | 0.3 | TunableWhiteOrDimToWarm (Note 10) | 0.1 | None | 0 | 150 | 150 | 0 | 0 | 30 | 300 | 1.5 | 2 | Assembly | 1 | 0 | 0 | 306
Aging Eye/Low-vision (Religious Worship Area) (Note 11) | Assembly - Places of religious worship | 142.8571 | 0.5 | 245 | 105 | 0.5 | 0.09 | Electric | 1 | Decorative/Display | 0.3 | TunableWhiteOrDimToWarm (Note 10) | 0.1 | None | 0 | 150 | 150 | 0 | 0 | 200 | 1500 | 1.5 | 2 | Assembly | 1 | 0 | 0 | 307
Aging Eye/Low-vision (Restroom) (Note 11) | Exhaust - Toilets, public | 10 | 0.5 | 250 | 250 | 0 | 0 | Gas | 1 | Decorative/Display | 0.2 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 50 | 100 | 1.5 | 2 | Office | 1 | 1 | 0 | 308
Aging Eye/Low-vision (Stairwell) (Note 11) | General - Corridors | 10 | 0.5 | 250 | 250 | 0 | 0 | Electric | 0.8 | Decorative/Display | 0.3 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 50 | 100 | 1.5 | 2 | Office | 1 | 1 | 0 | 309
Audience Seating Area | Assembly - Auditorium seating area | 142.8571 | 0.5 | 245 | 105 | 1 | 0.09 | Electric | 0.5 | Decorative/Display | 0.25 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 50 | 1000 | 1.5 | 2 | Assembly | 1 | 0 | 0 | 310
Auditorium Area | Assembly - Auditorium seating area | 142.8571 | 0.5 | 245 | 105 | 1 | 0.09 | Electric | 0.7 | Decorative/Display | 0.45 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 50 | 1000 | 1.5 | 2 | Assembly | 1 | 0 | 0 | 311
Auto Repair / Maintenance Area | Exhaust - Auto repair rooms | 10 | 0.5 | 275 | 475 | 1 | 0.18 | Gas | 0.55 | DetailedTaskWork (Note 7) | 0.2 | None | 0 | None | 0 | 150 | 150 | 0.75064 | 0 | 200 | 1500 | 1.5 | 2 | Manufacturing | 1 | 0 | 0 | 312
Barber, Beauty Salon, Spa Area | Retail - Beauty and nail salons | 10 | 0.5 | 250 | 200 | 2 | 0.18 | Gas | 0.7 | DetailedTaskWork (Note 7) | 0.3 | Decorative/Display | 0.25 | None | 0 | 150 | 150 | 0 | 0 | 500 | 500 | 1.5 | 2 | Retail | 1 | 0 | 0 | 313
Civic Meeting Place Area | Assembly - Legislative chambers | 66.6667 | 0.5 | 250 | 200 | 1.5 | 0.18 | Electric | 0.9 | Decorative/Display | 0.25 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 30 | 300 | 1.5 | 2 | Assembly | 1 | 0 | 0 | 314
Classroom, Lecture, Training, Vocational Areas | Education - Classrooms (ages 9-18) | 50 | 0.5 | 245 | 155 | 1 | 0.18 | Gas | 0.6 | WhiteOrChalkBoard (W/ft) (Note 1) | 7 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 50 | 500 | 1.5 | 2 | School | 1 | 0 | 0 | 315
Computer Room | Misc - Computer (not printing) | 3 | 0.5 | 275 | 475 | 0 | 0.18 | Electric | 0.5 | None | 0 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 75 | 300 | 1 | 4 | Data | 0 | 1 | 0 | 316
Concourse and Atria Area | Retail - Mall common areas | 33.3333 | 0.5 | 250 | 250 | 0.5 | 0.18 | Electric | 0.6 | Decorative/Display | 0.25 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 100 | 300 | 1.5 | 2 | Retail | 1 | 1 | 0 | 317
Convention, Conference, Multipurpose and Meeting Area | General - Conference/meeting | 66.6667 | 0.5 | 245 | 155 | 1 | 0.09 | Electric | 0.75 | Decorative/Display | 0.25 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 30 | 300 | 1.5 | 2 | Assembly | 1 | 0 | 1 | 318
Copy Room | Exhaust - Copy, printing rooms | 10 | 0.5 | 250 | 250 | 1 | 0.18 | Electric | 0.5 | None | 0 | None | 0 | None | 0 | 8760 | 8760 | 0 | 0 | 75 | 500 | 1.5 | 2 | Office | 1 | 0 | 1 | 319
Corridor Area | General - Corridors | 10 | 0.5 | 250 | 250 | 0 | 0 | Electric | 0.4 | Decorative/Display | 0.25 | None | 0 | None | 0 | 8760 | 8760 | 0 | 0 | 50 | 100 | 1.5 | 2 | Office | 1 | 1 | 0 | 320
Dining Area (Bar/Lounge and Fine Dining) | Food Service - Restaurant dining rooms | 66.6667 | 0.5 | 275 | 275 | 0.5 | 0.578 | Gas | 0.45 | Decorative/Display | 0.35 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 50 | 200 | 1.5 | 2 | Restaurant | 1 | 0 | 0 | 321
Dining Area (Cafeteria/Fast Food) | Food Service - Cafeteria/fast-food dining | 66.6667 | 0.5 | 275 | 275 | 0.5 | 0.578 | Gas | 0.45 | Decorative/Display | 0.25 | None | 0 | None | 0 | 150 | 150 | 0 | 0.25 | 50 | 200 | 1.5 | 2 | Restaurant | 1 | 0 | 1 | 322
Dining Area (Family and Leisure) | Food Service - Cafeteria/fast-food dining | 66.6667 | 0.5 | 275 | 275 | 0.5 | 0.578 | Gas | 0.4 | Decorative/Display | 0.25 | None | 0 | None | 0 | 150 | 150 | 0 | 0.25 | 50 | 200 | 1.5 | 2 | Restaurant | 1 | 0 | 0 | 323
Electrical, Mechanical, Telephone Rooms | Misc - Telephone closets | 3 | 0.5 | 250 | 250 | 3 | 0.18 | Electric | 0.4 | DetailedTaskWork (Note 7) | 0.2 | None | 0 | None | 0 | 8760 | 8760 | 0 | 0 | 200 | 200 | 1 | 4 | Warehouse | 1 | 1 | 0 | 324
Exercise/Fitness Center and Gymnasium Areas | Sports/Entertainment - Gym, sports arena (play area) | 20 | 0.5 | 255 | 875 | 0.5 | 0.18 | Gas | 0.5 | None | 0 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 150 | 400 | 1.5 | 2 | Retail | 1 | 0 | 1 | 325
Financial Transaction Area | Misc - Banks or bank lobbies | 10 | 0.5 | 250 | 250 | 1.5 | 0.18 | Electric | 0.7 | Decorative/Display | 0.25 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 100 | 300 | 1.5 | 2 | Office | 1 | 0 | 0 | 326
Healthcare Facility and Hospitals (Exam/Treatment Room) | Misc - All others | 10 | 0.5 | 250 | 200 | 1.5 | 0.24 | Electric | 1.15 | None | 0 | None | 0 | None | 0 | 150 | 150 | 1.126 | 0 | 300 | 3000 | 1.5 | 2 | Health | 1 | 0 | 0 | 327
Healthcare Facility and Hospitals (Imaging Room) | Misc - All others | 10 | 0.5 | 250 | 200 | 1.5 | 0.24 | Gas | 0.6 | Decorative/Display | 0.2 | TunableWhiteOrDimToWarm (Note 10) | 0.1 | None | 0 | 150 | 150 | 0 | 0 | 75 | 500 | 1.5 | 2 | Health | 1 | 0 | 0 | 328
Healthcare Facility and Hospitals (Medical Supply Room) | Misc - All others | 10 | 0.5 | 250 | 200 | 1.5 | 0.24 | Gas | 0.55 | None | 0 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 50 | 300 | 1.5 | 2 | Health | 1 | 0 | 0 | 329
Healthcare Facility and Hospitals (Nursery) | Misc - All others | 10 | 0.5 | 250 | 200 | 1.5 | 0.24 | Gas | 0.8 | TunableWhiteOrDimToWarm (Note 10) | 0.1 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 20 | 200 | 1.5 | 2 | Health | 1 | 0 | 0 | 330
Healthcare Facility and Hospitals (Nurse's Station) | Misc - All others | 10 | 0.5 | 250 | 200 | 1.5 | 0.24 | Gas | 0.85 | TunableWhiteOrDimToWarm (Note 10) | 0.1 | DetailedTaskWork (Note 7) | 0.2 | None | 0 | 150 | 150 | 0 | 0 | 75 | 500 | 1.5 | 2 | Health | 1 | 0 | 0 | 331
Healthcare Facility and Hospitals (Operating Room) | Misc - All others | 10 | 0.5 | 250 | 200 | 1.5 | 0.24 | Gas | 1.9 | None | 0 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 300 | 3000 | 1.5 | 2 | Health | 1 | 0 | 0 | 332
Healthcare Facility and Hospitals (Patient Room) | Misc - All others | 10 | 0.5 | 250 | 200 | 1.5 | 0.24 | Gas | 0.7 | Decorative/Display | 0.15 | TunableWhiteOrDimToWarm (Note 10) | 0.1 | None | 0 | 150 | 150 | 0 | 0 | 20 | 200 | 1.5 | 2 | Health | 1 | 0 | 0 | 333
Healthcare Facility and Hospitals (Physical Therapy Room) | Misc - All others | 10 | 0.5 | 250 | 200 | 1.5 | 0.24 | Electric | 0.75 | TunableWhiteOrDimToWarm (Note 10) | 0.1 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 75 | 500 | 1.5 | 2 | Health | 1 | 0 | 0 | 334
Healthcare Facility and Hospitals (Recovery Room) | Misc - All others | 10 | 0.5 | 250 | 200 | 1.5 | 0.24 | Gas | 0.9 | TunableWhiteOrDimToWarm (Note 10) | 0.1 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 20 | 200 | 1.5 | 2 | Health | 1 | 0 | 0 | 335
High-Rise Residential Living Spaces | NA | 5 | 0.5 | 245 | 155 | 0.5 | RULE Spc:DwellingUnitXGalPerDay | Gas | na | None | 0 | None | 0 | None | 0 | 150 | 150 | 0.6824 | 0 | 20 | 200 | 1.5 | 2 | ResidentialLiving | 0 | 1 | 0 | 336
Hotel Function Area | Lodging - Multipurpose assembly | 142.8571 | 0.5 | 250 | 200 | 0.5 | 0.096 | Gas | 0.85 | Decorative/Display | 0.25 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 50 | 300 | 1.5 | 2 | Assembly | 0 | 0 | 0 | 337
Hotel/Motel Guest Room | Lodging - Bedroom/living room | 5 | 0.5 | 245 | 155 | 0.5 | 4.48 | Gas | na | None | 0 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 20 | 200 | 1.5 | 2 | ResidentialLiving | 0 | 0 | 0 | 338
Kitchen/Food Preparation Area | Food Service - Kitchen (cooking) | 5 | 0.5 | 275 | 475 | 1.5 | 0.578 | Gas | 0.95 | None | 0 | None | 0 | None | 0 | 150 | 150 | 17.5377 | 1.12 | 100 | 500 | 1.5 | 2 | Restaurant | 1 | 0 | 1 | 339
Kitchenette or Residential Kitchen | Exhaust - Kitchenettes | 5 | 0.5 | 275 | 475 | 1 | 0.36 | Gas | 0.95 | None | 0 | None | 0 | None | 0 | 150 | 150 | 3 | 0.5 | 100 | 500 | 1.5 | 2 | Office | 1 | 0 | 0 | 340
Laboratory, Scientific | Education - University/college laboratories | 10 | 0.5 | 250 | 200 | 2 | 0.18 | Gas | 0.9 | SpecializedTaskWork (Note 8) | 0.35 | None | 0 | None | 0 | 150 | 150 | 12.6926 | 0.28 | 500 | 1000 | 1.5 | 2 | Laboratory | 1 | 1 | 0 | 341
Laundry Area | Lodging - Laundry rooms, central | 10 | 0.5 | 250 | 250 | 3 | 0.578 | Gas | 0.45 | None | 0 | None | 0 | None | 0 | 8760 | 8760 | 0.75064 | 0 | 100 | 300 | 1.5 | 2 | ResidentialCommon | 1 | 0 | 1 | 342
Library (Reading Area) | Assembly - Libraries (reading rooms and stack areas) | 20 | 0.5 | 250 | 200 | 1.5 | 0.18 | Electric | 0.8 | Decorative/Display | 0.25 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 150 | 500 | 1.5 | 2 | Office | 1 | 0 | 0 | 343
Library (Stacks Area) | Assembly - Libraries (reading rooms and stack areas) | 10 | 0.5 | 250 | 200 | 1.5 | 0.18 | Electric | 1 | None | 0 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 200 | 300 | 1 | 4 | Office | 1 | 0 | 0 | 344
Lobby, Main Entry | Office - Main entry lobbies | 66.6667 | 0.5 | 250 | 250 | 0.5 | 0.09 | Electric | 0.7 | Decorative/Display | 0.25 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 50 | 200 | 1.5 | 2 | Assembly | 1 | 0 | 1 | 345
Locker Room | Exhaust - Locker rooms for athletic or industrial facilities | 20 | 0.5 | 255 | 475 | 0.5 | 0.578 | Gas | 0.45 | None | 0 | None | 0 | None | 0 | 8760 | 8760 | 0 | 0 | 20 | 200 | 1 | 4 | Assembly | 1 | 0 | 1 | 346
Lounge, Breakroom, or Waiting Area | General - Break rooms | 66.6667 | 0.5 | 275 | 275 | 1 | 0.09 | Gas | 0.55 | Decorative/Display | 0.25 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 40 | 300 | 1.5 | 2 | Assembly | 1 | 1 | 0 | 347
Manufacturing, Commercial & Industrial Work Area (Low Bay) | Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 10 | 0.5 | 275 | 475 | 1 | 0.18 | Gas | 0.6 | DetailedTaskWork (Note 7) | 0.2 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 300 | 1000 | 1.5 | 2 | Manufacturing | 1 | 0 | 0 | 348
Manufacturing, Commercial & Industrial Work Area (High Bay) | Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 10 | 0.5 | 275 | 475 | 1 | 0.18 | Gas | 0.65 | DetailedTaskWork (Note 7) | 0.2 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 300 | 1000 | 1.5 | 2 | Manufacturing | 1 | 0 | 0 | 349
Manufacturing, Commercial & Industrial Work Area (Precision) | Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 10 | 0.5 | 250 | 200 | 1 | 0.18 | Gas | 0.85 | PrecisionWork (Note 9) | 0.7 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 1000 | 3000 | 1.5 | 2 | Manufacturing | 1 | 0 | 0 | 350
Museum Area (Exhibition/Display) | Assembly - Museums/galleries | 66.6667 | 0.5 | 250 | 250 | 1.5 | 0.09 | Electric | 0.6 | Decorative/Display | 0.45 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 150 | 500 | 1.5 | 2 | Assembly | 1 | 0 | 0 | 351
Museum Area (Restoration Room) | Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 10 | 0.5 | 250 | 250 | 1.5 | 0.18 | Electric | 0.7 | DetailedTaskWork (Note 7) | 0.35 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 150 | 500 | 1.5 | 2 | Assembly | 1 | 0 | 0 | 352
Office Area (>250 square feet) | Office - Office space | 10 | 0.5 | 250 | 200 | 1.5 | 0.18 | Electric | 0.6 | Decorative/Display&PortableLightingForOffice (Note 6) | 0.2 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 75 | 500 | 1 | 4 | Office | 1 | 0 | 0 | 353
Office Area (<250 square feet) | Office - Office space | 10 | 0.5 | 250 | 200 | 1.5 | 0.18 | Electric | 0.65 | Decorative/Display&PortableLightingForOffice (Note 6) | 0.2 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 75 | 500 | 1.5 | 2 | Office | 1 | 0 | 0 | 354
Parking Garage Area (Parking Zone and Ramps) | Exhaust - Parking garages | 5 | 0.5 | 250 | 200 | 0 | 0 | Electric | 0.1 | FirstATM/TicketMachine (W) | 100 | AdditionalATM/TicketMachine (50 W each) | 50 | None | 0 | 8760 | 8760 | 0 | 0 | 10 | 40 | 1.5 | 2 | Parking | 1 | 1 | 0 | 355
Parking Garage Area (Daylight Adaptation Zones) (Note 2) | Exhaust - Parking garages | 5 | 0.5 | 250 | 200 | 0 | 0 | Electric | 1 | None | 0 | None | 0 | None | 0 | 8760 | 8760 | 0 | 0 | 10 | 40 | 1.5 | 2 | Parking | 1 | 1 | 0 | 356
Pharmacy Area | Misc - Pharmacy (preparation area) | 10 | 0.5 | 250 | 200 | 5 | 0.18 | Electric | 1 | SpecializedTaskWork (Note 8) | 0.35 | None | 0 | None | 0 | 150 | 150 | 0 | 1 | 100 | 1000 | 1.5 | 2 | Retail | 1 | 0 | 0 | 357
Retail Sales Area (Grocery Sales) | Retail - Supermarket | 16.6667 | 0.5 | 250 | 200 | 1 | 0.18 | Gas | 1 | Decorative/Display | 0.35 | None | 0 | None | 0 | 150 | 150 | 0 | 5 | 100 | 1000 | 1.5 | 2 | Retail | 1 | 0 | 0 | 358
Retail Sales Area (Retail Merchandise Sales) | Retail - Sales | 16.6667 | 0.5 | 250 | 200 | 1 | 0.18 | Electric | 0.95 | Decorative/Display | 0.35 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 100 | 1000 | 1.5 | 2 | Retail | 1 | 0 | 0 | 359
Retail Sales Area (Fitting Room) | Retail - Sales | 16.6667 | 0.5 | 250 | 200 | 1 | 0.18 | Electric | 0.6 | ExternalIlluminatedMirror (Note5) | 40 | InternalIlluminatedMirror (Note 5) | 120 | None | 0 | 150 | 150 | 0 | 0 | 100 | 1000 | 1.5 | 2 | Retail | 1 | 0 | 0 | 360
Religious Worship Area | Assembly - Places of religious worship | 142.8571 | 0.5 | 245 | 105 | 0.5 | 0.09 | Electric | 0.95 | Decorative/Display | 0.25 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 200 | 1500 | 1.5 | 2 | Assembly | 1 | 0 | 0 | 361
Restrooms | Exhaust - Toilets, public | 10 | 0.5 | 250 | 250 | 0 | 0 | Gas | 0.65 | Decorative/Display | 0.35 | None | 0 | None | 0 | 8760 | 8760 | 0 | 0 | 50 | 100 | 1.5 | 2 | Office | 1 | 1 | 0 | 362
Stairwell | General - Corridors | 10 | 0.5 | 250 | 250 | 0 | 0 | Electric | 0.6 | Decorative/Display | 0.35 | None | 0 | None | 0 | 8760 | 8760 | 0 | 0 | 50 | 100 | 1.5 | 2 | Office | 1 | 1 | 0 | 363
Storage, Commercial/Industrial (Warehouse) | Misc - Warehouses | 2 | 0.5 | 275 | 475 | 0.2 | 0.18 | Electric | 0.4 | None | 0 | None | 0 | None | 0 | 8760 | 8760 | 0 | 0 | 50 | 300 | 1.5 | 2 | Warehouse | 1 | 0 | 0 | 364
Storage, Commercial/Industrial (Refrigerated) | Misc - Freezer and refrigerated spaces (<50F) | 0 | 0.5 | 275 | 475 | 0.2 | 0.18 | Electric | 0.4 | None | 0 | None | 0 | None | 0 | 8760 | 8760 | 0 | 10 | 50 | 300 | 1.5 | 2 | Warehouse | 1 | 0 | 0 | 365
Storage, Commercial/Industrial (Shipping & Handling) | Misc - Shipping/receiving | 5 | 0.5 | 275 | 475 | 0.5 | 0.18 | Electric | 0.6 | None | 0 | None | 0 | None | 0 | 8760 | 8760 | 0 | 0 | 50 | 300 | 1.5 | 2 | Warehouse | 1 | 0 | 0 | 366
Storage, General | Misc - All others | 0 | 0.5 | 250 | 200 | 0.2 | 0 | Electric | 0.4 | None | 0 | None | 0 | None | 0 | 8760 | 8760 | 0 | 0 | 50 | 300 | 1.5 | 2 | Warehouse | 1 | 1 | 0 | 380
Sports Arena - Playing Area (> 5,000 Spectators) | Sports/Entertainment - Gym, sports arena (play area) | 80 | 0.5 | 255 | 875 | 0.5 | 0.18 | Gas | 2.25 | None | 0 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 150 | 400 | 1.5 | 2 | Retail | 0 | 0 | 0 | 367
Sports Arena - Playing Area (2,000 - 5,000 Spectators) | Sports/Entertainment - Gym, sports arena (play area) | 66.6667 | 0.5 | 255 | 875 | 0.5 | 0.18 | Gas | 1.45 | None | 0 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 150 | 400 | 1.5 | 2 | Retail | 0 | 0 | 0 | 368
Sports Arena - Playing Area (< 2,000 Spectators) | Sports/Entertainment - Gym, sports arena (play area) | 50 | 0.5 | 255 | 875 | 0.5 | 0.18 | Gas | 1.1 | None | 0 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 150 | 400 | 1.5 | 2 | Retail | 0 | 0 | 0 | 369
Sports Arena - Playing Area (Recreational) | Sports/Entertainment - Gym, sports arena (play area) | 20 | 0.5 | 255 | 875 | 0.2 | 0.9 | Gas | 0.75 | None | 0 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 150 | 400 | 1.5 | 2 | Retail | 1 | 0 | 0 | 370
Theater Area (Motion Picture) | Assembly - Auditorium seating area | 142.8571 | 0.5 | 245 | 105 | 0.5 | 0.09 | Electric | 0.5 | Decorative/Display | 0.25 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 2 | 50 | 1.5 | 2 | Assembly | 1 | 0 | 0 | 371
Theater Area (Performance) | Sports/Entertainment - Stages, studios | 142.8571 | 0.5 | 245 | 105 | 0.5 | 0.09 | Gas | 0.8 | Decorative/Display | 0.25 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 2 | 200 | 1.5 | 2 | Assembly | 1 | 0 | 1 | 372
Transportation Function (Baggage Area) | Misc - Transportation waiting | 33.3333 | 0.5 | 250 | 250 | 0.5 | 0.18 | Electric | 0.4 | None | 0 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 50 | 500 | 1.5 | 2 | Assembly | 0 | 0 | 0 | 373
Transportation Function (Ticketing Area) | Misc - Transportation waiting | 33.3333 | 0.5 | 250 | 250 | 0.5 | 0.18 | Electric | 0.45 | Decorative/Display | 0.2 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 50 | 500 | 1.5 | 2 | Assembly | 0 | 0 | 0 | 374
Unleased Tenant Area | Office - Office space | 10 | 0.5 | 250 | 200 | 1.5 | 0.18 | Electric | 0.6 | None | 0 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 75 | 500 | 1 | 4 | Office | 1 | 0 | 1 | 375
Unoccupied-Exclude from Gross Floor Area | NA | 0 | 0.5 | 250 | 250 | 0 | 0 | Gas | 0 | None | 0 | None | 0 | None | 0 | 8760 | 8760 | 0 | 0 | 0 | 0 | 0 | 0 | Unoccupied | 1 | 1 | 0 | 376
Unoccupied-Include in Gross Floor Area | NA | 0 | 0.5 | 250 | 250 | 0 | 0 | Gas | 0 | None | 0 | None | 0 | None | 0 | 8760 | 8760 | 0 | 0 | 0 | 0 | 0 | 0 | Unoccupied | 1 | 1 | 0 | 377
Videoconferencing Studio | General - Conference/meeting | 10 | 0.5 | 250 | 200 | 1.5 | 0.18 | Electric | 0.9 | Videoconferencing (Note 14) | 1 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 300 | 300 | 1.5 | 2 | Office | 1 | 0 | 0 | 378
All other | Misc - All others | 10 | 0.5 | 250 | 200 | 1 | 0.18 | Gas | 0.4 | None | 0 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 100 | 300 | 1.5 | 2 | Office | 1 | 0 | 1 | 301
Conference, Multipurpose and Meeting Area | General - Conference/meeting | 66.6667 | 0.5 | 245 | 155 | 1 | 0.09 | Electric | 0.75 | Decorative/Display | 0.3 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 30 | 300 | 1.5 | 2 | Assembly | 1 | 0 | 1 | 381
Storage | Misc - All others | 0 | 0.5 | 250 | 200 | 0.2 | 0 | Electric | 0.45 | None | 0 | None | 0 | None | 0 | 8760 | 8760 | 0 | 0 | 50 | 300 | 1.5 | 2 | Warehouse | 0 | 1 | 0 | 379
Health Care / Assisted Living (Nurse's Station) | Misc - All others | 10 | 0.5 | 250 | 200 | 1.5 | 0.24 | Gas | 0.75 | TunableWhiteOrDimToWarm (Note 10) | 0.1 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 75 | 500 | 1.5 | 2 | ResidentialCommon | 0 | 0 | 0 | 382
Health Care / Assisted Living (Physical Therapy Room) | Misc - All others | 10 | 0.5 | 250 | 200 | 1.5 | 0.24 | Electric | 0.85 | TunableWhiteOrDimToWarm (Note 10) | 0.1 | None | 0 | None | 0 | 150 | 150 | 0 | 0 | 75 | 500 | 1.5 | 2 | ResidentialCommon | 0 | 0 | 0 | 383

## 2025 SpaceFuncData-Input
[10 empty] | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22
2025 NACM Space Type | Default Ventilation Space Function | People | Occupancy Vent Factor | Sensible heat | Latent heat | Receptacle | Hot water | Baseline WtrHtr Type | Lighting | Additional Allowance For Enclosed Space Of Ceiling Hight > 10' (W/ft2) | Additional Allowance For Detailed Task Work (W/ft2) | Additional Allowance For Specialized Task Work (W/ft2) | Additional Allowance For Decorative/Display (W/ft2) | Additional Allowance For Precision Work (W/ft2) | Additional Allowance For White Or Chalk Board (W/ft) | Additional Allowance For Video Conferencing Studio Lighting (W/ft2) | Additional Allowance For ATM/Ticket Machine (W) | Additional Allowance For Decorative/Display And Portable Lighting Office (W/ft2) | Additional Allowance For External Iluminate Mirror (W/ft2) | Additional Allowance For Internal Iluminate Mirror (W/ft2) | Additional Allowance For Transition Lighting Off At Night (W/ft2) | Additional Allowance For Tunable White Or Dim To Warm (W/ft2) | Additional Allowance For Wall Display MH <= 10'6" (W/ft) | Additional Allowance For Wall Display MH 10'7" - 14' (W/ft) | Additional Allowance For Wall Display MH > 14' (W/ft) | Additional Allowance For Floor Display And Task MH <= 10'6" (W/ft2) | Additional Allowance For Floor Display And Task MH 10'7" - 14' (W/ft2) | Additional Allowance For Floor Display And Task MH > 14' (W/ft2) | Additional Allowance For Valuable Display Case (W/ft2) | Cooling UMLH Limit | Heating UMLH Limit | Gas Equipment Power | Refrig Load | Illuminance Setpoint for Daylighting |  | Primary Sidelit Daylighting Zone Setpoint Adjustment Factor | Secondary Sidelit Daylighting Zone Setpoint Adjustment Factor | Schedule | Eligible for Healthcare | Excluded From Predominant Calculation | FuncSchGrp is Editable | SpcFuncIdx (For Perf Reporting) | Notes
|  | # per 1000 ft² |  | per person | per person | Load W/ft² | Gal/h per person |  | W/ft² | 4: W/ft², unless noted otherwise; 6: W/ft², unless noted otherwise; 8: W/ft², unless noted otherwise; 9: W/ft² | Hrs | Hrs | Btu/h-ft2 | W/ft2 | Min (lux) | Max (lux)
Aging Eye/Low-vision (Corridor Area) (Note 11) | General - Corridors | 10 | 0.5 | 250 | 250 | 0 | 0 | Electric | 0.7 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 50 | 100 | 1.5 | 2 | Office | 1 | 1 | 0 | 302
Aging Eye/Low-vision (Dining) (Note 11) | Food Service - Cafeteria/fast-food dining | 66.6667 | 0.5 | 275 | 275 | 0.5 | 0.578 | Gas | 0.8 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0.25 | 50 | 200 | 1.5 | 2 | Restaurant | 1 | 0 | 0 | 303
Aging Eye/Low-vision (Lobby, Main Entry) (Note 11) | Office - Main entry lobbies | 66.6667 | 0.5 | 250 | 250 | 0.5 | 0.09 | Electric | 0.85 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 50 | 200 | 1.5 | 2 | Assembly | 1 | 0 | 0 | 304
Aging Eye/Low-vision (Lounge/Waiting Area) (Note 11) | General - Break rooms | 66.6667 | 0.5 | 275 | 275 | 1 | 0.09 | Gas | 0.8 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 40 | 300 | 1.5 | 2 | Assembly | 1 | 0 | 0 | 305
Aging Eye/Low-vision (Multipurpose Room) (Note 11) | General - Conference/meeting | 66.6667 | 0.5 | 245 | 155 | 1 | 0.09 | Electric | 0.85 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 30 | 300 | 1.5 | 2 | Assembly | 1 | 0 | 0 | 306
Aging Eye/Low-vision (Religious Worship Area) (Note 11) | Assembly - Places of religious worship | 142.8571 | 0.5 | 245 | 105 | 0.5 | 0.09 | Electric | 1 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 200 | 1500 | 1.5 | 2 | Assembly | 1 | 0 | 0 | 307
Aging Eye/Low-vision (Restroom) (Note 11) | Exhaust - Toilets, public | 10 | 0.5 | 250 | 250 | 0 | 0 | Gas | 1 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 50 | 100 | 1.5 | 2 | Office | 1 | 1 | 0 | 308
Aging Eye/Low-vision (Stairwell) (Note 11) | General - Corridors | 10 | 0.5 | 250 | 250 | 0 | 0 | Electric | 0.8 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 50 | 100 | 1.5 | 2 | Office | 1 | 1 | 0 | 309
Audience Seating Area | Assembly - Auditorium seating area | 142.8571 | 0.5 | 245 | 105 | 1 | 0.09 | Electric | 0.5 | 0 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 50 | 1000 | 1.5 | 2 | Assembly | 1 | 0 | 0 | 310
Auditorium Area | Assembly - Auditorium seating area | 142.8571 | 0.5 | 245 | 105 | 1 | 0.09 | Electric | 0.7 | 0 | 0 | 0 | 0.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 50 | 1000 | 1.5 | 2 | Assembly | 1 | 0 | 0 | 311
Auto Repair / Maintenance Area | Exhaust - Auto repair rooms | 10 | 0.5 | 275 | 475 | 1 | 0.18 | Gas | 0.55 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0.75064 | 0 | 200 | 1500 | 1.5 | 2 | Manufacturing | 1 | 0 | 0 | 312
Barber, Beauty Salon, Spa Area | Retail - Beauty and nail salons | 10 | 0.5 | 250 | 200 | 2 | 0.18 | Gas | 0.7 | 0 | 0.3 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 500 | 500 | 1.5 | 2 | Retail | 1 | 0 | 0 | 313
Civic Meeting Place Area | Assembly - Legislative chambers | 66.6667 | 0.5 | 250 | 200 | 1.5 | 0.18 | Electric | 0.9 | 0 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 30 | 300 | 1.5 | 2 | Assembly | 1 | 0 | 0 | 314
Classroom, Lecture, Training, Vocational Areas | Education - Classrooms (ages 9-18) | 50 | 0.5 | 245 | 155 | 1 | 0.18 | Gas | 0.6 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 50 | 500 | 1.5 | 2 | School | 1 | 0 | 0 | 315
Computer Room | Misc - Computer (not printing) | 3 | 0.5 | 275 | 475 | 0 | 0.18 | Electric | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 75 | 300 | 1 | 4 | Data | 0 | 1 | 0 | 316
Concourse and Atria Area | Retail - Mall common areas | 33.3333 | 0.5 | 250 | 250 | 0.5 | 0.18 | Electric | 0.6 | 0 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 100 | 300 | 1.5 | 2 | Retail | 1 | 1 | 0 | 317
Convention, Conference, Multipurpose and Meeting Area | General - Conference/meeting | 66.6667 | 0.5 | 245 | 155 | 1 | 0.09 | Electric | 0.75 | 0 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2.35 | 2.66 | 0.3 | 0.35 | 0.4 | 0 | 150 | 150 | 0 | 0 | 30 | 300 | 1.5 | 2 | Assembly | 1 | 0 | 1 | 318
Copy Room | Exhaust - Copy, printing rooms | 10 | 0.5 | 250 | 250 | 1 | 0.18 | Electric | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8760 | 8760 | 0 | 0 | 75 | 500 | 1.5 | 2 | Office | 1 | 0 | 1 | 319
Corridor Area | General - Corridors | 10 | 0.5 | 250 | 250 | 0 | 0 | Electric | 0.4 | 0 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8760 | 8760 | 0 | 0 | 50 | 100 | 1.5 | 2 | Office | 1 | 1 | 0 | 320
Dining Area (Bar/Lounge and Fine Dining) | Food Service - Restaurant dining rooms | 66.6667 | 0.5 | 275 | 275 | 0.5 | 0.578 | Gas | 0.45 | 0.25 | 0 | 0 | 0.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.25 | 1.5 | 1.7 | 0.45 | 0.52 | 0.6 | 0 | 150 | 150 | 0 | 0 | 50 | 200 | 1.5 | 2 | Restaurant | 1 | 0 | 0 | 321
Dining Area (Cafeteria/Fast Food) | Food Service - Cafeteria/fast-food dining | 66.6667 | 0.5 | 275 | 275 | 0.5 | 0.578 | Gas | 0.45 | 0 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0.25 | 50 | 200 | 1.5 | 2 | Restaurant | 1 | 0 | 1 | 322
Dining Area (Family and Leisure) | Food Service - Cafeteria/fast-food dining | 66.6667 | 0.5 | 275 | 275 | 0.5 | 0.578 | Gas | 0.4 | 0 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0.25 | 50 | 200 | 1.5 | 2 | Restaurant | 1 | 0 | 0 | 323
Electrical, Mechanical, Telephone Rooms | Misc - Telephone closets | 3 | 0.5 | 250 | 250 | 3 | 0.18 | Electric | 0.4 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8760 | 8760 | 0 | 0 | 200 | 200 | 1 | 4 | Warehouse | 1 | 1 | 0 | 324
Exercise/Fitness Center and Gymnasium Areas | Sports/Entertainment - Gym, sports arena (play area) | 20 | 0.5 | 255 | 875 | 0.5 | 0.18 | Gas | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 150 | 400 | 1.5 | 2 | Retail | 1 | 0 | 1 | 325
Financial Transaction Area | Misc - Banks or bank lobbies | 10 | 0.5 | 250 | 250 | 1.5 | 0.18 | Electric | 0.7 | 0 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 100 | 300 | 1.5 | 2 | Office | 1 | 0 | 0 | 326
Healthcare Facility and Hospitals (Exam/Treatment Room) | Misc - All others | 10 | 0.5 | 250 | 200 | 1.5 | 0.24 | Electric | 1.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 1.126 | 0 | 300 | 3000 | 1.5 | 2 | Health | 1 | 0 | 0 | 327
Healthcare Facility and Hospitals (Imaging Room) | Misc - All others | 10 | 0.5 | 250 | 200 | 1.5 | 0.24 | Gas | 0.6 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 75 | 500 | 1.5 | 2 | Health | 1 | 0 | 0 | 328
Healthcare Facility and Hospitals (Medical Supply Room) | Misc - All others | 10 | 0.5 | 250 | 200 | 1.5 | 0.24 | Gas | 0.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 50 | 300 | 1.5 | 2 | Health | 1 | 0 | 0 | 329
Healthcare Facility and Hospitals (Nursery) | Misc - All others | 10 | 0.5 | 250 | 200 | 1.5 | 0.24 | Gas | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 20 | 200 | 1.5 | 2 | Health | 1 | 0 | 0 | 330
Healthcare Facility and Hospitals (Nurse's Station) | Misc - All others | 10 | 0.5 | 250 | 200 | 1.5 | 0.24 | Gas | 0.85 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 75 | 500 | 1.5 | 2 | Health | 1 | 0 | 0 | 331
Healthcare Facility and Hospitals (Operating Room) | Misc - All others | 10 | 0.5 | 250 | 200 | 1.5 | 0.24 | Gas | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 300 | 3000 | 1.5 | 2 | Health | 1 | 0 | 0 | 332
Healthcare Facility and Hospitals (Patient Room) | Misc - All others | 10 | 0.5 | 250 | 200 | 1.5 | 0.24 | Gas | 0.7 | 0 | 0 | 0 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 20 | 200 | 1.5 | 2 | Health | 1 | 0 | 0 | 333
Healthcare Facility and Hospitals (Physical Therapy Room) | Misc - All others | 10 | 0.5 | 250 | 200 | 1.5 | 0.24 | Electric | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 75 | 500 | 1.5 | 2 | Health | 1 | 0 | 0 | 334
Healthcare Facility and Hospitals (Recovery Room) | Misc - All others | 10 | 0.5 | 250 | 200 | 1.5 | 0.24 | Gas | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 20 | 200 | 1.5 | 2 | Health | 1 | 0 | 0 | 335
High-Rise Residential Living Spaces | NA | 5 | 0.5 | 245 | 155 | 0.5 | RULE Spc:DwellingUnitXGalPerDay | Gas | na | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0.6824 | 0 | 20 | 200 | 1.5 | 2 | ResidentialLiving | 0 | 1 | 0 | 336
Hotel Function Area | Lodging - Multipurpose assembly | 142.8571 | 0.5 | 250 | 200 | 0.5 | 0.096 | Gas | 0.85 | 0 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 50 | 300 | 1.5 | 2 | Assembly | 0 | 0 | 0 | 337
Hotel/Motel Guest Room | Lodging - Bedroom/living room | 5 | 0.5 | 245 | 155 | 0.5 | 4.48 | Gas | na | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 20 | 200 | 1.5 | 2 | ResidentialLiving | 0 | 0 | 0 | 338
Kitchen/Food Preparation Area | Food Service - Kitchen (cooking) | 5 | 0.5 | 275 | 475 | 1.5 | 0.578 | Gas | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 17.5377 | 1.12 | 100 | 500 | 1.5 | 2 | Restaurant | 1 | 0 | 1 | 339
Kitchenette or Residential Kitchen | Exhaust - Kitchenettes | 5 | 0.5 | 275 | 475 | 1 | 0.36 | Gas | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 3 | 0.5 | 100 | 500 | 1.5 | 2 | Office | 1 | 0 | 0 | 340
Laboratory, Scientific | Education - University/college laboratories | 10 | 0.5 | 250 | 200 | 2 | 0.18 | Gas | 0.9 | 0 | 0 | 0.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 12.6926 | 0.28 | 500 | 1000 | 1.5 | 2 | Laboratory | 1 | 1 | 0 | 341
Laundry Area | Lodging - Laundry rooms, central | 10 | 0.5 | 250 | 250 | 3 | 0.578 | Gas | 0.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8760 | 8760 | 0.75064 | 0 | 100 | 300 | 1.5 | 2 | ResidentialCommon | 1 | 0 | 1 | 342
Library (Reading Area) | Assembly - Libraries (reading rooms and stack areas) | 20 | 0.5 | 250 | 200 | 1.5 | 0.18 | Electric | 0.8 | 0 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 150 | 500 | 1.5 | 2 | Office | 1 | 0 | 0 | 343
Library (Stacks Area) | Assembly - Libraries (reading rooms and stack areas) | 10 | 0.5 | 250 | 200 | 1.5 | 0.18 | Electric | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 200 | 300 | 1 | 4 | Office | 1 | 0 | 0 | 344
Lobby, Main Entry | Office - Main entry lobbies | 66.6667 | 0.5 | 250 | 250 | 0.5 | 0.09 | Electric | 0.7 | 0 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3.5 | 4 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 50 | 200 | 1.5 | 2 | Assembly | 1 | 0 | 1 | 345
Locker Room | Exhaust - Locker rooms for athletic or industrial facilities | 20 | 0.5 | 255 | 475 | 0.5 | 0.578 | Gas | 0.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8760 | 8760 | 0 | 0 | 20 | 200 | 1 | 4 | Assembly | 1 | 0 | 1 | 346
Lounge, Breakroom, or Waiting Area | General - Break rooms | 66.6667 | 0.5 | 275 | 275 | 1 | 0.09 | Gas | 0.55 | 0 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 40 | 300 | 1.5 | 2 | Assembly | 1 | 1 | 0 | 347
Manufacturing, Commercial & Industrial Work Area (Low Bay) | Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 10 | 0.5 | 275 | 475 | 1 | 0.18 | Gas | 0.6 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 300 | 1000 | 1.5 | 2 | Manufacturing | 1 | 0 | 0 | 348
Manufacturing, Commercial & Industrial Work Area (High Bay) | Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 10 | 0.5 | 275 | 475 | 1 | 0.18 | Gas | 0.65 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 300 | 1000 | 1.5 | 2 | Manufacturing | 1 | 0 | 0 | 349
Manufacturing, Commercial & Industrial Work Area (Precision) | Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 10 | 0.5 | 250 | 200 | 1 | 0.18 | Gas | 0.85 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 1000 | 3000 | 1.5 | 2 | Manufacturing | 1 | 0 | 0 | 350
Museum Area (Exhibition/Display) | Assembly - Museums/galleries | 66.6667 | 0.5 | 250 | 250 | 1.5 | 0.09 | Electric | 0.6 | 0 | 0 | 0 | 0.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 150 | 500 | 1.5 | 2 | Assembly | 1 | 0 | 0 | 351
Museum Area (Restoration Room) | Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 10 | 0.5 | 250 | 250 | 1.5 | 0.18 | Electric | 0.7 | 0 | 0.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 150 | 500 | 1.5 | 2 | Assembly | 1 | 0 | 0 | 352
Office Area (>250 square feet) | Office - Office space | 10 | 0.5 | 250 | 200 | 1.5 | 0.18 | Electric | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 75 | 500 | 1 | 4 | Office | 1 | 0 | 0 | 353
Office Area (<250 square feet) | Office - Office space | 10 | 0.5 | 250 | 200 | 1.5 | 0.18 | Electric | 0.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 75 | 500 | 1.5 | 2 | Office | 1 | 0 | 0 | 354
Parking Garage Area (Parking Zone and Ramps) | Exhaust - Parking garages | 5 | 0.5 | 250 | 200 | 0 | 0 | Electric | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | First 100 + 50 for each additional one | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8760 | 8760 | 0 | 0 | 10 | 40 | 1.5 | 2 | Parking | 1 | 1 | 0 | 355
Parking Garage Area (Daylight Adaptation Zones) (Note 2) | Exhaust - Parking garages | 5 | 0.5 | 250 | 200 | 0 | 0 | Electric | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8760 | 8760 | 0 | 0 | 10 | 40 | 1.5 | 2 | Parking | 1 | 1 | 0 | 356
Pharmacy Area | Misc - Pharmacy (preparation area) | 10 | 0.5 | 250 | 200 | 5 | 0.18 | Electric | 1 | 0 | 0 | 0.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 1 | 100 | 1000 | 1.5 | 2 | Retail | 1 | 0 | 0 | 357
Retail Sales Area (Grocery Sales) | Retail - Supermarket | 16.6667 | 0.5 | 250 | 200 | 1 | 0.18 | Gas | 1 | 0.1 | 0 | 0 | 0.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6 | 7.76 | 8.8 | 0.6 | 0.7 | 0.8 | 0 | 150 | 150 | 0 | 5 | 100 | 1000 | 1.5 | 2 | Retail | 1 | 0 | 0 | 358
Retail Sales Area (Retail Merchandise Sales) | Retail - Sales | 16.6667 | 0.5 | 250 | 200 | 1 | 0.18 | Electric | 0.95 | 0.1 | 0 | 0 | 0.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5 | 11.2 | 12.7 | 0.45 | 0.52 | 0.6 | 0.5 | 150 | 150 | 0 | 0 | 100 | 1000 | 1.5 | 2 | Retail | 1 | 0 | 0 | 359
Retail Sales Area (Fitting Room) | Retail - Sales | 16.6667 | 0.5 | 250 | 200 | 1 | 0.18 | Electric | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 100 | 1000 | 1.5 | 2 | Retail | 1 | 0 | 0 | 360
Religious Worship Area | Assembly - Places of religious worship | 142.8571 | 0.5 | 245 | 105 | 0.5 | 0.09 | Electric | 0.95 | 0 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 200 | 1500 | 1.5 | 2 | Assembly | 1 | 0 | 0 | 361
Restrooms | Exhaust - Toilets, public | 10 | 0.5 | 250 | 250 | 0 | 0 | Gas | 0.65 | 0 | 0 | 0 | 0.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8760 | 8760 | 0 | 0 | 50 | 100 | 1.5 | 2 | Office | 1 | 1 | 0 | 362
Stairwell | General - Corridors | 10 | 0.5 | 250 | 250 | 0 | 0 | Electric | 0.6 | 0 | 0 | 0 | 0.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8760 | 8760 | 0 | 0 | 50 | 100 | 1.5 | 2 | Office | 1 | 1 | 0 | 363
Storage, Commercial/Industrial (Warehouse) | Misc - Warehouses | 2 | 0.5 | 275 | 475 | 0.2 | 0.18 | Electric | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8760 | 8760 | 0 | 0 | 50 | 300 | 1.5 | 2 | Warehouse | 1 | 0 | 0 | 364
Storage, Commercial/Industrial (Refrigerated) | Misc - Freezer and refrigerated spaces (<50F) | 0 | 0.5 | 275 | 475 | 0.2 | 0.18 | Electric | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8760 | 8760 | 0 | 10 | 50 | 300 | 1.5 | 2 | Warehouse | 1 | 0 | 0 | 365
Storage, Commercial/Industrial (Shipping & Handling) | Misc - Shipping/receiving | 5 | 0.5 | 275 | 475 | 0.5 | 0.18 | Electric | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8760 | 8760 | 0 | 0 | 50 | 300 | 1.5 | 2 | Warehouse | 1 | 0 | 0 | 366
Storage, General | Misc - All others | 0 | 0.5 | 250 | 200 | 0.2 | 0 | Electric | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8760 | 8760 | 0 | 0 | 50 | 300 | 1.5 | 2 | Warehouse | 1 | 1 | 0 | 380
Sports Arena - Playing Area (> 5,000 Spectators) | Sports/Entertainment - Gym, sports arena (play area) | 80 | 0.5 | 255 | 875 | 0.5 | 0.18 | Gas | 2.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 150 | 400 | 1.5 | 2 | Retail | 0 | 0 | 0 | 367
Sports Arena - Playing Area (2,000 - 5,000 Spectators) | Sports/Entertainment - Gym, sports arena (play area) | 66.6667 | 0.5 | 255 | 875 | 0.5 | 0.18 | Gas | 1.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 150 | 400 | 1.5 | 2 | Retail | 0 | 0 | 0 | 368
Sports Arena - Playing Area (< 2,000 Spectators) | Sports/Entertainment - Gym, sports arena (play area) | 50 | 0.5 | 255 | 875 | 0.5 | 0.18 | Gas | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 150 | 400 | 1.5 | 2 | Retail | 0 | 0 | 0 | 369
Sports Arena - Playing Area (Recreational) | Sports/Entertainment - Gym, sports arena (play area) | 20 | 0.5 | 255 | 875 | 0.2 | 0.9 | Gas | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 150 | 400 | 1.5 | 2 | Retail | 1 | 0 | 0 | 370
Theater Area (Motion Picture) | Assembly - Auditorium seating area | 142.8571 | 0.5 | 245 | 105 | 0.5 | 0.09 | Electric | 0.5 | 0 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 2 | 50 | 1.5 | 2 | Assembly | 1 | 0 | 0 | 371
Theater Area (Performance) | Sports/Entertainment - Stages, studios | 142.8571 | 0.5 | 245 | 105 | 0.5 | 0.09 | Gas | 0.8 | 0 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 2 | 200 | 1.5 | 2 | Assembly | 1 | 0 | 1 | 372
Transportation Function (Baggage Area) | Misc - Transportation waiting | 33.3333 | 0.5 | 250 | 250 | 0.5 | 0.18 | Electric | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 50 | 500 | 1.5 | 2 | Assembly | 0 | 0 | 0 | 373
Transportation Function (Ticketing Area) | Misc - Transportation waiting | 33.3333 | 0.5 | 250 | 250 | 0.5 | 0.18 | Electric | 0.45 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 50 | 500 | 1.5 | 2 | Assembly | 0 | 0 | 0 | 374
Unleased Tenant Area | Office - Office space | 10 | 0.5 | 250 | 200 | 1.5 | 0.18 | Electric | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 75 | 500 | 1 | 4 | Office | 1 | 0 | 1 | 375
Unoccupied-Exclude from Gross Floor Area | NA | 0 | 0.5 | 250 | 250 | 0 | 0 | Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8760 | 8760 | 0 | 0 | 0 | 0 | 0 | 0 | Unoccupied | 1 | 1 | 0 | 376
Unoccupied-Include in Gross Floor Area | NA | 0 | 0.5 | 250 | 250 | 0 | 0 | Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8760 | 8760 | 0 | 0 | 0 | 0 | 0 | 0 | Unoccupied | 1 | 1 | 0 | 377
Videoconferencing Studio | General - Conference/meeting | 10 | 0.5 | 250 | 200 | 1.5 | 0.18 | Electric | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 300 | 300 | 1.5 | 2 | Office | 1 | 0 | 0 | 378
All other | Misc - All others | 10 | 0.5 | 250 | 200 | 1 | 0.18 | Gas | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 100 | 300 | 1.5 | 2 | Office | 1 | 0 | 1 | 301
Conference, Multipurpose and Meeting Area | General - Conference/meeting | 66.6667 | 0.5 | 245 | 155 | 1 | 0.09 | Electric | 0.75 | 0 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2.35 | 2.66 | 0.3 | 0.35 | 0.4 | 0 | 150 | 150 | 0 | 0 | 30 | 300 | 1.5 | 2 | Assembly | 1 | 0 | 1 | 381
Storage | Misc - All others | 0 | 0.5 | 250 | 200 | 0.2 | 0 | Electric | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8760 | 8760 | 0 | 0 | 50 | 300 | 1.5 | 2 | Warehouse | 0 | 1 | 0 | 379
Health Care / Assisted Living (Nurse's Station) | Misc - All others | 10 | 0.5 | 250 | 200 | 1.5 | 0.24 | Gas | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 75 | 500 | 1.5 | 2 | ResidentialCommon | 0 | 0 | 0 | 382
Health Care / Assisted Living (Physical Therapy Room) | Misc - All others | 10 | 0.5 | 250 | 200 | 1.5 | 0.24 | Electric | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 75 | 500 | 1.5 | 2 | ResidentialCommon | 0 | 0 | 0 | 383

## For CSV - 2025 SpcFuncData
// This table pasted into App5-4A_SpaceBySpace-T24N_2025.csv
TABLE SpaceFunctionData
| FuncType | VentSpcFuncDef | OccDens | OccVentFrac | OccSensHtRt | OccLatHtRt | RecptPwrDens | HotWtrHrlyUsePerPers | BaseWtrHtrType | IntLPDReg | HiCeilingAllow | DetTaskAllow | SpecTaskAllow | DecorativeAllow | PrecAllow | WhtOrChkAllow | VideoAllow | PrkgATMAllow | PortOffLtgAllow | ExtIllumMirrorAllow | IntIllumMirrorAllow | TransLtgOffAtNightAllow | TunWhtOrDimToWarmAllow | WallDisplayLoMHAllow | WallDisplayMeMHAllow | WallDisplayHiMHAllow | FlrDispTaskLoMHAllow | FlrDispTaskMeMHAllow | FlrDispTaskHiMHAllow | ValDispAllow | ClgUMLHLimit | HtgUMLHLimit | GasEqpPwrDens | CommRfrgEPD | IllumSetptMin | IllumSetptMax | IllumSetptAdjFacPri | IllumSetptAdjFacSec | FuncSchGrp | OccSchRef | RecptSchRef | HotWtrHtgSchRef | IntLtgRegSchRef | GasEqpSchRef | CommRfrgEqpSchRef | InfSchRef | AvailSchRef | HtgTstatSchRef | ClgTstatSchRef | ElevSchRef | EscalSchRef | WtrHtrTempSetptSchRef | SpcFuncIdx | HlthcareEligible | ExcludeFromPredominantCalc | FuncSchGrpIsEditable | NRCCPRFSpaceFunction | NRCCPRFSpaceFunctionTailored | PVBatteryBldgType | ;
| //SpaceBySpace |  | # per 1000 ft² |  | Btu / occupant | Btu / occupant | Load W/ft² | Gal/h per person |  | W/ft² | W/ft² | W/ft² | W/ft² | W/ft² | W/ft² | W/ft | W/ft² | W | W/ft² | W | W | W/ft² | W/ft² | W/ft | W/ft | W/ft | W/ft² | W/ft² | W/ft² | W/ft² | Hrs | Hrs | Btu/h-ft2 | W/ft2 | lux | lux |  |  |  | Occupancy Schedule | Receptacle Schedule | Hot Water Schedule | Regulated Lighting Schedule | Gas Equipment Schedule | Refrigeration Schedule | Infiltration Schedule | Availability Sched | Heating Setpoint Schedule (F) | Cooling Setpoint Schedule (F) | Elevator Schedule | Escalator Schedule | Water Heater Temperature Setpoint Schedule | Space Function Index | Is Eligible for Healthcare Exemption | Excluded From Predominant Calculation | FuncSchGrp is Editable | Mapping from Spc:SpcFunc to NRCC PRF | Mapping from Spc:SpcFunc to NRCC PRF | Bldg types present in 2022 std tables 140.10-A,B | ;
| Aging Eye/Low-vision (Corridor Area) | General - Corridors | 10 | 0.5 | 250 | 250 | 0 | 0 | Electric | 0.7 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 50 | 100 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | 302 | 1 | 1 | 0 | LowVisionCorridorArea | NA | default by predominance | ;
| Aging Eye/Low-vision (Dining) | Food Service - Cafeteria/fast-food dining | 66.67 | 0.5 | 275 | 275 | 0.5 | 0.578 | Gas | 0.8 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0.25 | 50 | 200 | 1.5 | 2 | Restaurant | RestaurantOccupancy | RestaurantReceptacle | RestaurantServiceHotWater | RestaurantLights | RestaurantGasEquip | RestaurantRefrigeration | RestaurantInfiltration | RestaurantHVACAvail | RestaurantHtgSetpt | RestaurantClgSetpt | RestaurantElevator | RestaurantEscalator | RestaurantWtrHtrSetpt | 303 | 1 | 0 | 0 | LowVisionDiningArea | NA | default by predominance | ; |  | 2022 std tables 140.10-A,B Bldg Type mapping | mapping to 2025 BldgType | 2022 Bldg Type as stated in standard
| Aging Eye/Low-vision (Lobby, Main Entry) | Office - Main entry lobbies | 66.67 | 0.5 | 250 | 250 | 0.5 | 0.09 | Electric | 0.85 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 50 | 200 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | 304 | 1 | 0 | 0 | LowVisionLobbyMainEntry | NA | default by predominance | ; |  | Grocery | Retail, Grocery | Grocery
| Aging Eye/Low-vision (Lounge/Waiting Area) | General - Break rooms | 66.67 | 0.5 | 275 | 275 | 1 | 0.09 | Gas | 0.8 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 40 | 300 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | 305 | 1 | 0 | 0 | LowVisionWaitingArea | NA | default by predominance | ; |  | Highrise Multifamily | Highrise Multifamily | Highrise Multifamily
| Aging Eye/Low-vision (Multipurpose Room) | General - Conference/meeting | 66.67 | 0.5 | 245 | 155 | 1 | 0.09 | Electric | 0.85 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 30 | 300 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | 306 | 1 | 0 | 0 | LowVisionMultipurposeRoom | NA | default by predominance | ; |  | Office, Financial, Unleased Tenant | Office, Financial, Unleased, Med Office/Clinic | Office, Financial Institutions, Unleased Tenant Space
| Aging Eye/Low-vision (Religious Worship Area) | Assembly - Places of religious worship | 142.86 | 0.5 | 245 | 105 | 0.5 | 0.09 | Electric | 1 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 200 | 1500 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | 307 | 1 | 0 | 0 | LowVisionReligiousWorshipArea | NA | Religious Worship | ; |  | Retail | Retail, Grocery | Retail
| Aging Eye/Low-vision (Restroom) | Exhaust - Toilets, public | 10 | 0.5 | 250 | 250 | 0 | 0 | Gas | 1 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 50 | 100 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | 308 | 1 | 1 | 0 | LowVisionRestroom | NA | default by predominance | ; |  | School | School | School
| Aging Eye/Low-vision (Stairwell) | General - Corridors | 10 | 0.5 | 250 | 250 | 0 | 0 | Electric | 0.8 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 50 | 100 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | 309 | 1 | 1 | 0 | LowVisionStairwell | NA | default by predominance | ; |  | Warehouse | Warehouse | Warehouse
| Audience Seating Area | Assembly - Auditorium seating area | 142.86 | 0.5 | 245 | 105 | 1 | 0.09 | Electric | 0.5 | 0 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 50 | 1000 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | 310 | 1 | 0 | 0 | AudienceSeatingArea | NA | default by predominance | ; |  | Other | - revert to 2025 SpcFunc mapping default - | Auditorium, Convention Center, Hotel/Motel, Library, Medical Office Building/Clinic, Restaurant, Theater
| Auditorium Area | Assembly - Auditorium seating area | 142.86 | 0.5 | 245 | 105 | 1 | 0.09 | Electric | 0.7 | 0 | 0 | 0 | 0.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 50 | 1000 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | 311 | 1 | 0 | 0 | AuditoriumArea | AuditoriumArea | Other | ;
| Auto Repair / Maintenance Area | Exhaust - Auto repair rooms | 10 | 0.5 | 275 | 475 | 1 | 0.18 | Gas | 0.55 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0.75064 | 0 | 200 | 1500 | 1.5 | 2 | Manufacturing | ManufacturingOccupancy | ManufacturingReceptacle | ManufacturingServiceHotWater | ManufacturingLights | ManufacturingGasEquip | ManufacturingRefrigeration | ManufacturingInfiltration | ManufacturingHVACAvail | ManufacturingHtgSetpt | ManufacturingClgSetpt | ManufacturingElevator | ManufacturingEscalator | ManufacturingWtrHtrSetpt | 312 | 1 | 0 | 0 | AutoRepairArea | NA | none | ;
| Barber, Beauty Salon, Spa Area | Retail - Beauty and nail salons | 10 | 0.5 | 250 | 200 | 2 | 0.18 | Gas | 0.7 | 0 | 0.3 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 500 | 500 | 1.5 | 2 | Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt | 313 | 1 | 0 | 0 | BeautySalonArea | NA | Retail, Grocery | ; |  | 2025 std tables 140.10-A,B Bldg Type mapping | 2025 Bldg Type as stated in standard
| Civic Meeting Place Area | Assembly - Legislative chambers | 66.67 | 0.5 | 250 | 200 | 1.5 | 0.18 | Electric | 0.9 | 0 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 30 | 300 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | 314 | 1 | 0 | 0 | CivicMeetingPlaceArea | NA | default by predominance | ; |  | Events, Exhibits | Events & Exhibits
| Classroom, Lecture, Training, Vocational Areas | Education - Classrooms (ages 9-18) | 50 | 0.5 | 245 | 155 | 1 | 0.18 | Gas | 0.6 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 50 | 500 | 1.5 | 2 | School | SchoolOccupancy | SchoolReceptacle | SchoolServiceHotWater | SchoolLights | SchoolGasEquip | SchoolRefrigeration | SchoolInfiltration | SchoolHVACAvail | SchoolHtgSetpt | SchoolClgSetpt | SchoolElevator | SchoolEscalator | SchoolWtrHtrSetpt | 315 | 1 | 0 | 0 | ClassroomLectureTrainingVocationalArea | NA | School | ; |  | Library | Library
| Computer Room | Misc - Computer (not printing) | 3 | 0.5 | 275 | 475 | 0 | 0.18 | Electric | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 75 | 300 | 1 | 4 | Data | DataOccupancy | DataReceptacle | DataServiceHotWater | DataLights | DataGasEquip | DataRefrigeration | DataInfiltration | DataHVACAvail | DataHtgSetpt | DataClgSetpt | DataElevator | DataEscalator | DataWtrHtrSetpt | 316 | 0 | 1 | 0 | ComputerRoom | NA | default by predominance | ; | Computer Room | Hotel/Motel | Hotel/Motel
| Concourse and Atria Area | Retail - Mall common areas | 33.33 | 0.5 | 250 | 250 | 0.5 | 0.18 | Electric | 0.6 | 0 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 100 | 300 | 1.5 | 2 | Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt | 317 | 1 | 1 | 0 | MallAndAtria | NA | default by predominance | ; |  | Office, Financial, Unleased, Med Office/Clinic | Office, Financial Institution, Unleased Tenant Space, Medical Office Building/Clinic
| Convention, Conference, Multipurpose and Meeting Area | General - Conference/meeting | 66.67 | 0.5 | 245 | 155 | 1 | 0.09 | Electric | 0.75 | 0 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2.35 | 2.66 | 0.3 | 0.35 | 0.4 | 0 | 150 | 150 | 0 | 0 | 30 | 300 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | 318 | 1 | 0 | 1 | ConventionConferenceMultipurposeMeetingCenterArea | MultipurposeArea | Other | ; |  | Restaurants | Restaurants
| Copy Room | Exhaust - Copy, printing rooms | 10 | 0.5 | 250 | 250 | 1 | 0.18 | Electric | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8760 | 8760 | 0 | 0 | 75 | 500 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | 319 | 1 | 0 | 1 | CopyRoom | NA | default by predominance | ; |  | Retail, Grocery | Retail, Grocery
| Corridor Area | General - Corridors | 10 | 0.5 | 250 | 250 | 0 | 0 | Electric | 0.4 | 0 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8760 | 8760 | 0 | 0 | 50 | 100 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | 320 | 1 | 1 | 0 | CorridorArea | NA | default by predominance | ; |  | School | School
| Dining Area (Bar/Lounge and Fine Dining) | Food Service - Restaurant dining rooms | 66.67 | 0.5 | 275 | 275 | 0.5 | 0.578 | Gas | 0.45 | 0.25 | 0 | 0 | 0.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.25 | 1.5 | 1.7 | 0.45 | 0.52 | 0.6 | 0 | 150 | 150 | 0 | 0 | 50 | 200 | 1.5 | 2 | Restaurant | RestaurantOccupancy | RestaurantReceptacle | RestaurantServiceHotWater | RestaurantLights | RestaurantGasEquip | RestaurantRefrigeration | RestaurantInfiltration | RestaurantHVACAvail | RestaurantHtgSetpt | RestaurantClgSetpt | RestaurantElevator | RestaurantEscalator | RestaurantWtrHtrSetpt | 321 | 1 | 0 | 0 | BarLoungeFineDiningArea | DiningArea | Restaurants | ; |  | Warehouse | Warehouse
| Dining Area (Cafeteria/Fast Food) | Food Service - Cafeteria/fast-food dining | 66.67 | 0.5 | 275 | 275 | 0.5 | 0.578 | Gas | 0.45 | 0 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0.25 | 50 | 200 | 1.5 | 2 | Restaurant | RestaurantOccupancy | RestaurantReceptacle | RestaurantServiceHotWater | RestaurantLights | RestaurantGasEquip | RestaurantRefrigeration | RestaurantInfiltration | RestaurantHVACAvail | RestaurantHtgSetpt | RestaurantClgSetpt | RestaurantElevator | RestaurantEscalator | RestaurantWtrHtrSetpt | 322 | 1 | 0 | 1 | FastfoodDining | DiningArea | default by predominance | ; |  | Religious Worship | Religious Worship
| Dining Area (Family and Leisure) | Food Service - Cafeteria/fast-food dining | 66.67 | 0.5 | 275 | 275 | 0.5 | 0.578 | Gas | 0.4 | 0 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0.25 | 50 | 200 | 1.5 | 2 | Restaurant | RestaurantOccupancy | RestaurantReceptacle | RestaurantServiceHotWater | RestaurantLights | RestaurantGasEquip | RestaurantRefrigeration | RestaurantInfiltration | RestaurantHVACAvail | RestaurantHtgSetpt | RestaurantClgSetpt | RestaurantElevator | RestaurantEscalator | RestaurantWtrHtrSetpt | 323 | 1 | 0 | 0 | FamilyDiningArea | DiningArea | Restaurants | ; |  | Sports, Recreation | Sports & Recreation
| Electrical, Mechanical, Telephone Rooms | Misc - Telephone closets | 3 | 0.5 | 250 | 250 | 3 | 0.18 | Electric | 0.4 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8760 | 8760 | 0 | 0 | 200 | 200 | 1 | 4 | Warehouse | WarehouseOccupancy | WarehouseReceptacle | WarehouseServiceHotWater | WarehouseLights | WarehouseGasEquip | WarehouseRefrigeration | WarehouseInfiltration | WarehouseHVACAvail | WarehouseHtgSetpt | WarehouseClgSetpt | WarehouseElevator | WarehouseEscalator | WarehouseWtrHtrSetpt | 324 | 1 | 1 | 0 | ElectricalMechancialTelephoneRoom | NA | default by predominance | ; |  | Highrise Multifamily | Multifamily > 3 stories
| Exercise/Fitness Center and Gymnasium Areas | Sports/Entertainment - Gym, sports arena (play area) | 20 | 0.5 | 255 | 875 | 0.5 | 0.18 | Gas | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 150 | 400 | 1.5 | 2 | Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt | 325 | 1 | 0 | 1 | ExerciseCenterGymnasiumArea | NA | default by predominance | ;
| Financial Transaction Area | Misc - Banks or bank lobbies | 10 | 0.5 | 250 | 250 | 1.5 | 0.18 | Electric | 0.7 | 0 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 100 | 300 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | 326 | 1 | 0 | 0 | FinancialTransactionsArea | NA | Office, Financial, Unleased, Med Office/Clinic | ;
| Healthcare Facility and Hospitals (Exam/Treatment Room) | Misc - All others | 10 | 0.5 | 250 | 200 | 1.5 | 0.24 | Electric | 1.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 1.126 | 0 | 300 | 3000 | 1.5 | 2 | Health | HealthOccupancy | HealthReceptacle | HealthServiceHotWater | HealthLights | HealthGasEquip | HealthRefrigeration | HealthInfiltration | HealthHVACAvail | HealthHtgSetpt | HealthClgSetpt | HealthElevator | HealthEscalator | HealthWtrHtrSetpt | 327 | 1 | 0 | 0 | HospitalExamTreatment | NA | Other | ;
| Healthcare Facility and Hospitals (Imaging Room) | Misc - All others | 10 | 0.5 | 250 | 200 | 1.5 | 0.24 | Gas | 0.6 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 75 | 500 | 1.5 | 2 | Health | HealthOccupancy | HealthReceptacle | HealthServiceHotWater | HealthLights | HealthGasEquip | HealthRefrigeration | HealthInfiltration | HealthHVACAvail | HealthHtgSetpt | HealthClgSetpt | HealthElevator | HealthEscalator | HealthWtrHtrSetpt | 328 | 1 | 0 | 0 | HospitalImaging | NA | Other | ;
| Healthcare Facility and Hospitals (Medical Supply Room) | Misc - All others | 10 | 0.5 | 250 | 200 | 1.5 | 0.24 | Gas | 0.55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 50 | 300 | 1.5 | 2 | Health | HealthOccupancy | HealthReceptacle | HealthServiceHotWater | HealthLights | HealthGasEquip | HealthRefrigeration | HealthInfiltration | HealthHVACAvail | HealthHtgSetpt | HealthClgSetpt | HealthElevator | HealthEscalator | HealthWtrHtrSetpt | 329 | 1 | 0 | 0 | HospitalMedicalSupply | NA | Other | ;
| Healthcare Facility and Hospitals (Nursery) | Misc - All others | 10 | 0.5 | 250 | 200 | 1.5 | 0.24 | Gas | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 20 | 200 | 1.5 | 2 | Health | HealthOccupancy | HealthReceptacle | HealthServiceHotWater | HealthLights | HealthGasEquip | HealthRefrigeration | HealthInfiltration | HealthHVACAvail | HealthHtgSetpt | HealthClgSetpt | HealthElevator | HealthEscalator | HealthWtrHtrSetpt | 330 | 1 | 0 | 0 | HospitalNursery | NA | Other | ;
| Healthcare Facility and Hospitals (Nurse's Station) | Misc - All others | 10 | 0.5 | 250 | 200 | 1.5 | 0.24 | Gas | 0.85 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 75 | 500 | 1.5 | 2 | Health | HealthOccupancy | HealthReceptacle | HealthServiceHotWater | HealthLights | HealthGasEquip | HealthRefrigeration | HealthInfiltration | HealthHVACAvail | HealthHtgSetpt | HealthClgSetpt | HealthElevator | HealthEscalator | HealthWtrHtrSetpt | 331 | 1 | 0 | 0 | HospitalNurseStation | NA | Other | ;
| Healthcare Facility and Hospitals (Operating Room) | Misc - All others | 10 | 0.5 | 250 | 200 | 1.5 | 0.24 | Gas | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 300 | 3000 | 1.5 | 2 | Health | HealthOccupancy | HealthReceptacle | HealthServiceHotWater | HealthLights | HealthGasEquip | HealthRefrigeration | HealthInfiltration | HealthHVACAvail | HealthHtgSetpt | HealthClgSetpt | HealthElevator | HealthEscalator | HealthWtrHtrSetpt | 332 | 1 | 0 | 0 | HospitalOperatingRoom | NA | Other | ;
| Healthcare Facility and Hospitals (Patient Room) | Misc - All others | 10 | 0.5 | 250 | 200 | 1.5 | 0.24 | Gas | 0.7 | 0 | 0 | 0 | 0.15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 20 | 200 | 1.5 | 2 | Health | HealthOccupancy | HealthReceptacle | HealthServiceHotWater | HealthLights | HealthGasEquip | HealthRefrigeration | HealthInfiltration | HealthHVACAvail | HealthHtgSetpt | HealthClgSetpt | HealthElevator | HealthEscalator | HealthWtrHtrSetpt | 333 | 1 | 0 | 0 | HospitalPatientRoom | NA | Other | ;
| Healthcare Facility and Hospitals (Physical Therapy Room) | Misc - All others | 10 | 0.5 | 250 | 200 | 1.5 | 0.24 | Electric | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 75 | 500 | 1.5 | 2 | Health | HealthOccupancy | HealthReceptacle | HealthServiceHotWater | HealthLights | HealthGasEquip | HealthRefrigeration | HealthInfiltration | HealthHVACAvail | HealthHtgSetpt | HealthClgSetpt | HealthElevator | HealthEscalator | HealthWtrHtrSetpt | 334 | 1 | 0 | 0 | HospitalPhysicalTherapy | NA | Other | ;
| Healthcare Facility and Hospitals (Recovery Room) | Misc - All others | 10 | 0.5 | 250 | 200 | 1.5 | 0.24 | Gas | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 20 | 200 | 1.5 | 2 | Health | HealthOccupancy | HealthReceptacle | HealthServiceHotWater | HealthLights | HealthGasEquip | HealthRefrigeration | HealthInfiltration | HealthHVACAvail | HealthHtgSetpt | HealthClgSetpt | HealthElevator | HealthEscalator | HealthWtrHtrSetpt | 335 | 1 | 0 | 0 | HospitalRecovery | NA | Other | ;
| High-Rise Residential Living Spaces | NA | 5 | 0.5 | 245 | 155 | 0.5 | RULE Spc:DwellingUnitXGalPerDay | Gas | na | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0.6824 | 0 | 20 | 200 | 1.5 | 2 | ResidentialLiving | ResidentialLivingOccupancy | ResidentialLivingReceptacle | ResidentialLivingServiceHotWater | ResidentialLivingLights | ResidentialLivingGasEquip | ResidentialLivingRefrigeration | ResidentialLivingInfiltration | ResidentialLivingHVACAvail | ResidentialLivingHtgSetpt | ResidentialLivingClgSetpt | ResidentialLivingElevator | ResidentialLivingEscalator | ResidentialLivingWtrHtrSetpt | 336 | 0 | 1 | 0 | HighRiseResidentialLivingSpace | NA | Highrise Multifamily | ; | High-Rise Residential Living Spaces
| Hotel Function Area | Lodging - Multipurpose assembly | 142.86 | 0.5 | 250 | 200 | 0.5 | 0.096 | Gas | 0.85 | 0 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 50 | 300 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | 337 | 0 | 0 | 0 | HotelFunctionArea | HotelBallroomEventsArea | Hotel/Motel | ; | Hotel Function Area
| Hotel/Motel Guest Room | Lodging - Bedroom/living room | 5 | 0.5 | 245 | 155 | 0.5 | 4.48 | Gas | na | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 20 | 200 | 1.5 | 2 | ResidentialLiving | ResidentialLivingOccupancy | ResidentialLivingReceptacle | ResidentialLivingServiceHotWater | ResidentialLivingLights | ResidentialLivingGasEquip | ResidentialLivingRefrigeration | ResidentialLivingInfiltration | ResidentialLivingHVACAvail | ResidentialLivingHtgSetpt | ResidentialLivingClgSetpt | ResidentialLivingElevator | ResidentialLivingEscalator | ResidentialLivingWtrHtrSetpt | 338 | 0 | 0 | 0 | HotelMotelGuestRoom | NA | Hotel/Motel | ; | Hotel/Motel Guest Room
| Kitchen/Food Preparation Area | Food Service - Kitchen (cooking) | 5 | 0.5 | 275 | 475 | 1.5 | 0.578 | Gas | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 17.5377 | 1.12 | 100 | 500 | 1.5 | 2 | Restaurant | RestaurantOccupancy | RestaurantReceptacle | RestaurantServiceHotWater | RestaurantLights | RestaurantGasEquip | RestaurantRefrigeration | RestaurantInfiltration | RestaurantHVACAvail | RestaurantHtgSetpt | RestaurantClgSetpt | RestaurantElevator | RestaurantEscalator | RestaurantWtrHtrSetpt | 339 | 1 | 0 | 1 | KitchenCommercialFoodPreparation | NA | default by predominance | ;
| Kitchenette or Residential Kitchen | Exhaust - Kitchenettes | 5 | 0.5 | 275 | 475 | 1 | 0.36 | Gas | 0.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 3 | 0.5 | 100 | 500 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | 340 | 1 | 0 | 0 | KitchenetteResidentialKitchen | NA | default by predominance | ;
| Laboratory, Scientific | Education - University/college laboratories | 10 | 0.5 | 250 | 200 | 2 | 0.18 | Gas | 0.9 | 0 | 0 | 0.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 12.6926 | 0.28 | 500 | 1000 | 1.5 | 2 | Laboratory | LaboratoryOccupancy | LaboratoryReceptacle | LaboratoryServiceHotWater | LaboratoryLights | LaboratoryGasEquip | LaboratoryRefrigeration | LaboratoryInfiltration | LaboratoryHVACAvail | LaboratoryHtgSetpt | LaboratoryClgSetpt | LaboratoryElevator | LaboratoryEscalator | LaboratoryWtrHtrSetpt | 341 | 1 | 1 | 0 | LaboratoryScientific | NA | default by predominance | ;
| Laundry Area | Lodging - Laundry rooms, central | 10 | 0.5 | 250 | 250 | 3 | 0.578 | Gas | 0.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8760 | 8760 | 0.75064 | 0 | 100 | 300 | 1.5 | 2 | ResidentialCommon | ResidentialCommonOccupancy | ResidentialCommonReceptacle | ResidentialCommonServiceHotWater | ResidentialCommonLights | ResidentialCommonGasEquip | ResidentialCommonRefrigeration | ResidentialCommonInfiltration | ResidentialCommonHVACAvail | ResidentialCommonHtgSetpt | ResidentialCommonClgSetpt | ResidentialCommonElevator | ResidentialCommonEscalator | ResidentialCommonWtrHtrSetpt | 342 | 1 | 0 | 1 | Laundry | NA | default by predominance | ;
| Library (Reading Area) | Assembly - Libraries (reading rooms and stack areas) | 20 | 0.5 | 250 | 200 | 1.5 | 0.18 | Electric | 0.8 | 0 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 150 | 500 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | 343 | 1 | 0 | 0 | LibraryReadingArea | NA | Library | ;
| Library (Stacks Area) | Assembly - Libraries (reading rooms and stack areas) | 10 | 0.5 | 250 | 200 | 1.5 | 0.18 | Electric | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 200 | 300 | 1 | 4 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | 344 | 1 | 0 | 0 | LibraryStacks | NA | Library | ;
| Lobby, Main Entry | Office - Main entry lobbies | 66.67 | 0.5 | 250 | 250 | 0.5 | 0.09 | Electric | 0.7 | 0 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 3.5 | 4 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 50 | 200 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | 345 | 1 | 0 | 1 | LobbyMainEntry | MainEntryLobby | default by predominance | ;
| Locker Room | Exhaust - Locker rooms for athletic or industrial facilities | 20 | 0.5 | 255 | 475 | 0.5 | 0.578 | Gas | 0.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8760 | 8760 | 0 | 0 | 20 | 200 | 1 | 4 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | 346 | 1 | 0 | 1 | LockerDressingRoom | NA | default by predominance | ;
| Lounge, Breakroom, or Waiting Area | General - Break rooms | 66.67 | 0.5 | 275 | 275 | 1 | 0.09 | Gas | 0.55 | 0 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 40 | 300 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | 347 | 1 | 1 | 0 | LoungeBreakRoom | NA | default by predominance | ;
| Manufacturing, Commercial & Industrial Work Area (Low Bay) | Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 10 | 0.5 | 275 | 475 | 1 | 0.18 | Gas | 0.6 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 300 | 1000 | 1.5 | 2 | Manufacturing | ManufacturingOccupancy | ManufacturingReceptacle | ManufacturingServiceHotWater | ManufacturingLights | ManufacturingGasEquip | ManufacturingRefrigeration | ManufacturingInfiltration | ManufacturingHVACAvail | ManufacturingHtgSetpt | ManufacturingClgSetpt | ManufacturingElevator | ManufacturingEscalator | ManufacturingWtrHtrSetpt | 348 | 1 | 0 | 0 | GeneralCommercialIndustrialWorkAreaLowBay | NA | none | ;
| Manufacturing, Commercial & Industrial Work Area (High Bay) | Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 10 | 0.5 | 275 | 475 | 1 | 0.18 | Gas | 0.65 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 300 | 1000 | 1.5 | 2 | Manufacturing | ManufacturingOccupancy | ManufacturingReceptacle | ManufacturingServiceHotWater | ManufacturingLights | ManufacturingGasEquip | ManufacturingRefrigeration | ManufacturingInfiltration | ManufacturingHVACAvail | ManufacturingHtgSetpt | ManufacturingClgSetpt | ManufacturingElevator | ManufacturingEscalator | ManufacturingWtrHtrSetpt | 349 | 1 | 0 | 0 | GeneralCommercialIndustrialWorkAreaHighBay | NA | none | ;
| Manufacturing, Commercial & Industrial Work Area (Precision) | Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 10 | 0.5 | 250 | 200 | 1 | 0.18 | Gas | 0.85 | 0 | 0 | 0 | 0 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 1000 | 3000 | 1.5 | 2 | Manufacturing | ManufacturingOccupancy | ManufacturingReceptacle | ManufacturingServiceHotWater | ManufacturingLights | ManufacturingGasEquip | ManufacturingRefrigeration | ManufacturingInfiltration | ManufacturingHVACAvail | ManufacturingHtgSetpt | ManufacturingClgSetpt | ManufacturingElevator | ManufacturingEscalator | ManufacturingWtrHtrSetpt | 350 | 1 | 0 | 0 | GeneralCommercialIndustrialWorkAreaPrecision | NA | none | ;
| Museum Area (Exhibition/Display) | Assembly - Museums/galleries | 66.67 | 0.5 | 250 | 250 | 1.5 | 0.09 | Electric | 0.6 | 0 | 0 | 0 | 0.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 150 | 500 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | 351 | 1 | 0 | 0 | ExhibitMuseumArea | ExhibitMuseumArea | Events, Exhibits | ;
| Museum Area (Restoration Room) | Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 10 | 0.5 | 250 | 250 | 1.5 | 0.18 | Electric | 0.7 | 0 | 0.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 150 | 500 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | 352 | 1 | 0 | 0 | MuseumRestoration | NA | none | ;
| Office Area (>250 square feet) | Office - Office space | 10 | 0.5 | 250 | 200 | 1.5 | 0.18 | Electric | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 75 | 500 | 1 | 4 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | 353 | 1 | 0 | 0 | OfficeGreaterThan250Ft | NA | Office, Financial, Unleased, Med Office/Clinic | ;
| Office Area (<250 square feet) | Office - Office space | 10 | 0.5 | 250 | 200 | 1.5 | 0.18 | Electric | 0.65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 75 | 500 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | 354 | 1 | 0 | 0 | Office250FtOrLess | NA | Office, Financial, Unleased, Med Office/Clinic | ;
| Parking Garage Area (Parking Zone and Ramps) | Exhaust - Parking garages | 5 | 0.5 | 250 | 200 | 0 | 0 | Electric | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | First 100 + 50 for each additional one | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8760 | 8760 | 0 | 0 | 10 | 40 | 1.5 | 2 | Parking | ParkingOccupancy | ParkingReceptacle | ParkingServiceHotWater | ParkingLights | ParkingGasEquip | ParkingRefrigeration | ParkingInfiltration | ParkingHVACAvail | ParkingHtgSetpt | ParkingClgSetpt | ParkingElevator | ParkingEscalator | ParkingWtrHtrSetpt | 355 | 1 | 1 | 0 | ParkingGarageBuildingParkingArea | NA | none | ;
| Parking Garage Area (Daylight Adaptation Zones) | Exhaust - Parking garages | 5 | 0.5 | 250 | 200 | 0 | 0 | Electric | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8760 | 8760 | 0 | 0 | 10 | 40 | 1.5 | 2 | Parking | ParkingOccupancy | ParkingReceptacle | ParkingServiceHotWater | ParkingLights | ParkingGasEquip | ParkingRefrigeration | ParkingInfiltration | ParkingHVACAvail | ParkingHtgSetpt | ParkingClgSetpt | ParkingElevator | ParkingEscalator | ParkingWtrHtrSetpt | 356 | 1 | 1 | 0 | ParkingGarageAreaDaylightAdaptationZone | NA | none | ;
| Pharmacy Area | Misc - Pharmacy (preparation area) | 10 | 0.5 | 250 | 200 | 5 | 0.18 | Electric | 1 | 0 | 0 | 0.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 1 | 100 | 1000 | 1.5 | 2 | Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt | 357 | 1 | 0 | 0 | PharmacyArea | NA | default by predominance | ;
| Retail Sales Area (Grocery Sales) | Retail - Supermarket | 16.67 | 0.5 | 250 | 200 | 1 | 0.18 | Gas | 1 | 0.1 | 0 | 0 | 0.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6 | 7.76 | 8.8 | 0.6 | 0.7 | 0.8 | 0 | 150 | 150 | 0 | 5 | 100 | 1000 | 1.5 | 2 | Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt | 358 | 1 | 0 | 0 | GrocerySalesArea | GroceryStoreArea | Retail, Grocery | ;
| Retail Sales Area (Retail Merchandise Sales) | Retail - Sales | 16.67 | 0.5 | 250 | 200 | 1 | 0.18 | Electric | 0.95 | 0.1 | 0 | 0 | 0.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5 | 11.2 | 12.7 | 0.45 | 0.52 | 0.6 | 0.5 | 150 | 150 | 0 | 0 | 100 | 1000 | 1.5 | 2 | Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt | 359 | 1 | 0 | 0 | RetailSalesArea | RetailMerchandiseSales | Retail, Grocery | ;
| Retail Sales Area (Fitting Room) | Retail - Sales | 16.67 | 0.5 | 250 | 200 | 1 | 0.18 | Electric | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 100 | 1000 | 1.5 | 2 | Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt | 360 | 1 | 0 | 0 | RetailFittingRoom | NA | Retail, Grocery | ;
| Religious Worship Area | Assembly - Places of religious worship | 142.86 | 0.5 | 245 | 105 | 0.5 | 0.09 | Electric | 0.95 | 0 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 200 | 1500 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | 361 | 1 | 0 | 0 | ReligiousWorshipArea | ReligiousWorshipArea | Religious Worship | ;
| Restrooms | Exhaust - Toilets, public | 10 | 0.5 | 250 | 250 | 0 | 0 | Gas | 0.65 | 0 | 0 | 0 | 0.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8760 | 8760 | 0 | 0 | 50 | 100 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | 362 | 1 | 1 | 0 | Restroom | NA | default by predominance | ;
| Stairwell | General - Corridors | 10 | 0.5 | 250 | 250 | 0 | 0 | Electric | 0.6 | 0 | 0 | 0 | 0.35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8760 | 8760 | 0 | 0 | 50 | 100 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | 363 | 1 | 1 | 0 | Stairwell | NA | default by predominance | ;
| Storage, Commercial/Industrial (Warehouse) | Misc - Warehouses | 2 | 0.5 | 275 | 475 | 0.2 | 0.18 | Electric | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8760 | 8760 | 0 | 0 | 50 | 300 | 1.5 | 2 | Warehouse | WarehouseOccupancy | WarehouseReceptacle | WarehouseServiceHotWater | WarehouseLights | WarehouseGasEquip | WarehouseRefrigeration | WarehouseInfiltration | WarehouseHVACAvail | WarehouseHtgSetpt | WarehouseClgSetpt | WarehouseElevator | WarehouseEscalator | WarehouseWtrHtrSetpt | 364 | 1 | 0 | 0 | CommercialIndustrialWarehouse | NA | Warehouse | ;
| Storage, Commercial/Industrial (Refrigerated) | Misc - Freezer and refrigerated spaces (<50F) | 0 | 0.5 | 275 | 475 | 0.2 | 0.18 | Electric | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8760 | 8760 | 0 | 10 | 50 | 300 | 1.5 | 2 | Warehouse | WarehouseOccupancy | WarehouseReceptacle | WarehouseServiceHotWater | WarehouseLights | WarehouseGasEquip | WarehouseRefrigeration | WarehouseInfiltration | WarehouseHVACAvail | WarehouseHtgSetpt | WarehouseClgSetpt | WarehouseElevator | WarehouseEscalator | WarehouseWtrHtrSetpt | 365 | 1 | 0 | 0 | CommercialIndustrialStorageAreaRefrigerated | NA | Warehouse | ;
| Storage, Commercial/Industrial (Shipping & Handling) | Misc - Shipping/receiving | 5 | 0.5 | 275 | 475 | 0.5 | 0.18 | Electric | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8760 | 8760 | 0 | 0 | 50 | 300 | 1.5 | 2 | Warehouse | WarehouseOccupancy | WarehouseReceptacle | WarehouseServiceHotWater | WarehouseLights | WarehouseGasEquip | WarehouseRefrigeration | WarehouseInfiltration | WarehouseHVACAvail | WarehouseHtgSetpt | WarehouseClgSetpt | WarehouseElevator | WarehouseEscalator | WarehouseWtrHtrSetpt | 366 | 1 | 0 | 0 | CommercialIndustrialStorageShipping | NA | Warehouse | ;
| Storage, General | Misc - All others | 0 | 0.5 | 250 | 200 | 0.2 | 0 | Electric | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8760 | 8760 | 0 | 0 | 50 | 300 | 1.5 | 2 | Warehouse | WarehouseOccupancy | WarehouseReceptacle | WarehouseServiceHotWater | WarehouseLights | WarehouseGasEquip | WarehouseRefrigeration | WarehouseInfiltration | WarehouseHVACAvail | WarehouseHtgSetpt | WarehouseClgSetpt | WarehouseElevator | WarehouseEscalator | WarehouseWtrHtrSetpt | 380 | 1 | 1 | 0 | GeneralStorage | NA | default by predominance | ;
| Sports Arena - Playing Area (> 5,000 Spectators) | Sports/Entertainment - Gym, sports arena (play area) | 80 | 0.5 | 255 | 875 | 0.5 | 0.18 | Gas | 2.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 150 | 400 | 1.5 | 2 | Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt | 367 | 0 | 0 | 0 | SportsArenaSeatsGTE5000ClassI | NA | none | ; | Sports Arena - Playing Area (> 5,000 Spectators)
| Sports Arena - Playing Area (2,000 - 5,000 Spectators) | Sports/Entertainment - Gym, sports arena (play area) | 66.67 | 0.5 | 255 | 875 | 0.5 | 0.18 | Gas | 1.45 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 150 | 400 | 1.5 | 2 | Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt | 368 | 0 | 0 | 0 | SportsArenaSeatsLT5000ClassII | NA | none | ; | Sports Arena - Playing Area (2,000 - 5,000 Spectators)
| Sports Arena - Playing Area (< 2,000 Spectators) | Sports/Entertainment - Gym, sports arena (play area) | 50 | 0.5 | 255 | 875 | 0.5 | 0.18 | Gas | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 150 | 400 | 1.5 | 2 | Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt | 369 | 0 | 0 | 0 | SportsArenaSeatsLT2000ClassIII | NA | none | ; | Sports Arena - Playing Area (< 2,000 Spectators)
| Sports Arena - Playing Area (Recreational) | Sports/Entertainment - Gym, sports arena (play area) | 20 | 0.5 | 255 | 875 | 0.2 | 0.9 | Gas | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 150 | 400 | 1.5 | 2 | Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt | 370 | 1 | 0 | 0 | SportsArenaSeatsLimitedClassIV | NA | Sports, Recreation | ;
| Theater Area (Motion Picture) | Assembly - Auditorium seating area | 142.86 | 0.5 | 245 | 105 | 0.5 | 0.09 | Electric | 0.5 | 0 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 2 | 50 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | 371 | 1 | 0 | 0 | TheaterMotionPicture | MotionPictureTheater | Other | ;
| Theater Area (Performance) | Sports/Entertainment - Stages, studios | 142.86 | 0.5 | 245 | 105 | 0.5 | 0.09 | Gas | 0.8 | 0 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 2 | 200 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | 372 | 1 | 0 | 1 | TheaterPerformance | PerformanceTheater | Other | ;
| Transportation Function (Baggage Area) | Misc - Transportation waiting | 33.33 | 0.5 | 250 | 250 | 0.5 | 0.18 | Electric | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 50 | 500 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | 373 | 0 | 0 | 0 | TransportationFunctionConcourseBaggage | NA | none | ; | Transportation Function (Baggage Area)
| Transportation Function (Ticketing Area) | Misc - Transportation waiting | 33.33 | 0.5 | 250 | 250 | 0.5 | 0.18 | Electric | 0.45 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 50 | 500 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | 374 | 0 | 0 | 0 | TransportationFunctionTicketing | NA | none | ; | Transportation Function (Ticketing Area)
| Unleased Tenant Area | Office - Office space | 10 | 0.5 | 250 | 200 | 1.5 | 0.18 | Electric | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 75 | 500 | 1 | 4 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | 375 | 1 | 0 | 1 | UnleasedTenantArea | NA | Office, Financial, Unleased, Med Office/Clinic | ;
| Unoccupied-Exclude from Gross Floor Area | NA | 0 | 0.5 | 250 | 250 | 0 | 0 | Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8760 | 8760 | 0 | 0 | 0 | 0 | 0 | 0 | Unoccupied | UnoccupiedOccupancy | UnoccupiedReceptacle | UnoccupiedServiceHotWater | UnoccupiedLights | UnoccupiedGasEquip | UnoccupiedRefrigeration | UnoccupiedInfiltration | UnoccupiedHVACAvail | UnoccupiedHtgSetpt | UnoccupiedClgSetpt | UnoccupiedElevator | UnoccupiedEscalator | UnoccupiedWtrHtrSetpt | 376 | 1 | 1 | 0 | UnoccupiedExcludeInGrossFloorArea | NA | none | ;
| Unoccupied-Include in Gross Floor Area | NA | 0 | 0.5 | 250 | 250 | 0 | 0 | Gas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8760 | 8760 | 0 | 0 | 0 | 0 | 0 | 0 | Unoccupied | UnoccupiedOccupancy | UnoccupiedReceptacle | UnoccupiedServiceHotWater | UnoccupiedLights | UnoccupiedGasEquip | UnoccupiedRefrigeration | UnoccupiedInfiltration | UnoccupiedHVACAvail | UnoccupiedHtgSetpt | UnoccupiedClgSetpt | UnoccupiedElevator | UnoccupiedEscalator | UnoccupiedWtrHtrSetpt | 377 | 1 | 1 | 0 | UnoccupiedIncludeInGrossFloorArea | NA | default by predominance | ;
| Videoconferencing Studio | General - Conference/meeting | 10 | 0.5 | 250 | 200 | 1.5 | 0.18 | Electric | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 300 | 300 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | 378 | 1 | 0 | 0 | VideoConferencingStudio | NA | default by predominance | ;
| All other | Misc - All others | 10 | 0.5 | 250 | 200 | 1 | 0.18 | Gas | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 100 | 300 | 1.5 | 2 | Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt | 301 | 1 | 0 | 1 | AllOthersSpace | NA | none | ;
| Conference, Multipurpose and Meeting Area | General - Conference/meeting | 66.67 | 0.5 | 245 | 155 | 1 | 0.09 | Electric | 0.75 | 0 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2.35 | 2.66 | 0.3 | 0.35 | 0.4 | 0 | 150 | 150 | 0 | 0 | 30 | 300 | 1.5 | 2 | Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt | 381 | 1 | 0 | 1 | ConferenceMultipurposeMeetingCenterArea | MultipurposeArea | default by predominance | ;
| Storage | Misc - All others | 0 | 0.5 | 250 | 200 | 0.2 | 0 | Electric | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8760 | 8760 | 0 | 0 | 50 | 300 | 1.5 | 2 | Warehouse | WarehouseOccupancy | WarehouseReceptacle | WarehouseServiceHotWater | WarehouseLights | WarehouseGasEquip | WarehouseRefrigeration | WarehouseInfiltration | WarehouseHVACAvail | WarehouseHtgSetpt | WarehouseClgSetpt | WarehouseElevator | WarehouseEscalator | WarehouseWtrHtrSetpt | 379 | 0 | 1 | 0 | Storage | NA | default by predominance | ;
| Health Care / Assisted Living (Nurse's Station) | Misc - All others | 10 | 0.5 | 250 | 200 | 1.5 | 0.24 | Gas | 0.85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 75 | 500 | 1.5 | 2 | ResidentialCommon | ResidentialCommonOccupancy | ResidentialCommonReceptacle | ResidentialCommonServiceHotWater | ResidentialCommonLights | ResidentialCommonGasEquip | ResidentialCommonRefrigeration | ResidentialCommonInfiltration | ResidentialCommonHVACAvail | ResidentialCommonHtgSetpt | ResidentialCommonClgSetpt | ResidentialCommonElevator | ResidentialCommonEscalator | ResidentialCommonWtrHtrSetpt | 382 | 0 | 0 | 0 | AssistedLivingNurseStation | NA | Highrise Multifamily | ;
| Health Care / Assisted Living (Physical Therapy Room) | Misc - All others | 10 | 0.5 | 250 | 200 | 1.5 | 0.24 | Electric | 0.75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 150 | 0 | 0 | 75 | 500 | 1.5 | 2 | ResidentialCommon | ResidentialCommonOccupancy | ResidentialCommonReceptacle | ResidentialCommonServiceHotWater | ResidentialCommonLights | ResidentialCommonGasEquip | ResidentialCommonRefrigeration | ResidentialCommonInfiltration | ResidentialCommonHVACAvail | ResidentialCommonHtgSetpt | ResidentialCommonClgSetpt | ResidentialCommonElevator | ResidentialCommonEscalator | ResidentialCommonWtrHtrSetpt | 383 | 0 | 0 | 0 | AssistedLivingPhysicalTherapy | NA | Highrise Multifamily | ;
ENDTABLE
//
[40 empty] | Occupancy | Receptacle | ServiceHotWater | Lights | GasEquip | Refrigeration | Infiltration | HVACAvail | HtgSetpt | ClgSetpt | Elevator | Escalator | WtrHtrSetpt

## For CSV - 2019 VentSpcFuncData (hidden)
// This table pasted into App5-4C_Ventilation-T24N_2019.csv
TABLE VentilationSpaceFunctionData
| VentFuncType | CodeVentPerArea | CodeVentPerAreaForDCV | CodeExhContPerFixture | CodeExhIntrmtPerFixture | CodeExhPerArea | AirClass | VentShutoffOccSens | CodeVentPerPerson | VentOccDensSim | VentSpcFuncIdx
| // | Area Outdoor Air Rate, Ra | Min Air Rate for DCV | Continuous Exhaust Rate, | Intermittent Exhaust Rate, | Exhaust Rate, | Air Class | Notes | Person Outdoor Air Rate, Rp | Occ Density for Ra | For enums | ;
| // | cfm/ft2 | cfm/ft2 | cfm/unit | cfm/unit | cfm/ft² |  |  | cfm/person | people/1000ft2 |  | ;
| Assembly - Auditorium seating area | 1.07 | 0.15 | 0 | 0 | 0 | 1 | 1 | 15 | 71.3333 | 1 | ;
| Assembly - Courtrooms | 0.19 | 0.15 | 0 | 0 | 0 | 1 | 1 | 15 | 12.6667 | 2 | ;
| Assembly - Legislative chambers | 0.19 | 0.15 | 0 | 0 | 0 | 1 | 1 | 15 | 12.6667 | 3 | ;
| Assembly - Libraries (reading rooms and stack areas) | 0.15 | 0.15 | 0 | 0 | 0 | 1 | 0 | 15 | 0 | 4 | ;
| Assembly - Lobbies | 0.5 | 0.15 | 0 | 0 | 0 | 1 | 1 | 15 | 33.3333 | 5 | ;
| Assembly - Museums (childrens) | 0.25 | 0.15 | 0 | 0 | 0 | 1 | 0 | 15 | 16.6667 | 6 | ;
| Assembly - Museums/galleries | 0.25 | 0.15 | 0 | 0 | 0 | 1 | 1 | 15 | 16.6667 | 7 | ;
| Assembly - Places of religious worship | 1.07 | 0.15 | 0 | 0 | 0 | 1 | 1 | 15 | 71.3333 | 8 | ;
| Education - Art classroom | 0.15 | 0.15 | 0 | 0 | 0.7 | 2 | 0 | 15 | 0 | 9 | ;
| Education - Classrooms (ages 9-18) | 0.38 | 0.15 | 0 | 0 | 0 | 1 | 0 | 15 | 25.3333 | 10 | ;
| Education - Classrooms (ages 5-8) | 0.38 | 0.15 | 0 | 0 | 0 | 1 | 0 | 15 | 25.3333 | 11 | ;
| Education - Computer lab | 0.15 | 0.15 | 0 | 0 | 0 | 1 | 0 | 15 | 0 | 12 | ;
| Education - Daycare (through age 4) | 0.21 | 0.15 | 0 | 0 | 0 | 2 | 0 | 15 | 14 | 13 | ;
| Education - Daycare sickroom | 0.15 | 0.15 | 0 | 0 | 0 | 3 | 0 | 15 | 0 | 14 | ;
| Education - Lecture hall (fixed seats) | 0 | 0.15 | 0 | 0 | 0 | 1 | 1 | 15 | 0 | 15 | ;
| Education - Lecture/postsecondary classroom | 0.38 | 0.15 | 0 | 0 | 0 | 1 | 1 | 15 | 25.3333 | 16 | ;
| Education - Media center | 0.15 | 0.15 | 0 | 0 | 0 | 1 | 0 | 15 | 0 | 17 | ;
| Education - Metal shop | 0.15 | 0.15 | 0 | 0 | 0 | 2 | 0 | 15 | 0 | 18 | ;
| Education - Multiuse assembly | 0.5 | 0.15 | 0 | 0 | 0 | 1 | 1 | 15 | 33.3333 | 19 | ;
| Education - Music/theater/dance | 1.07 | 0.15 | 0 | 0 | 0 | 1 | 1 | 15 | 71.3333 | 20 | ;
| Education - Science laboratories | 0.15 | 0.15 | 0 | 0 | 1 | 2 | 0 | 15 | 0 | 21 | ;
| Education - University/college laboratories | 0.15 | 0.15 | 0 | 0 | 1 | 2 | 0 | 15 | 0 | 22 | ;
| Education - Wood shop | 0.15 | 0.15 | 0 | 0 | 0.5 | 2 | 0 | 15 | 0 | 23 | ;
| Exhaust - All other locker rooms | 0 | 0 | 0 | 0 | 0.25 | 2 | 0 | 0 | 0 | 24 | ;
| Exhaust - Arenas | 0 | 0 | 0 | 0 | 0.5 | 1 | 0 | 0 | 0 | 25 | ;
| Exhaust - Auto repair rooms | 0 | 0 | 0 | 0 | 1.5 | 2 | 0 | 0 | 0 | 26 | ;
| Exhaust - Cells with toilet | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 27 | ;
| Exhaust - Copy, printing rooms | 0 | 0 | 0 | 0 | 0.5 | 2 | 0 | 0 | 0 | 28 | ;
| Exhaust - Darkrooms | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 29 | ;
| Exhaust - Janitor closets, trash rooms, recycling | 0 | 0 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 30 | ;
| Exhaust - Kitchenettes | 0 | 0 | 0 | 0 | 0.3 | 2 | 0 | 0 | 0 | 31 | ;
| Exhaust - Locker rooms for athletic or industrial facilities | 0 | 0 | 0 | 0 | 0.5 | 2 | 0 | 0 | 0 | 32 | ;
| Exhaust - Paint spray booths | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 33 | ;
| Exhaust - Parking garages | 0 | 0 | 0 | 0 | 0.75 | 2 | 0 | 0 | 0 | 34 | ;
| Exhaust - Refrigerating machinery rooms | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 35 | ;
| Exhaust - Shower rooms | 0 | 0 | 20 | 50 | 0 | 2 | 0 | 0 | 0 | 36 | ;
| Exhaust - Soiled laundry storage rooms | 0 | 0 | 0 | 0 | 1 | 3 | 0 | 0 | 0 | 37 | ;
| Exhaust - Storage rooms, chemical | 0 | 0 | 0 | 0 | 1.5 | 4 | 0 | 0 | 0 | 38 | ;
| Exhaust - Toilets, private | 0 | 0 | 25 | 50 | 0 | 2 | 0 | 0 | 0 | 39 | ;
| Exhaust - Toilets, public | 0 | 0 | 50 | 0 | 0 | 2 | 0 | 0 | 0 | 40 | ;
| Exhaust - Woodwork shop/classrooms | 0 | 0 | 0 | 0 | 0.5 | 2 | 0 | 0 | 0 | 41 | ;
| Food Service - Bars, cocktail lounges | 0.5 | 0.2 | 0 | 0 | 0 | 2 | 0 | 15 | 33.3333 | 42 | ;
| Food Service - Cafeteria/fast-food dining | 0.5 | 0.15 | 0 | 0 | 0 | 2 | 0 | 15 | 33.3333 | 43 | ;
| Food Service - Kitchen (cooking) | 0.15 | 0.15 | 0 | 0 | 0.7 | 2 | 0 | 15 | 0 | 44 | ;
| Food Service - Restaurant dining rooms | 0.5 | 0.15 | 0 | 0 | 0 | 2 | 0 | 15 | 33.3333 | 45 | ;
| General - Break rooms | 0.5 | 0.15 | 0 | 0 | 0 | 1 | 1 | 15 | 33.3333 | 46 | ;
| General - Coffee Stations | 0.5 | 0.15 | 0 | 0 | 0 | 1 | 1 | 15 | 33.3333 | 47 | ;
| General - Conference/meeting | 0.5 | 0.15 | 0 | 0 | 0 | 1 | 1 | 15 | 33.3333 | 48 | ;
| General - Corridors | 0.15 | 0.15 | 0 | 0 | 0 | 1 | 1 | 15 | 0 | 49 | ;
| General - Occupiable storage rooms for liquids or gels | 0.15 | 0.15 | 0 | 0 | 0 | 2 | 0 | 15 | 0 | 50 | ;
| General - Unoccupied | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 51 | ;
| Lodging - Barracks sleeping areas | 0.15 | 0.15 | 0 | 0 | 0 | 1 | 1 | 15 | 0 | 52 | ;
| Lodging - Bedroom/living room | 0.15 | 0.15 | 0 | 0 | 0 | 1 | 1 | 15 | 0 | 53 | ;
| Lodging - Laundry rooms within dwelling units | 0.15 | 0.15 | 0 | 0 | 0 | 1 | 0 | 15 | 0 | 54 | ;
| Lodging - Laundry rooms, central | 0.15 | 0.15 | 0 | 0 | 0 | 2 | 0 | 15 | 0 | 55 | ;
| Lodging - Lobbies/pre-function | 0.5 | 0.15 | 0 | 0 | 0 | 1 | 1 | 15 | 33.3333 | 56 | ;
| Lodging - Multipurpose assembly | 0.5 | 0.15 | 0 | 0 | 0 | 1 | 1 | 15 | 33.3333 | 57 | ;
| Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 | 0 | 15 | 0 | 58 | ;
| Misc - Bank vaults/safe deposit | 0.15 | 0.15 | 0 | 0 | 0 | 2 | 1 | 15 | 0 | 59 | ;
| Misc - Banks or bank lobbies | 0.15 | 0.15 | 0 | 0 | 0 | 1 | 1 | 15 | 0 | 60 | ;
| Misc - Computer (not printing) | 0.15 | 0.15 | 0 | 0 | 0 | 1 | 1 | 15 | 0 | 61 | ;
| Misc - Freezer and refrigerated spaces (<50F) | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 62 | ;
| Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 0.15 | 0.15 | 0 | 0 | 0 | 3 | 0 | 15 | 0 | 63 | ;
| Misc - Pharmacy (preparation area) | 0.15 | 0.15 | 0 | 0 | 0 | 2 | 0 | 15 | 0 | 64 | ;
| Misc - Photo studios | 0.15 | 0.15 | 0 | 0 | 0 | 1 | 0 | 15 | 0 | 65 | ;
| Misc - Shipping/receiving | 0.15 | 0.15 | 0 | 0 | 0 | 2 | 0 | 15 | 0 | 66 | ;
| Misc - Sorting, packing, light assembly | 0.15 | 0.15 | 0 | 0 | 0 | 2 | 0 | 15 | 0 | 67 | ;
| Misc - Telephone closets | 0.15 | 0.15 | 0 | 0 | 0 | 1 | 0 | 15 | 0 | 68 | ;
| Misc - Transportation waiting | 0.5 | 0.15 | 0 | 0 | 0 | 1 | 1 | 15 | 33.3333 | 69 | ;
| Misc - Warehouses | 0.15 | 0.15 | 0 | 0 | 0 | 2 | 0 | 15 | 0 | 70 | ;
| Office - Breakrooms | 0.5 | 0.15 | 0 | 0 | 0 | 1 | 0 | 15 | 33.3333 | 71 | ;
| Office - Main entry lobbies | 0.5 | 0.15 | 0 | 0 | 0 | 1 | 1 | 15 | 33.3333 | 72 | ;
| Office - Occupiable storage rooms for dry materials | 0.15 | 0.15 | 0 | 0 | 0 | 1 | 0 | 15 | 0 | 73 | ;
| Office - Office space | 0.15 | 0.15 | 0 | 0 | 0 | 1 | 1 | 15 | 0 | 74 | ;
| Office - Reception areas | 0.15 | 0.15 | 0 | 0 | 0 | 1 | 1 | 15 | 0 | 75 | ;
| Office - Telephone/data entry | 0.15 | 0.15 | 0 | 0 | 0 | 1 | 1 | 15 | 0 | 76 | ;
| Residential - Common corridors | 0.15 | 0.15 | 0 | 0 | 0 | 1 | 1 | 15 | 0 | 77 | ;
| Retail - Barbershop | 0.4 | 0.4 | 0 | 0 | 0.5 | 2 | 1 | 15 | 0 | 78 | ;
| Retail - Beauty and nail salons | 0.4 | 0.4 | 0 | 0 | 0.6 | 2 | 0 | 15 | 0 | 79 | ;
| Retail - Coin-operated laundries | 0.3 | 0.3 | 0 | 0 | 0 | 2 | 0 | 15 | 0 | 80 | ;
| Retail - Mall common areas | 0.25 | 0.15 | 0 | 0 | 0 | 1 | 1 | 15 | 16.6667 | 81 | ;
| Retail - Pet shops (animal areas) | 0.25 | 0.15 | 0 | 0 | 0.9 | 2 | 0 | 15 | 16.6667 | 82 | ;
| Retail - Sales | 0.25 | 0.2 | 0 | 0 | 0 | 2 | 0 | 15 | 16.6667 | 83 | ;
| Retail - Supermarket | 0.25 | 0.2 | 0 | 0 | 0 | 1 | 1 | 15 | 16.6667 | 84 | ;
| Sports/Entertainment - Bowling alley (seating) | 1.07 | 0.15 | 0 | 0 | 0 | 1 | 0 | 15 | 71.3333 | 85 | ;
| Sports/Entertainment - Disco/dance floors | 1.5 | 0.15 | 0 | 0 | 0 | 2 | 1 | 15 | 100 | 86 | ;
| Sports/Entertainment - Gambling casinos | 0.68 | 0.15 | 0 | 0 | 0 | 1 | 0 | 15 | 45.3333 | 87 | ;
| Sports/Entertainment - Game arcades | 0.68 | 0.15 | 0 | 0 | 0 | 1 | 0 | 15 | 45.3333 | 88 | ;
| Sports/Entertainment - Gym, sports arena (play area) | 0.5 | 0.15 | 0 | 0 | 0 | 2 | 0 | 15 | 33.3333 | 89 | ;
| Sports/Entertainment - Health club/aerobics room | 0.15 | 0.15 | 0 | 0 | 0 | 2 | 0 | 15 | 0 | 90 | ;
| Sports/Entertainment - Health club/weight rooms | 0.15 | 0.15 | 0 | 0 | 0 | 2 | 0 | 15 | 0 | 91 | ;
| Sports/Entertainment - Spectator areas | 0.5 | 0.15 | 0 | 0 | 0 | 1 | 1 | 15 | 33.3333 | 92 | ;
| Sports/Entertainment - Stages, studios | 0.5 | 0.15 | 0 | 0 | 0 | 1 | 1 | 15 | 33.3333 | 93 | ;
| Sports/Entertainment - Swimming (deck) | 0.5 | 0.15 | 0 | 0 | 0 | 2 | 0 | 15 | 33.3333 | 94 | ;
| Sports/Entertainment - Swimming (pool) | 0.15 | 0.15 | 0 | 0 | 0 | 2 | 0 | 15 | 0 | 95 | ;
| NA | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | ;
ENDTABLE
Note on D62: David: Was 0.5

## For CSV - 2025 VentSpcFuncData
// This table pasted into App5-4C_Ventilation-T24N_2025.csv
TABLE VentilationSpaceFunctionData
| VentFuncType | MinOccDens | CodeVentPerArea | CodeExhContPerFixture | CodeExhIntrmtPerFixture | CodeExhPerArea | AirClass | VentSpcFuncIdx
| // | Minimum Occ Density, Pz | Area Outdoor Air Rate, Ra | Continuous Exhaust Rate, | Intermittent Exhaust Rate, | Exhaust Rate, | Air Class | For enums | ;
| // | people/1000ft2 | cfm/ft2 | cfm/unit | cfm/unit | cfm/ft² |  |  | ;
| Assembly - Auditorium seating area | 7 | 0.15 | 0 | 0 | 0 | 1 | 1 | ;
| Assembly - Courtrooms | 13 | 0.15 | 0 | 0 | 0 | 1 | 2 | ;
| Assembly - Legislative chambers | 13 | 0.15 | 0 | 0 | 0 | 1 | 3 | ;
| Assembly - Libraries (reading rooms and stack areas) | 10 | 0.15 | 0 | 0 | 0 | 1 | 4 | ;
| Assembly - Lobbies | 33 | 0.15 | 0 | 0 | 0 | 1 | 5 | ;
| Assembly - Museums (childrens) | 17 | 0.15 | 0 | 0 | 0 | 1 | 6 | ;
| Assembly - Museums/galleries | 17 | 0.15 | 0 | 0 | 0 | 1 | 7 | ;
| Assembly - Places of religious worship | 7 | 0.15 | 0 | 0 | 0 | 1 | 8 | ;
| Education - Art classroom | 25 | 0.15 | 0 | 0 | 0.7 | 2 | 9 | ;
| Education - Classrooms (ages 9-18) | 25 | 0.15 | 0 | 0 | 0 | 1 | 10 | ;
| Education - Classrooms (ages 5-8) | 25 | 0.15 | 0 | 0 | 0 | 1 | 11 | ;
| Education - Computer lab | 25 | 0.15 | 0 | 0 | 0 | 1 | 12 | ;
| Education - Daycare (through age 4) | 14 | 0.15 | 0 | 0 | 0 | 2 | 13 | ;
| Education - Daycare sickroom | 5 | 0.15 | 0 | 0 | 0 | 3 | 14 | ;
| Education - Lecture hall (fixed seats) | 71 | 0.15 | 0 | 0 | 0 | 1 | 15 | ;
| Education - Lecture/postsecondary classroom | 25 | 0.15 | 0 | 0 | 0 | 1 | 16 | ;
| Education - Media center | 25 | 0.15 | 0 | 0 | 0 | 1 | 17 | ;
| Education - Metal shop | 10 | 0.15 | 0 | 0 | 0 | 2 | 18 | ;
| Education - Multiuse assembly | 33 | 0.15 | 0 | 0 | 0 | 1 | 19 | ;
| Education - Music/theater/dance | 33 | 0.15 | 0 | 0 | 0 | 1 | 20 | ;
| Education - Science laboratories | 25 | 0.15 | 0 | 0 | 1 | 2 | 21 | ;
| Education - University/college laboratories | 25 | 0.15 | 0 | 0 | 1 | 2 | 22 | ;
| Education - Wood shop | 10 | 0.15 | 0 | 0 | 0.5 | 2 | 23 | ;
| Exhaust - All other locker rooms | 0 | 0 | 0 | 0 | 0.25 | 2 | 24 | ;
| Exhaust - Animal imaging(MRI/CT/PET) | 0 | 0 | 0 | 0 | 0.9 | 3 | 97 | ;
| Exhaust - Animal operating rooms | 0 | 0 | 0 | 0 | 3 | 3 | 98 | ;
| Exhaust - Animal postoperative recovery room | 0 | 0 | 0 | 0 | 1.5 | 3 | 99 | ;
| Exhaust - Animal preparation rooms | 0 | 0 | 0 | 0 | 1.5 | 3 | 100 | ;
| Exhaust - Animal procedure room | 0 | 0 | 0 | 0 | 2.25 | 3 | 101 | ;
| Exhaust - Animal surgery scrub | 0 | 0 | 0 | 0 | 1.5 | 3 | 102 | ;
| Exhaust - Animal Necropsy | 0 | 0 | 0 | 0 | 2.25 | 3 | 103 | ;
| Exhaust - Arenas | 0 | 0 | 0 | 0 | 0.5 | 1 | 25 | ;
| Exhaust - Auto repair rooms | 0 | 0 | 0 | 0 | 1.5 | 2 | 26 | ;
| Exhaust - Cells with toilet | 0 | 0 | 0 | 0 | 1 | 2 | 27 | ;
| Exhaust - Copy, printing rooms | 0 | 0 | 0 | 0 | 0.5 | 2 | 28 | ;
| Exhaust - Darkrooms | 0 | 0 | 0 | 0 | 1 | 2 | 29 | ;
| Exhaust - Janitor closets, trash rooms, recycling | 0 | 0 | 0 | 0 | 1 | 3 | 30 | ;
| Exhaust - Kitchenettes | 0 | 0 | 0 | 0 | 0.3 | 2 | 31 | ;
| Exhaust - Large-animal holding room | 0 | 0 | 0 | 0 | 2.25 | 3 | 104 | ;
| Exhaust - Locker rooms for athletic or industrial facilities | 0 | 0 | 0 | 0 | 0.5 | 2 | 32 | ;
| Exhaust - Paint spray booths | 0 | 0 | 0 | 0 | 0 | 4 | 33 | ;
| Exhaust - Parking garages | 0 | 0 | 0 | 0 | 0.75 | 2 | 34 | ;
| Exhaust - Refrigerating machinery rooms | 0 | 0 | 0 | 0 | 0 | 3 | 35 | ;
| Exhaust - Shower rooms | 0 | 0 | 20 | 50 | 0 | 2 | 36 | ;
| Exhaust - Small-animal-cage room (static cages) | 0 | 0 | 0 | 0 | 2.25 | 3 | 105 | ;
| Exhaust - Small-animal-cage room (ventilated cages) | 0 | 0 | 0 | 0 | 1.5 | 3 | 106 | ;
| Exhaust - Soiled laundry storage rooms | 0 | 0 | 0 | 0 | 1 | 3 | 37 | ;
| Exhaust - Storage rooms, chemical | 0 | 0 | 0 | 0 | 1.5 | 4 | 38 | ;
| Exhaust - Toilets, private | 0 | 0 | 25 | 50 | 0 | 2 | 39 | ;
| Exhaust - Toilets, public | 0 | 0 | 50 | 70 | 0 | 2 | 40 | ;
| Exhaust - Woodwork shop/classrooms | 0 | 0 | 0 | 0 | 0.5 | 2 | 41 | ;
| Food Service - Bars, cocktail lounges | 33 | 0.2 | 0 | 0 | 0 | 2 | 42 | ;
| Food Service - Cafeteria/fast-food dining | 33 | 0.15 | 0 | 0 | 0 | 2 | 43 | ;
| Food Service - Kitchen (cooking) | 3 | 0.15 | 0 | 0 | 0.7 | 2 | 44 | ;
| Food Service - Restaurant dining rooms | 33 | 0.15 | 0 | 0 | 0 | 2 | 45 | ;
| General - Break rooms | 33 | 0.15 | 0 | 0 | 0 | 1 | 46 | ;
| General - Coffee Stations | 33 | 0.15 | 0 | 0 | 0 | 1 | 47 | ;
| General - Conference/meeting | 33 | 0.15 | 0 | 0 | 0 | 1 | 48 | ;
| General - Corridors | 5 | 0.15 | 0 | 0 | 0 | 1 | 49 | ;
| General - Occupiable storage rooms for liquids or gels | 2 | 0.15 | 0 | 0 | 0 | 2 | 50 | ;
| General - Unoccupied | 0 | 0 | 0 | 0 | 0 | 1 | 51 | ;
| Lodging - Barracks sleeping areas | 5 | 0.15 | 0 | 0 | 0 | 1 | 52 | ;
| Lodging - Bedroom/living room | 3 | 0.15 | 0 | 0 | 0 | 1 | 53 | ;
| Lodging - Laundry rooms within dwelling units | 5 | 0.15 | 0 | 0 | 0 | 1 | 54 | ;
| Lodging - Laundry rooms, central | 5 | 0.15 | 0 | 0 | 0 | 2 | 55 | ;
| Lodging - Lobbies/pre-function | 33 | 0.15 | 0 | 0 | 0 | 1 | 56 | ;
| Lodging - Multipurpose assembly | 33 | 0.15 | 0 | 0 | 0 | 1 | 57 | ;
| Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 | 58 | ;
| Misc - Bank vaults/safe deposit | 5 | 0.15 | 0 | 0 | 0 | 2 | 59 | ;
| Misc - Banks or bank lobbies | 5 | 0.15 | 0 | 0 | 0 | 1 | 60 | ;
| Misc - Computer (not printing) | 5 | 0.15 | 0 | 0 | 0 | 1 | 61 | ;
| Misc - Freezer and refrigerated spaces (<50F) | 0 | 0 | 0 | 0 | 0 | 2 | 62 | ;
| Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 5 | 0.15 | 0 | 0 | 0 | 3 | 63 | ;
| Misc - Pharmacy (preparation area) | 5 | 0.15 | 0 | 0 | 0 | 2 | 64 | ;
| Misc - Photo studios | 5 | 0.15 | 0 | 0 | 0 | 1 | 65 | ;
| Misc - Shipping/receiving | 5 | 0.15 | 0 | 0 | 0 | 2 | 66 | ;
| Misc - Sorting, packing, light assembly | 5 | 0.15 | 0 | 0 | 0 | 2 | 67 | ;
| Misc - Telephone closets | 5 | 0.4 | 0 | 0 | 0 | 1 | 68 | ;
| Misc - Transportation waiting | 33 | 0.4 | 0 | 0 | 0 | 1 | 69 | ;
| Misc - Warehouses | 1 | 0.3 | 0 | 0 | 0 | 2 | 70 | ;
| Office - Breakrooms | 33 | 0.15 | 0 | 0 | 0 | 1 | 71 | ;
| Office - Main entry lobbies | 33 | 0.15 | 0 | 0 | 0 | 1 | 72 | ;
| Office - Occupiable storage rooms for dry materials | 2 | 0.15 | 0 | 0 | 0 | 1 | 73 | ;
| Office - Office space | 5 | 0.15 | 0 | 0 | 0 | 1 | 74 | ;
| Office - Reception areas | 5 | 0.15 | 0 | 0 | 0 | 1 | 75 | ;
| Office - Telephone/data entry | 33 | 0.15 | 0 | 0 | 0 | 1 | 76 | ;
| Residential - Common corridors | 5 | 0.15 | 0 | 0 | 0 | 1 | 77 | ;
| Retail - Barbershop | 17 | 0.4 | 0 | 0 | 0.5 | 2 | 78 | ;
| Retail - Beauty and nail salons | 17 | 0.4 | 0 | 0 | 0.6 | 2 | 79 | ;
| Retail - Coin-operated laundries | 17 | 0.3 | 0 | 0 | 0 | 2 | 80 | ;
| Retail - Mall common areas | 17 | 0.15 | 0 | 0 | 0 | 1 | 81 | ;
| Retail - Pet shops (animal areas) | 17 | 0.2 | 0 | 0 | 0.9 | 2 | 82 | ;
| Retail - Sales | 17 | 0.2 | 0 | 0 | 0 | 2 | 83 | ;
| Retail - Supermarket | 17 | 0.2 | 0 | 0 | 0 | 1 | 84 | ;
| Sports/Entertainment - Bowling alley (seating) | 7 | 0.15 | 0 | 0 | 0 | 1 | 85 | ;
| Sports/Entertainment - Disco/dance floors | 100 | 0.15 | 0 | 0 | 0 | 2 | 86 | ;
| Sports/Entertainment - Gambling casinos | 45 | 0.15 | 0 | 0 | 0 | 1 | 87 | ;
| Sports/Entertainment - Game arcades | 45 | 0.15 | 0 | 0 | 0 | 1 | 88 | ;
| Sports/Entertainment - Gym, sports arena (play area) | 10 | 0.15 | 0 | 0 | 0 | 2 | 89 | ;
| Sports/Entertainment - Health club/aerobics room | 10 | 0.15 | 0 | 0 | 0 | 2 | 90 | ;
| Sports/Entertainment - Health club/weight rooms | 10 | 0.15 | 0 | 0 | 0 | 2 | 91 | ;
| Sports/Entertainment - Spectator areas | 33 | 0.15 | 0 | 0 | 0 | 1 | 92 | ;
| Sports/Entertainment - Stages, studios | 33 | 0.15 | 0 | 0 | 0 | 1 | 93 | ;
| Sports/Entertainment - Swimming (deck) | 33 | 0.15 | 0 | 0 | 0 | 2 | 94 | ;
| Sports/Entertainment - Swimming (pool) | 10 | 0.15 | 0 | 0 | 0 | 2 | 95 | ;
| NA | 0 | 0 | 0 | 0 | 0 | 0 | 96 | ;
ENDTABLE

## 19 SpcFunc & VentSpcFunc combos (hidden)
Text File Generation
[15 empty] | 0.03 |  |  |  |  | 1, Spc:SpcFunc, | , | ;
[20 empty] | 2, | , "
For Rules
2019 NACM Space Type | Allowed Ventilation Space Type (Default in Bold Red) | Area Outdoor Air Rate Ra | Min Air Rate for DCVb | Continuous Exhaust Rate, | Intermittent Exhaust Rate, | Exhaust Rate, | Air Class | Notes | Baseline ventilation = proposed? | SpcOccDensSim | VentOccDensSim | VentOccDensSim used in rules | VentSpcFunc, Rp assumed for Design Ra | VentSpcFunc Rp_adj, Adjusted for Spc | Calculated Ra based on Rp_Adj at design occupancy | For TABLE ValidVentilationSpaceFunctionEnumerations look-up | SpcFuncIdx - 2019 | VentSpcFuncIdx | SpcFuncIdx
SpcFunc | VentSpcFunc | cfm/ft² | cfm/ft² | cfm/unit | cfm/unit | cfm/ft² |  |  |  | # per 1000 ft² | # per 1000 ft² | # per 1000 ft² | cfm/person | cfm/person | cfm/ft2 |  |  |  |  | 0, Spc:VentSpcFunc, 0
All other | Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | All other,Misc - All others | #REF! | 58 | #REF! | #REF!
All other | General - Unoccupied | 0 | 0 | 0 | 0 | 0 | 1 |  | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | All other,General - Unoccupied | #REF! | 51 | #REF! | 2, 51, "General - Unoccupied"
All other | Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | All other,Misc - All others | #REF! | 58 | #REF! | 2, 58, "Misc - All others"
All other | Exhaust - Cells with toilet | 0 | 0 | 0 | 0 | 1 | 2 |  | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | All other,Exhaust - Cells with toilet | #REF! | 27 | #REF! | 2, 27, "Exhaust - Cells with toilet"
All other | Sports/Entertainment - Game arcades | 0.68 | 0.15 | 0 | 0 | 0 | 1 |  | No | #REF! | 45.3333 | 45.3333 | 15 | #REF! | #REF! | All other,Sports/Entertainment - Game arcades | #REF! | 88 | #REF! | 2, 88, "Sports/Entertainment - Game arcades"
Audience Seating Area | Assembly - Auditorium seating area | 1.07 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 71.3333 | 71.3333 | 15 | #REF! | #REF! | Audience Seating Area,Assembly - Auditorium seating area | #REF! | 1 | #REF! | #REF!
Audience Seating Area | Assembly - Auditorium seating area | 1.07 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 71.3333 | 71.3333 | 15 | #REF! | #REF! | Audience Seating Area,Assembly - Auditorium seating area | #REF! | 1 | #REF! | 2, 1, "Assembly - Auditorium seating area"
Audience Seating Area | Assembly - Courtrooms | 0.19 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 12.6667 | 12.6667 | 15 | #REF! | #REF! | Audience Seating Area,Assembly - Courtrooms | #REF! | 2 | #REF! | 2, 2, "Assembly - Courtrooms"
Audience Seating Area | Assembly - Legislative chambers | 0.19 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 12.6667 | 12.6667 | 15 | #REF! | #REF! | Audience Seating Area,Assembly - Legislative chambers | #REF! | 3 | #REF! | 2, 3, "Assembly - Legislative chambers"
Audience Seating Area | Exhaust - Arenas | 0 | 0 | 0 | 0 | 0.5 | 1 | Exh. Note B | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Audience Seating Area,Exhaust - Arenas | #REF! | 25 | #REF! | 2, 25, "Exhaust - Arenas"
Audience Seating Area | Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Audience Seating Area,Misc - All others | #REF! | 58 | #REF! | 2, 58, "Misc - All others"
Audience Seating Area | Sports/Entertainment - Bowling alley (seating) | 1.07 | 0.15 | 0 | 0 | 0 | 1 |  | No | #REF! | 71.3333 | 71.3333 | 15 | #REF! | #REF! | Audience Seating Area,Sports/Entertainment - Bowling alley (seating) | #REF! | 85 | #REF! | 2, 85, "Sports/Entertainment - Bowling alley (seating)"
Audience Seating Area | Sports/Entertainment - Spectator areas | 0.5 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Audience Seating Area,Sports/Entertainment - Spectator areas | #REF! | 92 | #REF! | 2, 92, "Sports/Entertainment - Spectator areas"
Auditorium Area | Assembly - Auditorium seating area | 1.07 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 71.3333 | 71.3333 | 15 | #REF! | #REF! | Auditorium Area,Assembly - Auditorium seating area | #REF! | 1 | #REF! | #REF!
Auditorium Area | Assembly - Auditorium seating area | 1.07 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 71.3333 | 71.3333 | 15 | #REF! | #REF! | Auditorium Area,Assembly - Auditorium seating area | #REF! | 1 | #REF! | 2, 1, "Assembly - Auditorium seating area"
Auditorium Area | Assembly - Courtrooms | 0.19 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 12.6667 | 12.6667 | 15 | #REF! | #REF! | Auditorium Area,Assembly - Courtrooms | #REF! | 2 | #REF! | 2, 2, "Assembly - Courtrooms"
Auditorium Area | Assembly - Legislative chambers | 0.19 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 12.6667 | 12.6667 | 15 | #REF! | #REF! | Auditorium Area,Assembly - Legislative chambers | #REF! | 3 | #REF! | 2, 3, "Assembly - Legislative chambers"
Auditorium Area | Exhaust - Arenas | 0 | 0 | 0 | 0 | 0.5 | 1 | Exh. Note B | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Auditorium Area,Exhaust - Arenas | #REF! | 25 | #REF! | 2, 25, "Exhaust - Arenas"
Auditorium Area | Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Auditorium Area,Misc - All others | #REF! | 58 | #REF! | 2, 58, "Misc - All others"
Auto Repair / Maintenance Area | Exhaust - Auto repair rooms | 0 | 0 | 0 | 0 | 1.5 | 2 | Exh. Note A | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Auto Repair / Maintenance Area,Exhaust - Auto repair rooms | #REF! | 26 | #REF! | #REF!
Auto Repair / Maintenance Area | Exhaust - Auto repair rooms | 0 | 0 | 0 | 0 | 1.5 | 2 | Exh. Note A | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Auto Repair / Maintenance Area,Exhaust - Auto repair rooms | #REF! | 26 | #REF! | 2, 26, "Exhaust - Auto repair rooms"
Beauty Salon Area | Retail - Beauty and nail salons | 0.4 | 0.4 | 0 | 0 | 0.6 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Beauty Salon Area,Retail - Beauty and nail salons | #REF! | 79 | #REF! | #REF!
Beauty Salon Area | Retail - Barbershop | 0.4 | 0.4 | 0 | 0 | 0.5 | 2 | F | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Beauty Salon Area,Retail - Barbershop | #REF! | 78 | #REF! | 2, 78, "Retail - Barbershop"
Beauty Salon Area | Retail - Beauty and nail salons | 0.4 | 0.4 | 0 | 0 | 0.6 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Beauty Salon Area,Retail - Beauty and nail salons | #REF! | 79 | #REF! | 2, 79, "Retail - Beauty and nail salons"
Civic Meeting Place Area | Assembly - Legislative chambers | 0.19 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 12.6667 | 12.6667 | 15 | #REF! | #REF! | Civic Meeting Place Area,Assembly - Legislative chambers | #REF! | 3 | #REF! | #REF!
Civic Meeting Place Area | Assembly - Auditorium seating area | 1.07 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 71.3333 | 71.3333 | 15 | #REF! | #REF! | Civic Meeting Place Area,Assembly - Auditorium seating area | #REF! | 1 | #REF! | 2, 1, "Assembly - Auditorium seating area"
Civic Meeting Place Area | Assembly - Courtrooms | 0.19 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 12.6667 | 12.6667 | 15 | #REF! | #REF! | Civic Meeting Place Area,Assembly - Courtrooms | #REF! | 2 | #REF! | 2, 2, "Assembly - Courtrooms"
Civic Meeting Place Area | Assembly - Legislative chambers | 0.19 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 12.6667 | 12.6667 | 15 | #REF! | #REF! | Civic Meeting Place Area,Assembly - Legislative chambers | #REF! | 3 | #REF! | 2, 3, "Assembly - Legislative chambers"
Civic Meeting Place Area | General - Conference/meeting | 0.5 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Civic Meeting Place Area,General - Conference/meeting | #REF! | 48 | #REF! | 2, 48, "General - Conference/meeting"
Civic Meeting Place Area | Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Civic Meeting Place Area,Misc - All others | #REF! | 58 | #REF! | 2, 58, "Misc - All others"
Classroom, Lecture, Training, Vocational Areas | Education - Classrooms (ages 9-18) | 0.38 | 0.15 | 0 | 0 | 0 | 1 |  | No | #REF! | 25.3333 | 25.3333 | 15 | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Education - Classrooms (ages 9-18) | #REF! | 10 | #REF! | #REF!
Classroom, Lecture, Training, Vocational Areas | Education - Art classroom | 0.15 | 0.15 | 0 | 0 | 0.7 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Education - Art classroom | #REF! | 9 | #REF! | 2, 9, "Education - Art classroom"
Classroom, Lecture, Training, Vocational Areas | Education - Classrooms (ages 9-18) | 0.38 | 0.15 | 0 | 0 | 0 | 1 |  | No | #REF! | 25.3333 | 25.3333 | 15 | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Education - Classrooms (ages 9-18) | #REF! | 10 | #REF! | 2, 10, "Education - Classrooms (ages 9-18)"
Classroom, Lecture, Training, Vocational Areas | Education - Classrooms (ages 5-8) | 0.15 | 0.15 | 0 | 0 | 0.7 | 2 |  | No | #REF! | 25.3333 | 25.3333 | 15 | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Education - Classrooms (ages 5-8) | #REF! | 11 | #REF! | 2, 11, "Education - Classrooms (ages 5-8)"
Classroom, Lecture, Training, Vocational Areas | Education - Computer lab | 0.15 | 0.15 | 0 | 0 | 0 | 1 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Education - Computer lab | #REF! | 12 | #REF! | 2, 12, "Education - Computer lab"
Classroom, Lecture, Training, Vocational Areas | Education - Daycare (through age 4) | 0.21 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 14 | 14 | 15 | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Education - Daycare (through age 4) | #REF! | 13 | #REF! | 2, 13, "Education - Daycare (through age 4)"
Classroom, Lecture, Training, Vocational Areas | Education - Daycare sickroom | 0.15 | 0.15 | 0 | 0 | 0 | 3 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Education - Daycare sickroom | #REF! | 14 | #REF! | 2, 14, "Education - Daycare sickroom"
Classroom, Lecture, Training, Vocational Areas | Education - Lecture hall (fixed seats) | 0 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Education - Lecture hall (fixed seats) | #REF! | 15 | #REF! | 2, 15, "Education - Lecture hall (fixed seats)"
Classroom, Lecture, Training, Vocational Areas | Education - Lecture/postsecondary classroom | 0.38 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 25.3333 | 25.3333 | 15 | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Education - Lecture/postsecondary classroom | #REF! | 16 | #REF! | 2, 16, "Education - Lecture/postsecondary classroom"
Classroom, Lecture, Training, Vocational Areas | Education - Media center | 0.15 | 0.15 | 0 | 0 | 0 | 1 | A | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Education - Media center | #REF! | 17 | #REF! | 2, 17, "Education - Media center"
Classroom, Lecture, Training, Vocational Areas | Education - Multiuse assembly | 0.5 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Education - Multiuse assembly | #REF! | 19 | #REF! | 2, 19, "Education - Multiuse assembly"
Classroom, Lecture, Training, Vocational Areas | Education - Music/theater/dance | 1.07 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | #N/A | #N/A | #N/A | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Education - Music/theater/dance | #REF! | #N/A | #REF! | #N/A
Classroom, Lecture, Training, Vocational Areas | Education - Science laboratories | 0.15 | 0.15 | 0 | 0 | 1 | 2 |  | Yes | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Education - Science laboratories | #REF! | 21 | #REF! | 2, 21, "Education - Science laboratories"
Classroom, Lecture, Training, Vocational Areas | Education - University/college laboratories | 0.15 | 0.15 | 0 | 0 | 1 | 2 |  | Yes | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Education - University/college laboratories | #REF! | 22 | #REF! | 2, 22, "Education - University/college laboratories"
Classroom, Lecture, Training, Vocational Areas | Education - Wood shop | 0.15 | 0.15 | 0 | 0 | 0.5 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Education - Wood shop | #REF! | 23 | #REF! | 2, 23, "Education - Wood shop"
Classroom, Lecture, Training, Vocational Areas | Education - Metal shop | 0.15 | 0.15 | 0 | 0 | 0 | 2 | 0 | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Education - Metal shop | #REF! | 18 | #REF! | 2, 18, "Education - Metal shop"
Classroom, Lecture, Training, Vocational Areas | Exhaust - Auto repair rooms | 0 | 0 | 0 | 0 | 1.5 | 2 | Exh. Note A | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Exhaust - Auto repair rooms | #REF! | 26 | #REF! | 2, 26, "Exhaust - Auto repair rooms"
Classroom, Lecture, Training, Vocational Areas | Exhaust - Woodwork shop/classrooms | 0 | 0 | 0 | 0 | 0.5 | 2 | 0 | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Exhaust - Woodwork shop/classrooms | #REF! | 41 | #REF! | 2, 41, "Exhaust - Woodwork shop/classrooms"
Classroom, Lecture, Training, Vocational Areas | Food Service - Kitchen (cooking) | 0.15 | 0.15 | 0 | 0 | 0.7 | 2 |  | Yes | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Food Service - Kitchen (cooking) | #REF! | 44 | #REF! | 2, 44, "Food Service - Kitchen (cooking)"
Classroom, Lecture, Training, Vocational Areas | Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Misc - All others | #REF! | 58 | #REF! | 2, 58, "Misc - All others"
Classroom, Lecture, Training, Vocational Areas | Retail - Barbershop | 0.4 | 0.4 | 0 | 0 | 0.5 | 2 | F | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Retail - Barbershop | #REF! | 78 | #REF! | 2, 78, "Retail - Barbershop"
Classroom, Lecture, Training, Vocational Areas | Retail - Beauty and nail salons | 0.4 | 0.4 | 0 | 0 | 0.6 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Retail - Beauty and nail salons | #REF! | 79 | #REF! | 2, 79, "Retail - Beauty and nail salons"
Commercial/Industrial Storage (Refrigerated) | Misc - Freezer and refrigerated spaces (<50F) | 0 | 0 | 0 | 0 | 0 | 2 | E | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Commercial/Industrial Storage (Refrigerated),Misc - Freezer and refrigerated spaces (<50F) | #REF! | 62 | #REF! | #REF!
Commercial/Industrial Storage (Refrigerated) | Exhaust - Refrigerating machinery rooms | 0 | 0 | 0 | 0 | 0 | 3 | Exh. Note F | Yes | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Commercial/Industrial Storage (Refrigerated),Exhaust - Refrigerating machinery rooms | #REF! | 35 | #REF! | 2, 35, "Exhaust - Refrigerating machinery rooms"
Commercial/Industrial Storage (Refrigerated) | Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Commercial/Industrial Storage (Refrigerated),Misc - All others | #REF! | 58 | #REF! | 2, 58, "Misc - All others"
Commercial/Industrial Storage (Refrigerated) | Misc - Freezer and refrigerated spaces (<50F) | 0 | 0 | 0 | 0 | 0 | 2 | E | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Commercial/Industrial Storage (Refrigerated),Misc - Freezer and refrigerated spaces (<50F) | #REF! | 62 | #REF! | 2, 62, "Misc - Freezer and refrigerated spaces (<50F)"
Commercial/Industrial Storage (Shipping & Handling) | Misc - Shipping/receiving | 0.15 | 0.15 | 0 | 0 | 0 | 2 | B | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Commercial/Industrial Storage (Shipping & Handling),Misc - Shipping/receiving | #REF! | 66 | #REF! | #REF!
Commercial/Industrial Storage (Shipping & Handling) | Misc - Shipping/receiving | 0.15 | 0.15 | 0 | 0 | 0 | 2 | B | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Commercial/Industrial Storage (Shipping & Handling),Misc - Shipping/receiving | #REF! | 66 | #REF! | 2, 66, "Misc - Shipping/receiving"
Commercial/Industrial Storage (Warehouse) | Misc - Warehouses | 0.15 | 0.15 | 0 | 0 | 0 | 2 | B | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Commercial/Industrial Storage (Warehouse),Misc - Warehouses | #REF! | 70 | #REF! | #REF!
Commercial/Industrial Storage (Warehouse) | Exhaust - Storage rooms, chemical | 0 | 0 | 0 | 0 | 1.5 | 4 | Exh. Note F | Yes | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Commercial/Industrial Storage (Warehouse),Exhaust - Storage rooms, chemical | #REF! | 38 | #REF! | 2, 38, "Exhaust - Storage rooms, chemical"
Commercial/Industrial Storage (Warehouse) | General - Occupiable storage rooms for liquids or gels | 0.15 | 0.15 | 0 | 0 | 0 | 2 | B | Yes | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Commercial/Industrial Storage (Warehouse),General - Occupiable storage rooms for liquids or gels | #REF! | 50 | #REF! | 2, 50, "General - Occupiable storage rooms for liquids or gels"
Commercial/Industrial Storage (Warehouse) | Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Commercial/Industrial Storage (Warehouse),Misc - All others | #REF! | 58 | #REF! | 2, 58, "Misc - All others"
Commercial/Industrial Storage (Warehouse) | Misc - Warehouses | 0.15 | 0.15 | 0 | 0 | 0 | 2 | B | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Commercial/Industrial Storage (Warehouse),Misc - Warehouses | #REF! | 70 | #REF! | 2, 70, "Misc - Warehouses"
Commercial/Industrial Storage (Warehouse) | Office - Occupiable storage rooms for dry materials | 0.15 | 0.15 | 0 | 0 | 0 | 1 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Commercial/Industrial Storage (Warehouse),Office - Occupiable storage rooms for dry materials | #REF! | 73 | #REF! | 2, 73, "Office - Occupiable storage rooms for dry materials"
Computer Room | Misc - Computer (not printing) | 0.15 | 0.15 | 0 | 0 | 0 | 1 | F | Yes | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Computer Room,Misc - Computer (not printing) | #REF! | 61 | #REF! | #REF!
Computer Room | Education - Computer lab | 0.15 | 0.15 | 0 | 0 | 0 | 1 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Computer Room,Education - Computer lab | #REF! | 12 | #REF! | 2, 12, "Education - Computer lab"
Computer Room | Education - Media center | 0.15 | 0.15 | 0 | 0 | 0 | 1 | A | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Computer Room,Education - Media center | #REF! | 17 | #REF! | 2, 17, "Education - Media center"
Computer Room | Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Computer Room,Misc - All others | #REF! | 58 | #REF! | 2, 58, "Misc - All others"
Computer Room | Misc - Computer (not printing) | 0.15 | 0.15 | 0 | 0 | 0 | 1 | F | Yes | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Computer Room,Misc - Computer (not printing) | #REF! | 61 | #REF! | 2, 61, "Misc - Computer (not printing)"
Computer Room | Office - Telephone/data entry | 0.15 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Computer Room,Office - Telephone/data entry | #REF! | 76 | #REF! | 2, 76, "Office - Telephone/data entry"
Concourse and Atria Area | Retail - Mall common areas | 0.25 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 16.6667 | 16.6667 | 15 | #REF! | #REF! | Concourse and Atria Area,Retail - Mall common areas | #REF! | 81 | #REF! | #REF!
Concourse and Atria Area | Assembly - Lobbies | 0.5 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Concourse and Atria Area,Assembly - Lobbies | #REF! | 5 | #REF! | 2, 5, "Assembly - Lobbies"
Concourse and Atria Area | General - Corridors | 0.15 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Concourse and Atria Area,General - Corridors | #REF! | 49 | #REF! | 2, 49, "General - Corridors"
Concourse and Atria Area | Lodging - Lobbies/pre-function | 0.5 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Concourse and Atria Area,Lodging - Lobbies/pre-function | #REF! | 56 | #REF! | 2, 56, "Lodging - Lobbies/pre-function"
Concourse and Atria Area | Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Concourse and Atria Area,Misc - All others | #REF! | 58 | #REF! | 2, 58, "Misc - All others"
Concourse and Atria Area | Misc - Transportation waiting | 0.5 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Concourse and Atria Area,Misc - Transportation waiting | #REF! | 69 | #REF! | 2, 69, "Misc - Transportation waiting"
Concourse and Atria Area | Office - Main entry lobbies | 0.5 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Concourse and Atria Area,Office - Main entry lobbies | #REF! | 72 | #REF! | 2, 72, "Office - Main entry lobbies"
Concourse and Atria Area | Retail - Mall common areas | 0.25 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 16.6667 | 16.6667 | 15 | #REF! | #REF! | Concourse and Atria Area,Retail - Mall common areas | #REF! | 81 | #REF! | 2, 81, "Retail - Mall common areas"
Convention, Conference, Multipurpose and Meeting Area | General - Conference/meeting | 0.5 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Convention, Conference, Multipurpose and Meeting Area,General - Conference/meeting | #REF! | 48 | #REF! | #REF!
Convention, Conference, Multipurpose and Meeting Area | Assembly - Courtrooms | 0.19 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 12.6667 | 12.6667 | 15 | #REF! | #REF! | Convention, Conference, Multipurpose and Meeting Area,Assembly - Courtrooms | #REF! | 2 | #REF! | 2, 2, "Assembly - Courtrooms"
Convention, Conference, Multipurpose and Meeting Area | Assembly - Legislative chambers | 0.19 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 12.6667 | 12.6667 | 15 | #REF! | #REF! | Convention, Conference, Multipurpose and Meeting Area,Assembly - Legislative chambers | #REF! | 3 | #REF! | 2, 3, "Assembly - Legislative chambers"
Convention, Conference, Multipurpose and Meeting Area | Assembly - Places of religious worship | 1.07 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 71.3333 | 71.3333 | 15 | #REF! | #REF! | Convention, Conference, Multipurpose and Meeting Area,Assembly - Places of religious worship | #REF! | 8 | #REF! | 2, 8, "Assembly - Places of religious worship"
Convention, Conference, Multipurpose and Meeting Area | Education - Lecture hall (fixed seats) | 0 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Convention, Conference, Multipurpose and Meeting Area,Education - Lecture hall (fixed seats) | #REF! | 15 | #REF! | 2, 15, "Education - Lecture hall (fixed seats)"
Convention, Conference, Multipurpose and Meeting Area | Education - Multiuse assembly | 0.5 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Convention, Conference, Multipurpose and Meeting Area,Education - Multiuse assembly | #REF! | 19 | #REF! | 2, 19, "Education - Multiuse assembly"
Convention, Conference, Multipurpose and Meeting Area | General - Conference/meeting | 0.5 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Convention, Conference, Multipurpose and Meeting Area,General - Conference/meeting | #REF! | 48 | #REF! | 2, 48, "General - Conference/meeting"
Convention, Conference, Multipurpose and Meeting Area | Lodging - Multipurpose assembly | 0.5 | 0.5 | 0 | 0 | 0 | 1 | F | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Convention, Conference, Multipurpose and Meeting Area,Lodging - Multipurpose assembly | #REF! | 57 | #REF! | 2, 57, "Lodging - Multipurpose assembly"
Convention, Conference, Multipurpose and Meeting Area | Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Convention, Conference, Multipurpose and Meeting Area,Misc - All others | #REF! | 58 | #REF! | 2, 58, "Misc - All others"
Copy Room | Exhaust - Copy, printing rooms | 0 | 0 | 0 | 0 | 0.5 | 2 |  | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Copy Room,Exhaust - Copy, printing rooms | #REF! | 28 | #REF! | #REF!
Copy Room | Exhaust - Copy, printing rooms | 0 | 0 | 0 | 0 | 0.5 | 2 |  | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Copy Room,Exhaust - Copy, printing rooms | #REF! | 28 | #REF! | 2, 28, "Exhaust - Copy, printing rooms"
Corridor Area | General - Corridors | 0.15 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Corridor Area,General - Corridors | #REF! | 49 | #REF! | #REF!
Corridor Area | General - Corridors | 0.15 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Corridor Area,General - Corridors | #REF! | 49 | #REF! | 2, 49, "General - Corridors"
Corridor Area | Lodging - Lobbies/pre-function | 0.5 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Corridor Area,Lodging - Lobbies/pre-function | #REF! | 56 | #REF! | 2, 56, "Lodging - Lobbies/pre-function"
Corridor Area | Misc - Transportation waiting | 0.5 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Corridor Area,Misc - Transportation waiting | #REF! | 69 | #REF! | 2, 69, "Misc - Transportation waiting"
Corridor Area | Residential - Common corridors | 0.15 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Corridor Area,Residential - Common corridors | #REF! | 77 | #REF! | 2, 77, "Residential - Common corridors"
Corridor Area | Retail - Mall common areas | 0.25 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 16.6667 | 16.6667 | 15 | #REF! | #REF! | Corridor Area,Retail - Mall common areas | #REF! | 81 | #REF! | 2, 81, "Retail - Mall common areas"
Dining Area (Bar/Lounge and Fine Dining) | Food Service - Restaurant dining rooms | 0.5 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Dining Area (Bar/Lounge and Fine Dining),Food Service - Restaurant dining rooms | #REF! | 45 | #REF! | #REF!
Dining Area (Bar/Lounge and Fine Dining) | Food Service - Bars, cocktail lounges | 0.5 | 0.2 | 0 | 0 | 0 | 2 |  | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Dining Area (Bar/Lounge and Fine Dining),Food Service - Bars, cocktail lounges | #REF! | 42 | #REF! | 2, 42, "Food Service - Bars, cocktail lounges"
Dining Area (Bar/Lounge and Fine Dining) | Food Service - Restaurant dining rooms | 0.5 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Dining Area (Bar/Lounge and Fine Dining),Food Service - Restaurant dining rooms | #REF! | 45 | #REF! | 2, 45, "Food Service - Restaurant dining rooms"
Dining Area (Cafeteria/Fast Food) | Food Service - Cafeteria/fast-food dining | 0.5 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Dining Area (Cafeteria/Fast Food),Food Service - Cafeteria/fast-food dining | #REF! | 43 | #REF! | #REF!
Dining Area (Cafeteria/Fast Food) | Food Service - Cafeteria/fast-food dining | 0.5 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Dining Area (Cafeteria/Fast Food),Food Service - Cafeteria/fast-food dining | #REF! | 43 | #REF! | 2, 43, "Food Service - Cafeteria/fast-food dining"
Dining Area (Family and Leisure) | Food Service - Cafeteria/fast-food dining | 0.5 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Dining Area (Family and Leisure),Food Service - Cafeteria/fast-food dining | #REF! | 43 | #REF! | #REF!
Dining Area (Family and Leisure) | Food Service - Bars, cocktail lounges | 0.5 | 0.2 | 0 | 0 | 0 | 2 |  | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Dining Area (Family and Leisure),Food Service - Bars, cocktail lounges | #REF! | 42 | #REF! | 2, 42, "Food Service - Bars, cocktail lounges"
Dining Area (Family and Leisure) | Food Service - Cafeteria/fast-food dining | 0.5 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Dining Area (Family and Leisure),Food Service - Cafeteria/fast-food dining | #REF! | 43 | #REF! | 2, 43, "Food Service - Cafeteria/fast-food dining"
Dining Area (Family and Leisure) | Food Service - Restaurant dining rooms | 0.5 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Dining Area (Family and Leisure),Food Service - Restaurant dining rooms | #REF! | 45 | #REF! | 2, 45, "Food Service - Restaurant dining rooms"
Electrical, Mechanical, Telephone Rooms | Misc - Telephone closets | 0.15 | 0.15 | 0 | 0 | 0 | 1 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Electrical, Mechanical, Telephone Rooms,Misc - Telephone closets | #REF! | 68 | #REF! | #REF!
Electrical, Mechanical, Telephone Rooms | Exhaust - Refrigerating machinery rooms | 0 | 0 | 0 | 0 | 0 | 3 | Exh. Note F | Yes | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Electrical, Mechanical, Telephone Rooms,Exhaust - Refrigerating machinery rooms | #REF! | 35 | #REF! | 2, 35, "Exhaust - Refrigerating machinery rooms"
Electrical, Mechanical, Telephone Rooms | General - Unoccupied | 0 | 0 | 0 | 0 | 0 | 1 |  | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Electrical, Mechanical, Telephone Rooms,General - Unoccupied | #REF! | 51 | #REF! | 2, 51, "General - Unoccupied"
Electrical, Mechanical, Telephone Rooms | Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Electrical, Mechanical, Telephone Rooms,Misc - All others | #REF! | 58 | #REF! | 2, 58, "Misc - All others"
Electrical, Mechanical, Telephone Rooms | Misc - Telephone closets | 0.15 | 0.15 | 0 | 0 | 0 | 1 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Electrical, Mechanical, Telephone Rooms,Misc - Telephone closets | #REF! | 68 | #REF! | 2, 68, "Misc - Telephone closets"
Exercise/Fitness Center and Gymnasium Areas | Sports/Entertainment - Gym, sports arena (play area) | 0.5 | 0.15 | 0 | 0 | 0 | 2 | E | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Exercise/Fitness Center and Gymnasium Areas,Sports/Entertainment - Gym, sports arena (play area) | #REF! | 89 | #REF! | #REF!
Exercise/Fitness Center and Gymnasium Areas | Education - Multiuse assembly | 0.5 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Exercise/Fitness Center and Gymnasium Areas,Education - Multiuse assembly | #REF! | 19 | #REF! | 2, 19, "Education - Multiuse assembly"
Exercise/Fitness Center and Gymnasium Areas | Education - Music/theater/dance | 1.07 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | #N/A | #N/A | #N/A | #REF! | #REF! | Exercise/Fitness Center and Gymnasium Areas,Education - Music/theater/dance | #REF! | #N/A | #REF! | #N/A
Exercise/Fitness Center and Gymnasium Areas | Sports/Entertainment - Disco/dance floors | 1.5 | 0.15 | 0 | 0 | 0 | 2 | F | No | #REF! | 100 | 100 | 15 | #REF! | #REF! | Exercise/Fitness Center and Gymnasium Areas,Sports/Entertainment - Disco/dance floors | #REF! | 86 | #REF! | 2, 86, "Sports/Entertainment - Disco/dance floors"
Exercise/Fitness Center and Gymnasium Areas | Sports/Entertainment - Gym, sports arena (play area) | 0.5 | 0.15 | 0 | 0 | 0 | 2 | E | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Exercise/Fitness Center and Gymnasium Areas,Sports/Entertainment - Gym, sports arena (play area) | #REF! | 89 | #REF! | 2, 89, "Sports/Entertainment - Gym, sports arena (play area)"
Exercise/Fitness Center and Gymnasium Areas | Sports/Entertainment - Health club/aerobics room | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Exercise/Fitness Center and Gymnasium Areas,Sports/Entertainment - Health club/aerobics room | #REF! | 90 | #REF! | 2, 90, "Sports/Entertainment - Health club/aerobics room"
Exercise/Fitness Center and Gymnasium Areas | Sports/Entertainment - Health club/weight rooms | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Exercise/Fitness Center and Gymnasium Areas,Sports/Entertainment - Health club/weight rooms | #REF! | 91 | #REF! | 2, 91, "Sports/Entertainment - Health club/weight rooms"
Exercise/Fitness Center and Gymnasium Areas | Sports/Entertainment - Swimming (deck) | 0.5 | 0.15 | 0 | 0 | 0 | 2 | C | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Exercise/Fitness Center and Gymnasium Areas,Sports/Entertainment - Swimming (deck) | #REF! | 94 | #REF! | 2, 94, "Sports/Entertainment - Swimming (deck)"
Exercise/Fitness Center and Gymnasium Areas | Sports/Entertainment - Swimming (pool) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Exercise/Fitness Center and Gymnasium Areas,Sports/Entertainment - Swimming (pool) | #REF! | 95 | #REF! | 2, 95, "Sports/Entertainment - Swimming (pool)"
Financial Transaction Area | Misc - Banks or bank lobbies | 0.15 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Financial Transaction Area,Misc - Banks or bank lobbies | #REF! | 60 | #REF! | #REF!
Financial Transaction Area | Misc - Bank vaults/safe deposit | 0.15 | 0.15 | 0 | 0 | 0 | 2 | F | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Financial Transaction Area,Misc - Bank vaults/safe deposit | #REF! | 59 | #REF! | 2, 59, "Misc - Bank vaults/safe deposit"
Financial Transaction Area | Misc - Banks or bank lobbies | 0.15 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Financial Transaction Area,Misc - Banks or bank lobbies | #REF! | 60 | #REF! | 2, 60, "Misc - Banks or bank lobbies"
Financial Transaction Area | Office - Office space | 0.15 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Financial Transaction Area,Office - Office space | #REF! | 74 | #REF! | 2, 74, "Office - Office space"
General/Commercial & Industrial Work Area (High Bay) | Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 0.15 | 0.15 | 0 | 0 | 0 | 3 |  | Yes | #REF! | 0 | #REF! | 15 | #REF! | #REF! | General/Commercial & Industrial Work Area (High Bay),Misc - General manufacturing (excludes heavy industrial and process using chemicals) | #REF! | 63 | #REF! | #REF!
General/Commercial & Industrial Work Area (High Bay) | Exhaust - Copy, printing rooms | 0 | 0 | 0 | 0 | 0.5 | 2 |  | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | General/Commercial & Industrial Work Area (High Bay),Exhaust - Copy, printing rooms | #REF! | 28 | #REF! | 2, 28, "Exhaust - Copy, printing rooms"
General/Commercial & Industrial Work Area (High Bay) | Exhaust - Darkrooms | 0 | 0 | 0 | 0 | 1 | 2 |  | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | General/Commercial & Industrial Work Area (High Bay),Exhaust - Darkrooms | #REF! | 29 | #REF! | 2, 29, "Exhaust - Darkrooms"
General/Commercial & Industrial Work Area (High Bay) | Exhaust - Paint spray booths | 0 | 0 | 0 | 0 | 0 | 4 | Exh. Note F | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | General/Commercial & Industrial Work Area (High Bay),Exhaust - Paint spray booths | #REF! | 33 | #REF! | 2, 33, "Exhaust - Paint spray booths"
General/Commercial & Industrial Work Area (High Bay) | Exhaust - Woodwork shop/classrooms | 0 | 0 | 0 | 0 | 0.5 | 2 | 0 | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | General/Commercial & Industrial Work Area (High Bay),Exhaust - Woodwork shop/classrooms | #REF! | 41 | #REF! | 2, 41, "Exhaust - Woodwork shop/classrooms"
General/Commercial & Industrial Work Area (High Bay) | Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | General/Commercial & Industrial Work Area (High Bay),Misc - All others | #REF! | 58 | #REF! | 2, 58, "Misc - All others"
General/Commercial & Industrial Work Area (High Bay) | Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 0.15 | 0.15 | 0 | 0 | 0 | 3 |  | Yes | #REF! | 0 | #REF! | 15 | #REF! | #REF! | General/Commercial & Industrial Work Area (High Bay),Misc - General manufacturing (excludes heavy industrial and process using chemicals) | #REF! | 63 | #REF! | 2, 63, "Misc - General manufacturing (excludes heavy industrial and process using chemicals)"
General/Commercial & Industrial Work Area (High Bay) | Misc - Sorting, packing, light assembly | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | General/Commercial & Industrial Work Area (High Bay),Misc - Sorting, packing, light assembly | #REF! | 67 | #REF! | 2, 67, "Misc - Sorting, packing, light assembly"
General/Commercial & Industrial Work Area (Low Bay) | Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 0.15 | 0.15 | 0 | 0 | 0 | 3 |  | Yes | #REF! | 0 | #REF! | 15 | #REF! | #REF! | General/Commercial & Industrial Work Area (Low Bay),Misc - General manufacturing (excludes heavy industrial and process using chemicals) | #REF! | 63 | #REF! | #REF!
General/Commercial & Industrial Work Area (Low Bay) | Exhaust - Copy, printing rooms | 0 | 0 | 0 | 0 | 0.5 | 2 |  | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | General/Commercial & Industrial Work Area (Low Bay),Exhaust - Copy, printing rooms | #REF! | 28 | #REF! | 2, 28, "Exhaust - Copy, printing rooms"
General/Commercial & Industrial Work Area (Low Bay) | Exhaust - Darkrooms | 0 | 0 | 0 | 0 | 1 | 2 |  | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | General/Commercial & Industrial Work Area (Low Bay),Exhaust - Darkrooms | #REF! | 29 | #REF! | 2, 29, "Exhaust - Darkrooms"
General/Commercial & Industrial Work Area (Low Bay) | Exhaust - Janitor closets, trash rooms, recycling | 0 | 0 | 0 | 0 | 1 | 3 |  | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | General/Commercial & Industrial Work Area (Low Bay),Exhaust - Janitor closets, trash rooms, recycling | #REF! | 30 | #REF! | 2, 30, "Exhaust - Janitor closets, trash rooms, recycling"
General/Commercial & Industrial Work Area (Low Bay) | Exhaust - Paint spray booths | 0 | 0 | 0 | 0 | 0 | 4 | Exh. Note F | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | General/Commercial & Industrial Work Area (Low Bay),Exhaust - Paint spray booths | #REF! | 33 | #REF! | 2, 33, "Exhaust - Paint spray booths"
General/Commercial & Industrial Work Area (Low Bay) | Exhaust - Woodwork shop/classrooms | 0 | 0 | 0 | 0 | 0.5 | 2 | 0 | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | General/Commercial & Industrial Work Area (Low Bay),Exhaust - Woodwork shop/classrooms | #REF! | 41 | #REF! | 2, 41, "Exhaust - Woodwork shop/classrooms"
General/Commercial & Industrial Work Area (Low Bay) | Lodging - Laundry rooms, central | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | General/Commercial & Industrial Work Area (Low Bay),Lodging - Laundry rooms, central | #REF! | 55 | #REF! | 2, 55, "Lodging - Laundry rooms, central"
General/Commercial & Industrial Work Area (Low Bay) | Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | General/Commercial & Industrial Work Area (Low Bay),Misc - All others | #REF! | 58 | #REF! | 2, 58, "Misc - All others"
General/Commercial & Industrial Work Area (Low Bay) | Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 0.15 | 0.15 | 0 | 0 | 0 | 3 |  | Yes | #REF! | 0 | #REF! | 15 | #REF! | #REF! | General/Commercial & Industrial Work Area (Low Bay),Misc - General manufacturing (excludes heavy industrial and process using chemicals) | #REF! | 63 | #REF! | 2, 63, "Misc - General manufacturing (excludes heavy industrial and process using chemicals)"
General/Commercial & Industrial Work Area (Low Bay) | Misc - Sorting, packing, light assembly | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | General/Commercial & Industrial Work Area (Low Bay),Misc - Sorting, packing, light assembly | #REF! | 67 | #REF! | 2, 67, "Misc - Sorting, packing, light assembly"
General/Commercial & Industrial Work Area (Precision) | Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 0.15 | 0.15 | 0 | 0 | 0 | 3 |  | Yes | #REF! | 0 | #REF! | 15 | #REF! | #REF! | General/Commercial & Industrial Work Area (Precision),Misc - General manufacturing (excludes heavy industrial and process using chemicals) | #REF! | 63 | #REF! | #REF!
General/Commercial & Industrial Work Area (Precision) | Exhaust - Copy, printing rooms | 0 | 0 | 0 | 0 | 0.5 | 2 |  | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | General/Commercial & Industrial Work Area (Precision),Exhaust - Copy, printing rooms | #REF! | 28 | #REF! | 2, 28, "Exhaust - Copy, printing rooms"
General/Commercial & Industrial Work Area (Precision) | Exhaust - Darkrooms | 0 | 0 | 0 | 0 | 1 | 2 |  | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | General/Commercial & Industrial Work Area (Precision),Exhaust - Darkrooms | #REF! | 29 | #REF! | 2, 29, "Exhaust - Darkrooms"
General/Commercial & Industrial Work Area (Precision) | Exhaust - Paint spray booths | 0 | 0 | 0 | 0 | 0 | 4 | Exh. Note F | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | General/Commercial & Industrial Work Area (Precision),Exhaust - Paint spray booths | #REF! | 33 | #REF! | 2, 33, "Exhaust - Paint spray booths"
General/Commercial & Industrial Work Area (Precision) | Exhaust - Woodwork shop/classrooms | 0 | 0 | 0 | 0 | 0.5 | 2 | 0 | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | General/Commercial & Industrial Work Area (Precision),Exhaust - Woodwork shop/classrooms | #REF! | 41 | #REF! | 2, 41, "Exhaust - Woodwork shop/classrooms"
General/Commercial & Industrial Work Area (Precision) | Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | General/Commercial & Industrial Work Area (Precision),Misc - All others | #REF! | 58 | #REF! | 2, 58, "Misc - All others"
General/Commercial & Industrial Work Area (Precision) | Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 0.15 | 0.15 | 0 | 0 | 0 | 3 |  | Yes | #REF! | 0 | #REF! | 15 | #REF! | #REF! | General/Commercial & Industrial Work Area (Precision),Misc - General manufacturing (excludes heavy industrial and process using chemicals) | #REF! | 63 | #REF! | 2, 63, "Misc - General manufacturing (excludes heavy industrial and process using chemicals)"
General/Commercial & Industrial Work Area (Precision) | Misc - Sorting, packing, light assembly | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | General/Commercial & Industrial Work Area (Precision),Misc - Sorting, packing, light assembly | #REF! | 67 | #REF! | 2, 67, "Misc - Sorting, packing, light assembly"
Healthcare Facility and Hospitals (Exam/Treatment Room) | Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Healthcare Facility and Hospitals (Exam/Treatment Room),Misc - All others | #REF! | 58 | #REF! | #REF!
Healthcare Facility and Hospitals (Exam/Treatment Room) | Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Healthcare Facility and Hospitals (Exam/Treatment Room),Misc - All others | #REF! | 58 | #REF! | 2, 58, "Misc - All others"
Healthcare Facility and Hospitals (Imaging Room) | Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Healthcare Facility and Hospitals (Imaging Room),Misc - All others | #REF! | 58 | #REF! | #REF!
Healthcare Facility and Hospitals (Imaging Room) | Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Healthcare Facility and Hospitals (Imaging Room),Misc - All others | #REF! | 58 | #REF! | 2, 58, "Misc - All others"
Healthcare Facility and Hospitals (Medical Supply Room) | Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Healthcare Facility and Hospitals (Medical Supply Room),Misc - All others | #REF! | 58 | #REF! | #REF!
Healthcare Facility and Hospitals (Medical Supply Room) | Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Healthcare Facility and Hospitals (Medical Supply Room),Misc - All others | #REF! | 58 | #REF! | 2, 58, "Misc - All others"
Healthcare Facility and Hospitals (Nursery) | Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Healthcare Facility and Hospitals (Nursery),Misc - All others | #REF! | 58 | #REF! | #REF!
Healthcare Facility and Hospitals (Nursery) | Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Healthcare Facility and Hospitals (Nursery),Misc - All others | #REF! | 58 | #REF! | 2, 58, "Misc - All others"
Healthcare Facility and Hospitals (Nurse's Station) | Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Healthcare Facility and Hospitals (Nurse's Station),Misc - All others | #REF! | 58 | #REF! | #REF!
Healthcare Facility and Hospitals (Nurse's Station) | Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Healthcare Facility and Hospitals (Nurse's Station),Misc - All others | #REF! | 58 | #REF! | 2, 58, "Misc - All others"
Healthcare Facility and Hospitals (Imaging Room) | Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Healthcare Facility and Hospitals (Imaging Room),Misc - All others | #REF! | 58 | #REF! | #REF!
Healthcare Facility and Hospitals (Imaging Room) | Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Healthcare Facility and Hospitals (Imaging Room),Misc - All others | #REF! | 58 | #REF! | 2, 58, "Misc - All others"
Healthcare Facility and Hospitals (Operating Room) | Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Healthcare Facility and Hospitals (Operating Room),Misc - All others | #REF! | 58 | #REF! | #REF!
Healthcare Facility and Hospitals (Operating Room) | Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Healthcare Facility and Hospitals (Operating Room),Misc - All others | #REF! | 58 | #REF! | 2, 58, "Misc - All others"
Healthcare Facility and Hospitals (Patient Room) | Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Healthcare Facility and Hospitals (Patient Room),Misc - All others | #REF! | 58 | #REF! | #REF!
Healthcare Facility and Hospitals (Patient Room) | Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Healthcare Facility and Hospitals (Patient Room),Misc - All others | #REF! | 58 | #REF! | 2, 58, "Misc - All others"
Healthcare Facility and Hospitals (Physical Therapy Room) | Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Healthcare Facility and Hospitals (Physical Therapy Room),Misc - All others | #REF! | 58 | #REF! | #REF!
Healthcare Facility and Hospitals (Physical Therapy Room) | Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Healthcare Facility and Hospitals (Physical Therapy Room),Misc - All others | #REF! | 58 | #REF! | 2, 58, "Misc - All others"
Healthcare Facility and Hospitals (Recovery Room) | Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Healthcare Facility and Hospitals (Recovery Room),Misc - All others | #REF! | 58 | #REF! | #REF!
Healthcare Facility and Hospitals (Recovery Room) | Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Healthcare Facility and Hospitals (Recovery Room),Misc - All others | #REF! | 58 | #REF! | 2, 58, "Misc - All others"
High-Rise Residential Living Spaces | NA | 0.15 | 0.15 | 0 | 0 | 0 | 2 | B | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | High-Rise Residential Living Spaces,NA | #REF! | 96 | #REF! | #REF!
High-Rise Residential Living Spaces | NA | 0.15 | 0.15 | 0 | 0 | 0 | 2 | B | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | High-Rise Residential Living Spaces,NA | 226 | 96 | #REF! | 2, 96, "NA"
Hotel Function Area | Lodging - Multipurpose assembly | 0.5 | 0.5 | 0 | 0 | 0 | 1 | F | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Hotel Function Area,Lodging - Multipurpose assembly | #REF! | 57 | #REF! | #REF!
Hotel Function Area | General - Conference/meeting | 0.5 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Hotel Function Area,General - Conference/meeting | #REF! | 48 | #REF! | 2, 48, "General - Conference/meeting"
Hotel Function Area | Lodging - Lobbies/pre-function | 0.5 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Hotel Function Area,Lodging - Lobbies/pre-function | #REF! | 56 | #REF! | 2, 56, "Lodging - Lobbies/pre-function"
Hotel Function Area | Lodging - Multipurpose assembly | 0.5 | 0.5 | 0 | 0 | 0 | 1 | F | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Hotel Function Area,Lodging - Multipurpose assembly | #REF! | 57 | #REF! | 2, 57, "Lodging - Multipurpose assembly"
Hotel Function Area | Sports/Entertainment - Gambling casinos | 0.68 | 0.15 | 0 | 0 | 0 | 1 |  | No | #REF! | 45.3333 | 45.3333 | 15 | #REF! | #REF! | Hotel Function Area,Sports/Entertainment - Gambling casinos | #REF! | 87 | #REF! | 2, 87, "Sports/Entertainment - Gambling casinos"
Hotel/Motel Guest Room | Lodging - Bedroom/living room | 0.15 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Hotel/Motel Guest Room,Lodging - Bedroom/living room | #REF! | 53 | #REF! | #REF!
Hotel/Motel Guest Room | Lodging - Barracks sleeping areas | 0.15 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Hotel/Motel Guest Room,Lodging - Barracks sleeping areas | #REF! | 52 | #REF! | 2, 52, "Lodging - Barracks sleeping areas"
Hotel/Motel Guest Room | Lodging - Bedroom/living room | 0.15 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Hotel/Motel Guest Room,Lodging - Bedroom/living room | #REF! | 53 | #REF! | 2, 53, "Lodging - Bedroom/living room"
Kitchen/Food Preparation Area | Food Service - Kitchen (cooking) | 0.15 | 0.15 | 0 | 0 | 0.7 | 2 |  | Yes | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Kitchen/Food Preparation Area,Food Service - Kitchen (cooking) | #REF! | 44 | #REF! | #REF!
Kitchen/Food Preparation Area | Food Service - Kitchen (cooking) | 0.15 | 0.15 | 0 | 0 | 0.7 | 2 |  | Yes | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Kitchen/Food Preparation Area,Food Service - Kitchen (cooking) | #REF! | 44 | #REF! | 2, 44, "Food Service - Kitchen (cooking)"
Kitchenette or Residential Kitchen | Exhaust - Kitchenettes | 0 | 0 | 0 | 0 | 0.3 | 2 |  | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Kitchenette or Residential Kitchen,Exhaust - Kitchenettes | #REF! | 31 | #REF! | #REF!
Kitchenette or Residential Kitchen | Exhaust - Kitchenettes | 0 | 0 | 0 | 0 | 0.3 | 2 |  | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Kitchenette or Residential Kitchen,Exhaust - Kitchenettes | #REF! | 31 | #REF! | 2, 31, "Exhaust - Kitchenettes"
Laundry Area | Lodging - Laundry rooms, central | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Laundry Area,Lodging - Laundry rooms, central | #REF! | 55 | #REF! | #REF!
Laundry Area | Exhaust - Soiled laundry storage rooms | 0 | 0 | 0 | 0 | 1 | 3 | Exh. Note F | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Laundry Area,Exhaust - Soiled laundry storage rooms | #REF! | 37 | #REF! | 2, 37, "Exhaust - Soiled laundry storage rooms"
Laundry Area | Lodging - Laundry rooms within dwelling units | 0.15 | 0.15 | 0 | 0 | 0 | 1 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Laundry Area,Lodging - Laundry rooms within dwelling units | #REF! | 54 | #REF! | 2, 54, "Lodging - Laundry rooms within dwelling units"
Laundry Area | Lodging - Laundry rooms, central | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Laundry Area,Lodging - Laundry rooms, central | #REF! | 55 | #REF! | 2, 55, "Lodging - Laundry rooms, central"
Laundry Area | Retail - Coin-operated laundries | 0.3 | 0.3 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Laundry Area,Retail - Coin-operated laundries | #REF! | 80 | #REF! | 2, 80, "Retail - Coin-operated laundries"
Library (Reading Area) | Assembly - Libraries (reading rooms and stack areas) | 0.15 | 0.15 | 0 | 0 | 0 | 1 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Library (Reading Area),Assembly - Libraries (reading rooms and stack areas) | #REF! | 4 | #REF! | #REF!
Library (Reading Area) | Assembly - Libraries (reading rooms and stack areas) | 0.15 | 0.15 | 0 | 0 | 0 | 1 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Library (Reading Area),Assembly - Libraries (reading rooms and stack areas) | #REF! | 4 | #REF! | 2, 4, "Assembly - Libraries (reading rooms and stack areas)"
Library (Stacks Area) | Assembly - Libraries (reading rooms and stack areas) | 0.15 | 0.15 | 0 | 0 | 0 | 1 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Library (Stacks Area),Assembly - Libraries (reading rooms and stack areas) | #REF! | 4 | #REF! | #REF!
Library (Stacks Area) | Assembly - Libraries (reading rooms and stack areas) | 0.15 | 0.15 | 0 | 0 | 0 | 1 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Library (Stacks Area),Assembly - Libraries (reading rooms and stack areas) | #REF! | 4 | #REF! | 2, 4, "Assembly - Libraries (reading rooms and stack areas)"
Locker Room | Exhaust - Locker rooms for athletic or industrial facilities | 0 | 0 | 0 | 0 | 0.5 | 2 |  | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Locker Room,Exhaust - Locker rooms for athletic or industrial facilities | #REF! | 32 | #REF! | #REF!
Locker Room | Exhaust - All other locker rooms | 0 | 0 | 0 | 0 | 0.25 | 2 |  | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Locker Room,Exhaust - All other locker rooms | #REF! | 24 | #REF! | 2, 24, "Exhaust - All other locker rooms"
Locker Room | Exhaust - Locker rooms for athletic or industrial facilities | 0 | 0 | 0 | 0 | 0.5 | 2 |  | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Locker Room,Exhaust - Locker rooms for athletic or industrial facilities | #REF! | 32 | #REF! | 2, 32, "Exhaust - Locker rooms for athletic or industrial facilities"
Locker Room | Exhaust - Shower rooms | 0 | 0 | 20 | 50 | 0 | 2 | Exh. Note G,H | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Locker Room,Exhaust - Shower rooms | #REF! | 36 | #REF! | 2, 36, "Exhaust - Shower rooms"
Lounge, Breakroom, or Waiting Area | General - Break rooms | 0.5 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Lounge, Breakroom, or Waiting Area,General - Break rooms | #REF! | 46 | #REF! | #REF!
Lounge, Breakroom, or Waiting Area | General - Break rooms | 0.5 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Lounge, Breakroom, or Waiting Area,General - Break rooms | #REF! | 46 | #REF! | 2, 46, "General - Break rooms"
Lounge, Breakroom, or Waiting Area | General - Coffee Stations | 0.5 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Lounge, Breakroom, or Waiting Area,General - Coffee Stations | #REF! | 47 | #REF! | 2, 47, "General - Coffee Stations"
Lounge, Breakroom, or Waiting Area | Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Lounge, Breakroom, or Waiting Area,Misc - All others | #REF! | 58 | #REF! | 2, 58, "Misc - All others"
Lounge, Breakroom, or Waiting Area | Misc - Transportation waiting | 0.5 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Lounge, Breakroom, or Waiting Area,Misc - Transportation waiting | #REF! | 69 | #REF! | 2, 69, "Misc - Transportation waiting"
Lounge, Breakroom, or Waiting Area | Office - Breakrooms | 0.5 | 0.15 | 0 | 0 | 0 | 1 |  | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Lounge, Breakroom, or Waiting Area,Office - Breakrooms | #REF! | 71 | #REF! | 2, 71, "Office - Breakrooms"
Lounge, Breakroom, or Waiting Area | Office - Reception areas | 0.15 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Lounge, Breakroom, or Waiting Area,Office - Reception areas | #REF! | 75 | #REF! | 2, 75, "Office - Reception areas"
Main Entry Lobby | Office - Main entry lobbies | 0.5 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Main Entry Lobby,Office - Main entry lobbies | #REF! | 72 | #REF! | #REF!
Main Entry Lobby | Assembly - Lobbies | 0.5 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Main Entry Lobby,Assembly - Lobbies | #REF! | 5 | #REF! | 2, 5, "Assembly - Lobbies"
Main Entry Lobby | Lodging - Lobbies/pre-function | 0.5 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Main Entry Lobby,Lodging - Lobbies/pre-function | #REF! | 56 | #REF! | 2, 56, "Lodging - Lobbies/pre-function"
Main Entry Lobby | Misc - Banks or bank lobbies | 0.15 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Main Entry Lobby,Misc - Banks or bank lobbies | #REF! | 60 | #REF! | 2, 60, "Misc - Banks or bank lobbies"
Main Entry Lobby | Office - Main entry lobbies | 0.5 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Main Entry Lobby,Office - Main entry lobbies | #REF! | 72 | #REF! | 2, 72, "Office - Main entry lobbies"
Museum Area (Exhibition/Display) | Assembly - Museums/galleries | 0.25 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 16.6667 | 16.6667 | 15 | #REF! | #REF! | Museum Area (Exhibition/Display),Assembly - Museums/galleries | #REF! | 7 | #REF! | #REF!
Museum Area (Exhibition/Display) | Assembly - Museums (childrens) | 0.25 | 0.15 | 0 | 0 | 0 | 1 |  | No | #REF! | 16.6667 | 16.6667 | 15 | #REF! | #REF! | Museum Area (Exhibition/Display),Assembly - Museums (childrens) | #REF! | 6 | #REF! | 2, 6, "Assembly - Museums (childrens)"
Museum Area (Exhibition/Display) | Assembly - Museums/galleries | 0.25 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 16.6667 | 16.6667 | 15 | #REF! | #REF! | Museum Area (Exhibition/Display),Assembly - Museums/galleries | #REF! | 7 | #REF! | 2, 7, "Assembly - Museums/galleries"
Museum Area (Restoration Room) | Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 0.15 | 0.15 | 0 | 0 | 0 | 3 |  | Yes | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Museum Area (Restoration Room),Misc - General manufacturing (excludes heavy industrial and process using chemicals) | #REF! | 63 | #REF! | #REF!
Museum Area (Restoration Room) | Education - Art classroom | 0.15 | 0.15 | 0 | 0 | 0.7 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Museum Area (Restoration Room),Education - Art classroom | #REF! | 9 | #REF! | 2, 9, "Education - Art classroom"
Museum Area (Restoration Room) | Education - Science laboratories | 0.15 | 0.15 | 0 | 0 | 1 | 2 |  | Yes | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Museum Area (Restoration Room),Education - Science laboratories | #REF! | 21 | #REF! | 2, 21, "Education - Science laboratories"
Museum Area (Restoration Room) | Education - University/college laboratories | 0.15 | 0.15 | 0 | 0 | 1 | 2 |  | Yes | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Museum Area (Restoration Room),Education - University/college laboratories | #REF! | 22 | #REF! | 2, 22, "Education - University/college laboratories"
Museum Area (Restoration Room) | Education - Wood shop | 0.15 | 0.15 | 0 | 0 | 0.5 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Museum Area (Restoration Room),Education - Wood shop | #REF! | 23 | #REF! | 2, 23, "Education - Wood shop"
Museum Area (Restoration Room) | Exhaust - Copy, printing rooms | 0 | 0 | 0 | 0 | 0.5 | 2 |  | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Museum Area (Restoration Room),Exhaust - Copy, printing rooms | #REF! | 28 | #REF! | 2, 28, "Exhaust - Copy, printing rooms"
Museum Area (Restoration Room) | Exhaust - Darkrooms | 0 | 0 | 0 | 0 | 1 | 2 |  | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Museum Area (Restoration Room),Exhaust - Darkrooms | #REF! | 29 | #REF! | 2, 29, "Exhaust - Darkrooms"
Museum Area (Restoration Room) | Exhaust - Woodwork shop/classrooms | 0 | 0 | 0 | 0 | 0.5 | 2 | 0 | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Museum Area (Restoration Room),Exhaust - Woodwork shop/classrooms | #REF! | 41 | #REF! | 2, 41, "Exhaust - Woodwork shop/classrooms"
Museum Area (Restoration Room) | General - Occupiable storage rooms for liquids or gels | 0.15 | 0.15 | 0 | 0 | 0 | 2 | B | Yes | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Museum Area (Restoration Room),General - Occupiable storage rooms for liquids or gels | #REF! | 50 | #REF! | 2, 50, "General - Occupiable storage rooms for liquids or gels"
Museum Area (Restoration Room) | Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Museum Area (Restoration Room),Misc - All others | #REF! | 58 | #REF! | 2, 58, "Misc - All others"
Museum Area (Restoration Room) | Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 0.15 | 0.15 | 0 | 0 | 0 | 3 |  | Yes | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Museum Area (Restoration Room),Misc - General manufacturing (excludes heavy industrial and process using chemicals) | #REF! | 63 | #REF! | 2, 63, "Misc - General manufacturing (excludes heavy industrial and process using chemicals)"
Museum Area (Restoration Room) | Misc - Photo studios | 0.15 | 0.15 | 0 | 0 | 0 | 1 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Museum Area (Restoration Room),Misc - Photo studios | #REF! | 65 | #REF! | 2, 65, "Misc - Photo studios"
Museum Area (Restoration Room) | Misc - Sorting, packing, light assembly | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Museum Area (Restoration Room),Misc - Sorting, packing, light assembly | #REF! | 67 | #REF! | 2, 67, "Misc - Sorting, packing, light assembly"
Office Area (<250 square feet) | Office - Office space | 0.15 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Office Area (<250 square feet),Office - Office space | #REF! | 74 | #REF! | #REF!
Office Area (<250 square feet) | Office - Office space | 0.15 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Office Area (<250 square feet),Office - Office space | #REF! | 74 | #REF! | 2, 74, "Office - Office space"
Office Area (>250 square feet) | Office - Office space | 0.15 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Office Area (>250 square feet),Office - Office space | #REF! | 74 | #REF! | #REF!
Office Area (>250 square feet) | Office - Office space | 0.15 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Office Area (>250 square feet),Office - Office space | #REF! | 74 | #REF! | 2, 74, "Office - Office space"
Office Area (Open plan office) | Office - Office space | 0.15 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Office Area (Open plan office),Office - Office space | #REF! | 74 | #REF! | #REF!
Office Area (Open plan office) | Office - Office space | 0.15 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Office Area (Open plan office),Office - Office space | #REF! | 74 | #REF! | 2, 74, "Office - Office space"
Parking Garage Area (Daylight Adaptation Zones) | Exhaust - Parking garages | 0 | 0 | 0 | 0 | 0.75 | 2 | Exh. Note C | Yes | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Parking Garage Area (Daylight Adaptation Zones),Exhaust - Parking garages | #REF! | 34 | #REF! | #REF!
Parking Garage Area (Daylight Adaptation Zones) | Exhaust - Parking garages | 0 | 0 | 0 | 0 | 0.75 | 2 | Exh. Note C | Yes | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Parking Garage Area (Daylight Adaptation Zones),Exhaust - Parking garages | #REF! | 34 | #REF! | 2, 34, "Exhaust - Parking garages"
Parking Garage Area (Dedicated Ramps) | Exhaust - Parking garages | 0 | 0 | 0 | 0 | 0.75 | 2 | Exh. Note C | Yes | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Parking Garage Area (Dedicated Ramps),Exhaust - Parking garages | #REF! | 34 | #REF! | #REF!
Parking Garage Area (Dedicated Ramps) | Exhaust - Parking garages | 0 | 0 | 0 | 0 | 0.75 | 2 | Exh. Note C | Yes | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Parking Garage Area (Dedicated Ramps),Exhaust - Parking garages | #REF! | 34 | #REF! | 2, 34, "Exhaust - Parking garages"
Parking Garage Area (Parking Zone) | Exhaust - Parking garages | 0 | 0 | 0 | 0 | 0.75 | 2 | Exh. Note C | Yes | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Parking Garage Area (Parking Zone),Exhaust - Parking garages | #REF! | 34 | #REF! | #REF!
Parking Garage Area (Parking Zone) | Exhaust - Parking garages | 0 | 0 | 0 | 0 | 0.75 | 2 | Exh. Note C | Yes | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Parking Garage Area (Parking Zone),Exhaust - Parking garages | #REF! | 34 | #REF! | 2, 34, "Exhaust - Parking garages"
Pharmacy Area | Misc - Pharmacy (preparation area) | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Pharmacy Area,Misc - Pharmacy (preparation area) | #REF! | 64 | #REF! | #REF!
Pharmacy Area | Misc - Pharmacy (preparation area) | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Pharmacy Area,Misc - Pharmacy (preparation area) | #REF! | 64 | #REF! | 2, 64, "Misc - Pharmacy (preparation area)"
Religious Worship Area | Assembly - Places of religious worship | 1.07 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 71.3333 | 71.3333 | 15 | #REF! | #REF! | Religious Worship Area,Assembly - Places of religious worship | #REF! | 8 | #REF! | #REF!
Religious Worship Area | Assembly - Places of religious worship | 1.07 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 71.3333 | 71.3333 | 15 | #REF! | #REF! | Religious Worship Area,Assembly - Places of religious worship | #REF! | 8 | #REF! | 2, 8, "Assembly - Places of religious worship"
Restrooms | Exhaust - Toilets, public | 0 | 0 | 50 | 0 | 0 | 2 | Exh. Note D | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Restrooms,Exhaust - Toilets, public | #REF! | 40 | #REF! | #REF!
Restrooms | Exhaust - Shower rooms | 0 | 0 | 20 | 50 | 0 | 2 | Exh. Note G,H | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Restrooms,Exhaust - Shower rooms | #REF! | 36 | #REF! | 2, 36, "Exhaust - Shower rooms"
Restrooms | Exhaust - Toilets, private | 0 | 0 | 25 | 50 | 0 | 2 | Exh. Note E | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Restrooms,Exhaust - Toilets, private | #REF! | 39 | #REF! | 2, 39, "Exhaust - Toilets, private"
Restrooms | Exhaust - Toilets, public | 0 | 0 | 50 | 0 | 0 | 2 | Exh. Note D | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Restrooms,Exhaust - Toilets, public | #REF! | 40 | #REF! | 2, 40, "Exhaust - Toilets, public"
Retail Sales Area (Fitting Room) | Retail - Sales | 0.25 | 0.2 | 0 | 0 | 0 | 2 |  | No | #REF! | 16.6667 | 16.6667 | 15 | #REF! | #REF! | Retail Sales Area (Fitting Room),Retail - Sales | #REF! | 83 | #REF! | #REF!
Retail Sales Area (Fitting Room) | Retail - Sales | 0.25 | 0.2 | 0 | 0 | 0 | 2 |  | No | #REF! | 16.6667 | 16.6667 | 15 | #REF! | #REF! | Retail Sales Area (Fitting Room),Retail - Sales | #REF! | 83 | #REF! | 2, 83, "Retail - Sales"
Retail Sales Area (Fitting Room) | Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Retail Sales Area (Fitting Room),Misc - All others | #REF! | 58 | #REF! | 2, 58, "Misc - All others"
Retail Sales Area (Grocery Sales) | Retail - Supermarket | 0.25 | 0.2 | 0 | 0 | 0 | 1 | F | No | #REF! | 16.6667 | 16.6667 | 15 | #REF! | #REF! | Retail Sales Area (Grocery Sales),Retail - Supermarket | #REF! | 84 | #REF! | #REF!
Retail Sales Area (Grocery Sales) | Retail - Supermarket | 0.25 | 0.2 | 0 | 0 | 0 | 1 | F | No | #REF! | 16.6667 | 16.6667 | 15 | #REF! | #REF! | Retail Sales Area (Grocery Sales),Retail - Supermarket | #REF! | 84 | #REF! | 2, 84, "Retail - Supermarket"
Retail Sales Area (Retail Merchandise Sales) | Retail - Sales | 0.25 | 0.2 | 0 | 0 | 0 | 2 |  | No | #REF! | 16.6667 | 16.6667 | 15 | #REF! | #REF! | Retail Sales Area (Retail Merchandise Sales),Retail - Sales | #REF! | 83 | #REF! | #REF!
Retail Sales Area (Retail Merchandise Sales) | Retail - Sales | 0.25 | 0.2 | 0 | 0 | 0 | 2 |  | No | #REF! | 16.6667 | 16.6667 | 15 | #REF! | #REF! | Retail Sales Area (Retail Merchandise Sales),Retail - Sales | #REF! | 83 | #REF! | 2, 83, "Retail - Sales"
Retail Sales Area (Retail Merchandise Sales) | Retail - Pet shops (animal areas) | 0.25 | 0.15 | 0 | 0 | 0.9 | 2 |  | No | #REF! | 16.6667 | 16.6667 | 15 | #REF! | #REF! | Retail Sales Area (Retail Merchandise Sales),Retail - Pet shops (animal areas) | #REF! | 82 | #REF! | 2, 82, "Retail - Pet shops (animal areas)"
Scientific Laboratory Area | Education - University/college laboratories | 0.15 | 0.15 | 0 | 0 | 1 | 2 |  | Yes | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Scientific Laboratory Area,Education - University/college laboratories | #REF! | 22 | #REF! | #REF!
Scientific Laboratory Area | Education - Science laboratories | 0.15 | 0.15 | 0 | 0 | 1 | 2 |  | Yes | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Scientific Laboratory Area,Education - Science laboratories | #REF! | 21 | #REF! | 2, 21, "Education - Science laboratories"
Scientific Laboratory Area | Education - University/college laboratories | 0.15 | 0.15 | 0 | 0 | 1 | 2 |  | Yes | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Scientific Laboratory Area,Education - University/college laboratories | #REF! | 22 | #REF! | 2, 22, "Education - University/college laboratories"
Scientific Laboratory Area | Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 0.15 | 0.15 | 0 | 0 | 0 | 3 |  | Yes | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Scientific Laboratory Area,Misc - General manufacturing (excludes heavy industrial and process using chemicals) | #REF! | 63 | #REF! | 2, 63, "Misc - General manufacturing (excludes heavy industrial and process using chemicals)"
Scientific Laboratory Area | Misc - Pharmacy (preparation area) | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Scientific Laboratory Area,Misc - Pharmacy (preparation area) | #REF! | 64 | #REF! | 2, 64, "Misc - Pharmacy (preparation area)"
Scientific Laboratory Area | Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Scientific Laboratory Area,Misc - All others | #REF! | 58 | #REF! | 2, 58, "Misc - All others"
Sports Arena - Playing Area (> 5,000 Spectators) | Sports/Entertainment - Gym, sports arena (play area) | 0.5 | 0.15 | 0 | 0 | 0 | 2 | E | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Sports Arena - Playing Area (> 5,000 Spectators),Sports/Entertainment - Gym, sports arena (play area) | #REF! | 89 | #REF! | #REF!
Sports Arena - Playing Area (> 5,000 Spectators) | Exhaust - Arenas | 0 | 0 | 0 | 0 | 0.5 | 1 | Exh. Note B | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Sports Arena - Playing Area (> 5,000 Spectators),Exhaust - Arenas | #REF! | 25 | #REF! | 2, 25, "Exhaust - Arenas"
Sports Arena - Playing Area (> 5,000 Spectators) | Sports/Entertainment - Gym, sports arena (play area) | 0.5 | 0.15 | 0 | 0 | 0 | 2 | E | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Sports Arena - Playing Area (> 5,000 Spectators),Sports/Entertainment - Gym, sports arena (play area) | #REF! | 89 | #REF! | 2, 89, "Sports/Entertainment - Gym, sports arena (play area)"
Sports Arena - Playing Area (> 5,000 Spectators) | Sports/Entertainment - Swimming (deck) | 0.5 | 0.15 | 0 | 0 | 0 | 2 | C | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Sports Arena - Playing Area (> 5,000 Spectators),Sports/Entertainment - Swimming (deck) | #REF! | 94 | #REF! | 2, 94, "Sports/Entertainment - Swimming (deck)"
Sports Arena - Playing Area (> 5,000 Spectators) | Sports/Entertainment - Swimming (pool) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Sports Arena - Playing Area (> 5,000 Spectators),Sports/Entertainment - Swimming (pool) | #REF! | 95 | #REF! | 2, 95, "Sports/Entertainment - Swimming (pool)"
Sports Arena - Playing Area (2,000 - 5,000 Spectators) | Sports/Entertainment - Gym, sports arena (play area) | 0.5 | 0.15 | 0 | 0 | 0 | 2 | E | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Sports Arena - Playing Area (2,000 - 5,000 Spectators),Sports/Entertainment - Gym, sports arena (play area) | #REF! | 89 | #REF! | #REF!
Sports Arena - Playing Area (2,000 - 5,000 Spectators) | Exhaust - Arenas | 0 | 0 | 0 | 0 | 0.5 | 1 | Exh. Note B | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Sports Arena - Playing Area (2,000 - 5,000 Spectators),Exhaust - Arenas | #REF! | 25 | #REF! | 2, 25, "Exhaust - Arenas"
Sports Arena - Playing Area (2,000 - 5,000 Spectators) | Sports/Entertainment - Gym, sports arena (play area) | 0.5 | 0.15 | 0 | 0 | 0 | 2 | E | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Sports Arena - Playing Area (2,000 - 5,000 Spectators),Sports/Entertainment - Gym, sports arena (play area) | #REF! | 89 | #REF! | 2, 89, "Sports/Entertainment - Gym, sports arena (play area)"
Sports Arena - Playing Area (2,000 - 5,000 Spectators) | Sports/Entertainment - Swimming (deck) | 0.5 | 0.15 | 0 | 0 | 0 | 2 | C | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Sports Arena - Playing Area (2,000 - 5,000 Spectators),Sports/Entertainment - Swimming (deck) | #REF! | 94 | #REF! | 2, 94, "Sports/Entertainment - Swimming (deck)"
Sports Arena - Playing Area (2,000 - 5,000 Spectators) | Sports/Entertainment - Swimming (pool) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Sports Arena - Playing Area (2,000 - 5,000 Spectators),Sports/Entertainment - Swimming (pool) | #REF! | 95 | #REF! | 2, 95, "Sports/Entertainment - Swimming (pool)"
Sports Arena - Playing Area (< 2,000 Spectators) | Sports/Entertainment - Gym, sports arena (play area) | 0.5 | 0.15 | 0 | 0 | 0 | 2 | E | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Sports Arena - Playing Area (< 2,000 Spectators),Sports/Entertainment - Gym, sports arena (play area) | #REF! | 89 | #REF! | #REF!
Sports Arena - Playing Area (< 2,000 Spectators) | Exhaust - Arenas | 0 | 0 | 0 | 0 | 0.5 | 1 | Exh. Note B | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Sports Arena - Playing Area (< 2,000 Spectators),Exhaust - Arenas | #REF! | 25 | #REF! | 2, 25, "Exhaust - Arenas"
Sports Arena - Playing Area (< 2,000 Spectators) | Sports/Entertainment - Gym, sports arena (play area) | 0.5 | 0.15 | 0 | 0 | 0 | 2 | E | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Sports Arena - Playing Area (< 2,000 Spectators),Sports/Entertainment - Gym, sports arena (play area) | #REF! | 89 | #REF! | 2, 89, "Sports/Entertainment - Gym, sports arena (play area)"
Sports Arena - Playing Area (< 2,000 Spectators) | Sports/Entertainment - Swimming (deck) | 0.5 | 0.15 | 0 | 0 | 0 | 2 | C | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Sports Arena - Playing Area (< 2,000 Spectators),Sports/Entertainment - Swimming (deck) | #REF! | 94 | #REF! | 2, 94, "Sports/Entertainment - Swimming (deck)"
Sports Arena - Playing Area (< 2,000 Spectators) | Sports/Entertainment - Swimming (pool) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Sports Arena - Playing Area (< 2,000 Spectators),Sports/Entertainment - Swimming (pool) | #REF! | 95 | #REF! | 2, 95, "Sports/Entertainment - Swimming (pool)"
Sports Arena - Playing Area (Recreational) | Sports/Entertainment - Gym, sports arena (play area) | 0.5 | 0.15 | 0 | 0 | 0 | 2 | E | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Sports Arena - Playing Area (Recreational),Sports/Entertainment - Gym, sports arena (play area) | #REF! | 89 | #REF! | #REF!
Sports Arena - Playing Area (Recreational) | Sports/Entertainment - Gym, sports arena (play area) | 0.5 | 0.15 | 0 | 0 | 0 | 2 | E | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Sports Arena - Playing Area (Recreational),Sports/Entertainment - Gym, sports arena (play area) | #REF! | 89 | #REF! | 2, 89, "Sports/Entertainment - Gym, sports arena (play area)"
Sports Arena - Playing Area (Recreational) | Sports/Entertainment - Health club/aerobics room | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Sports Arena - Playing Area (Recreational),Sports/Entertainment - Health club/aerobics room | #REF! | 90 | #REF! | 2, 90, "Sports/Entertainment - Health club/aerobics room"
Sports Arena - Playing Area (Recreational) | Sports/Entertainment - Health club/weight rooms | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Sports Arena - Playing Area (Recreational),Sports/Entertainment - Health club/weight rooms | #REF! | 91 | #REF! | 2, 91, "Sports/Entertainment - Health club/weight rooms"
Sports Arena - Playing Area (Recreational) | Sports/Entertainment - Swimming (deck) | 0.5 | 0.15 | 0 | 0 | 0 | 2 | C | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Sports Arena - Playing Area (Recreational),Sports/Entertainment - Swimming (deck) | #REF! | 94 | #REF! | 2, 94, "Sports/Entertainment - Swimming (deck)"
Sports Arena - Playing Area (Recreational) | Sports/Entertainment - Swimming (pool) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Sports Arena - Playing Area (Recreational),Sports/Entertainment - Swimming (pool) | #REF! | 95 | #REF! | 2, 95, "Sports/Entertainment - Swimming (pool)"
Stairwell | General - Corridors | 0.15 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Stairwell,General - Corridors | #REF! | 49 | #REF! | #REF!
Stairwell | General - Corridors | 0.15 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Stairwell,General - Corridors | #REF! | 49 | #REF! | 2, 49, "General - Corridors"
Stairwell | General - Unoccupied | 0 | 0 | 0 | 0 | 0 | 1 |  | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Stairwell,General - Unoccupied | #REF! | 51 | #REF! | 2, 51, "General - Unoccupied"
Stairwell | Residential - Common corridors | 0.15 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Stairwell,Residential - Common corridors | #REF! | 77 | #REF! | 2, 77, "Residential - Common corridors"
Theater Area (Motion Picture) | Assembly - Auditorium seating area | 1.07 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 71.3333 | 71.3333 | 15 | #REF! | #REF! | Theater Area (Motion Picture),Assembly - Auditorium seating area | #REF! | 1 | #REF! | #REF!
Theater Area (Motion Picture) | Assembly - Auditorium seating area | 1.07 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 71.3333 | 71.3333 | 15 | #REF! | #REF! | Theater Area (Motion Picture),Assembly - Auditorium seating area | #REF! | 1 | #REF! | 2, 1, "Assembly - Auditorium seating area"
Theater Area (Performance) | Sports/Entertainment - Stages, studios | 0.5 | 0.15 | 0 | 0 | 0 | 1 | D, F | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Theater Area (Performance),Sports/Entertainment - Stages, studios | #REF! | 93 | #REF! | #REF!
Theater Area (Performance) | Education - Music/theater/dance | 1.07 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | #N/A | #N/A | #N/A | #REF! | #REF! | Theater Area (Performance),Education - Music/theater/dance | #REF! | #N/A | #REF! | #N/A
Theater Area (Performance) | Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Theater Area (Performance),Misc - All others | #REF! | 58 | #REF! | 2, 58, "Misc - All others"
Theater Area (Performance) | Sports/Entertainment - Stages, studios | 0.5 | 0.15 | 0 | 0 | 0 | 1 | D, F | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Theater Area (Performance),Sports/Entertainment - Stages, studios | #REF! | 93 | #REF! | 2, 93, "Sports/Entertainment - Stages, studios"
Transportation Function (Baggage Area) | Misc - Transportation waiting | 0.5 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Transportation Function (Baggage Area),Misc - Transportation waiting | #REF! | 69 | #REF! | #REF!
Transportation Function (Baggage Area) | Misc - Sorting, packing, light assembly | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Transportation Function (Baggage Area),Misc - Sorting, packing, light assembly | #REF! | 67 | #REF! | 2, 67, "Misc - Sorting, packing, light assembly"
Transportation Function (Baggage Area) | Misc - Transportation waiting | 0.5 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Transportation Function (Baggage Area),Misc - Transportation waiting | #REF! | 69 | #REF! | 2, 69, "Misc - Transportation waiting"
Transportation Function (Ticketing Area) | Misc - Transportation waiting | 0.5 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Transportation Function (Ticketing Area),Misc - Transportation waiting | #REF! | 69 | #REF! | #REF!
Transportation Function (Ticketing Area) | Assembly - Lobbies | 0.5 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Transportation Function (Ticketing Area),Assembly - Lobbies | #REF! | 5 | #REF! | 2, 5, "Assembly - Lobbies"
Transportation Function (Ticketing Area) | Misc - Transportation waiting | 0.5 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Transportation Function (Ticketing Area),Misc - Transportation waiting | #REF! | 69 | #REF! | 2, 69, "Misc - Transportation waiting"
Unleased Tenant Area | Office - Office space | 0.15 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Unleased Tenant Area,Office - Office space | #REF! | 74 | #REF! | #REF!
Unleased Tenant Area | Retail - Sales | 0.25 | 0.2 | 0 | 0 | 0 | 2 |  | No | #REF! | 16.6667 | 16.6667 | 15 | #REF! | #REF! | Unleased Tenant Area,Retail - Sales | #REF! | 83 | #REF! | 2, 83, "Retail - Sales"
Unleased Tenant Area | Food Service - Cafeteria/fast-food dining | 0.5 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Unleased Tenant Area,Food Service - Cafeteria/fast-food dining | #REF! | 43 | #REF! | 2, 43, "Food Service - Cafeteria/fast-food dining"
Unleased Tenant Area | Food Service - Restaurant dining rooms | 0.5 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Unleased Tenant Area,Food Service - Restaurant dining rooms | #REF! | 45 | #REF! | 2, 45, "Food Service - Restaurant dining rooms"
Unleased Tenant Area | Misc - All others | 0.15 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Unleased Tenant Area,Misc - All others | #REF! | 58 | #REF! | 2, 58, "Misc - All others"
Unleased Tenant Area | Misc - Warehouses | 0.15 | 0.15 | 0 | 0 | 0 | 2 | B | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Unleased Tenant Area,Misc - Warehouses | #REF! | 70 | #REF! | 2, 70, "Misc - Warehouses"
Unleased Tenant Area | Office - Office space | 0.15 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Unleased Tenant Area,Office - Office space | #REF! | 74 | #REF! | 2, 74, "Office - Office space"
Unoccupied-Exclude from Gross Floor Area | NA | 0.15 | 0.15 | 0 | 0 | 0 | 2 | B | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Unoccupied-Exclude from Gross Floor Area,NA | #REF! | 96 | #REF! | #REF!
Unoccupied-Exclude from Gross Floor Area | NA | 0.15 | 0.15 | 0 | 0 | 0 | 2 | B | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Unoccupied-Exclude from Gross Floor Area,NA | #REF! | 96 | #REF! | 2, 96, "NA"
Unoccupied-Include in Gross Floor Area | NA | 0.15 | 0.15 | 0 | 0 | 0 | 2 | B | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Unoccupied-Include in Gross Floor Area,NA | #REF! | 96 | #REF! | #REF!
Unoccupied-Include in Gross Floor Area | NA | 0.15 | 0.15 | 0 | 0 | 0 | 2 | B | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Unoccupied-Include in Gross Floor Area,NA | #REF! | 96 | #REF! | 2, 96, "NA"
Videoconferencing Studio | General - Conference/meeting | 0.5 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Videoconferencing Studio,General - Conference/meeting | #REF! | 48 | #REF! | #REF!
Videoconferencing Studio | General - Conference/meeting | 0.5 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Videoconferencing Studio,General - Conference/meeting | #REF! | 48 | #REF! | 2, 48, "General - Conference/meeting"
Aging Eye/Low-vision (Corridor Area) | General - Corridors | 0.15 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Aging Eye/Low-vision (Corridor Area),General - Corridors | #REF! | 49 | #REF! | #REF!
Aging Eye/Low-vision (Corridor Area) | General - Corridors | 0.15 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Aging Eye/Low-vision (Corridor Area),General - Corridors | #REF! | 49 | #REF! | 2, 49, "General - Corridors"
Aging Eye/Low-vision (Dining) | Food Service - Cafeteria/fast-food dining | 0.5 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Aging Eye/Low-vision (Dining),Food Service - Cafeteria/fast-food dining | #REF! | 43 | #REF! | #REF!
Aging Eye/Low-vision (Dining) | Food Service - Cafeteria/fast-food dining | 0.5 | 0.15 | 0 | 0 | 0 | 2 |  | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Aging Eye/Low-vision (Dining),Food Service - Cafeteria/fast-food dining | #REF! | 43 | #REF! | 2, 43, "Food Service - Cafeteria/fast-food dining"
Aging Eye/Low-vision (Lounge/Waiting Area) | General - Break rooms | 0.5 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Aging Eye/Low-vision (Lounge/Waiting Area),General - Break rooms | #REF! | 46 | #REF! | #REF!
Aging Eye/Low-vision (Lounge/Waiting Area) | General - Break rooms | 0.5 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Aging Eye/Low-vision (Lounge/Waiting Area),General - Break rooms | #REF! | 46 | #REF! | 2, 46, "General - Break rooms"
Aging Eye/Low-vision (Main Entry Lobby) | Office - Main entry lobbies | 0.5 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Aging Eye/Low-vision (Main Entry Lobby),Office - Main entry lobbies | #REF! | 72 | #REF! | #REF!
Aging Eye/Low-vision (Main Entry Lobby) | Office - Main entry lobbies | 0.5 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Aging Eye/Low-vision (Main Entry Lobby),Office - Main entry lobbies | #REF! | 72 | #REF! | 2, 72, "Office - Main entry lobbies"
Aging Eye/Low-vision (Multipurpose Room) | General - Conference/meeting | 0.5 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Aging Eye/Low-vision (Multipurpose Room),General - Conference/meeting | #REF! | 48 | #REF! | #REF!
Aging Eye/Low-vision (Multipurpose Room) | General - Conference/meeting | 0.5 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 33.3333 | 33.3333 | 15 | #REF! | #REF! | Aging Eye/Low-vision (Multipurpose Room),General - Conference/meeting | #REF! | 48 | #REF! | 2, 48, "General - Conference/meeting"
Aging Eye/Low-vision (Religious Worship Area) | Assembly - Places of religious worship | 1.07 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 71.3333 | 71.3333 | 15 | #REF! | #REF! | Aging Eye/Low-vision (Religious Worship Area),Assembly - Places of religious worship | #REF! | 8 | #REF! | #REF!
Aging Eye/Low-vision (Religious Worship Area) | Assembly - Places of religious worship | 1.07 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 71.3333 | 71.3333 | 15 | #REF! | #REF! | Aging Eye/Low-vision (Religious Worship Area),Assembly - Places of religious worship | #REF! | 8 | #REF! | 2, 8, "Assembly - Places of religious worship"
Aging Eye/Low-vision (Restroom) | Exhaust - Toilets, public | 0 | 0 | 50 | 0 | 0 | 2 | Exh. Note D | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Aging Eye/Low-vision (Restroom),Exhaust - Toilets, public | #REF! | 40 | #REF! | #REF!
Aging Eye/Low-vision (Restroom) | Exhaust - Toilets, public | 0 | 0 | 50 | 0 | 0 | 2 | Exh. Note D | No | #REF! | 0 | #REF! | 0 | #REF! | #REF! | Aging Eye/Low-vision (Restroom),Exhaust - Toilets, public | #REF! | 40 | #REF! | 2, 40, "Exhaust - Toilets, public"
Aging Eye/Low-vision (Stairwell) | General - Corridors | 0.15 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Aging Eye/Low-vision (Stairwell),General - Corridors | #REF! | 49 | #REF! | #REF!
Aging Eye/Low-vision (Stairwell) | General - Corridors | 0.15 | 0.15 | 0 | 0 | 0 | 1 | F | No | #REF! | 0 | #REF! | 15 | #REF! | #REF! | Aging Eye/Low-vision (Stairwell),General - Corridors | #REF! | 49 | #REF! | 2, 49, "General - Corridors"
# times referenced above | VentSpcFunc from ventilation list | High-Rise Residential Mechanical Ventilation Rate (cfm) shall be Qfan:
7 | Assembly - Auditorium seating area | Qfan = (0.15 cfm/ft² x Afloor) + (3.5 cfm/bedroom x (Nbr + 1)) - (Vdwellingunit x 2 ach / 60 min/hr x Aext)
4 | Assembly - Courtrooms | where:
5 | Assembly - Legislative chambers | Afloor = dwelling unit floor area (ft²)
4 | Assembly - Libraries (reading rooms and stack areas) | Nbr = Number of bedrooms
3 | Assembly - Lobbies | Vdwellingunit = dwelling unit volume (ft³)
1 | Assembly - Museums (childrens) | Aext = fraction of dwelling unit perimeter wall and roof/ceiling exposed to the outdoors
2 | Assembly - Museums/galleries
3 | Assembly - Places of religious worship
2 | Education - Art classroom
2 | Education - Classrooms (ages 9-18)
1 | Education - Classrooms (ages 5-8)
2 | Education - Computer lab
1 | Education - Daycare (through age 4)
1 | Education - Daycare sickroom
2 | Education - Lecture hall (fixed seats)
1 | Education - Lecture/postsecondary classroom
2 | Education - Media center
3 | Education - Multiuse assembly
3 | Education - Music/theater/dance
3 | Education - Science laboratories
4 | Education - University/college laboratories
2 | Education - Wood shop
1 | Exhaust - All other locker rooms
5 | Exhaust - Arenas
3 | Exhaust - Auto repair rooms
1 | Exhaust - Cells with toilet
6 | Exhaust - Copy, printing rooms
4 | Exhaust - Darkrooms
1 | Exhaust - Janitor closets, trash rooms, recycling
2 | Exhaust - Kitchenettes
2 | Exhaust - Locker rooms for athletic or industrial facilities
3 | Exhaust - Paint spray booths
6 | Exhaust - Parking garages
2 | Exhaust - Refrigerating machinery rooms
2 | Exhaust - Shower rooms
1 | Exhaust - Soiled laundry storage rooms
1 | Exhaust - Storage rooms, chemical
0 | Exhaust - Toilets - private
2 | Exhaust - Toilets, public
5 | Exhaust - Woodwork shop/classrooms
2 | Food Service - Bars, cocktail lounges
5 | Food Service - Cafeteria/fast-food dining
3 | Food Service - Kitchen (cooking)
4 | Food Service - Restaurant dining rooms
2 | General - Break rooms
1 | General - Coffee Stations
6 | General - Conference/meeting
5 | General - Corridors
2 | General - Occupiable storage rooms for liquids or gels
3 | General - Unoccupied
1 | Lodging - Barracks sleeping areas
2 | Lodging - Bedroom/living room
1 | Lodging - Laundry rooms within dwelling units
3 | Lodging - Laundry rooms, central
4 | Lodging - Lobbies/pre-function
3 | Lodging - Multipurpose assembly
41 | Misc - All others
1 | Misc - Bank vaults/safe deposit
3 | Misc - Banks or bank lobbies
2 | Misc - Computer (not printing)
2 | Misc - Freezer and refrigerated spaces (<50F)
9 | Misc - General manufacturing (excludes heavy industrial and process using chemicals)
3 | Misc - Pharmacy (preparation area)
1 | Misc - Photo studios
2 | Misc - Shipping/receiving
5 | Misc - Sorting, packing, light assembly
2 | Misc - Telephone closets
7 | Misc - Transportation waiting
3 | Misc - Warehouses
1 | Office - Breakrooms
3 | Office - Main entry lobbies
1 | Office - Occupiable storage rooms for dry materials
9 | Office - Office space
1 | Office - Reception areas
1 | Office - Telephone/data entry
2 | Residential - Common corridors
2 | Retail - Barbershop
3 | Retail - Beauty and nail salons
1 | Retail - Coin-operated laundries
3 | Retail - Mall common areas
1 | Retail - Pet shops (animal areas)
5 | Retail - Sales
2 | Retail - Supermarket
1 | Sports/Entertainment - Bowling alley (seating)
1 | Sports/Entertainment - Disco/dance floors
1 | Sports/Entertainment - Gambling casinos
1 | Sports/Entertainment - Game arcades
10 | Sports/Entertainment - Gym, sports arena (play area)
2 | Sports/Entertainment - Health club/aerobics room
2 | Sports/Entertainment - Health club/weight rooms
1 | Sports/Entertainment - Spectator areas
2 | Sports/Entertainment - Stages, studios
5 | Sports/Entertainment - Swimming (deck)
Note on Y3: David Reddy: Line Feed (Char(10))
Note on M6: David Reddy: IfVentSpcFunc occupancy is 0, then use SpcFunc occupancy
Note on O6: David Reddy: This is the VentPerPerson assumed in rules for modeling DCV
Note on P6: David Reddy: Highlighted values are greater than the Ra defined in VentSpcFunc table

## 25 SpcFunc & VentSpcFunc combos
Text File Generation
[15 empty] | 0.03 | [5 empty] | 1, Spc:SpcFunc, | , | ;
[21 empty] | 2, | , "
For Rules
2025 NACM Space Type | Allowed Ventilation Space Type (Default in Bold Red) | Area Outdoor Air Rate Ra | Min Air Rate for DCVb | Continuous Exhaust Rate, | Intermittent Exhaust Rate, | Exhaust Rate, | Air Class | Notes | Baseline ventilation = proposed? | SpcOccDensSim | VentOccDensSim | VentOccDensSim used in rules | VentSpcFunc, Rp assumed for Design Ra | VentSpcFunc Rp_adj, Adjusted for Spc | Calculated Ra based on Rp_Adj at design occupancy | For TABLE ValidVentilationSpaceFunctionEnumerations look-up | SpcFuncIdx - 2025 | VentSpcFuncIdx | SpcFuncIdx | ResOtherZnFunc
SpcFunc | VentSpcFunc | cfm/ft² | cfm/ft² | cfm/unit | cfm/unit | cfm/ft² |  |  |  | # per 1000 ft² | # per 1000 ft² | # per 1000 ft² | cfm/person | cfm/person | cfm/ft2 |  |  |  |  | 0/1 | 0, Spc:VentSpcFunc, 0
All other | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | All other,Misc - All others | 301 | 58 | 79 | 1 | 1, Spc:SpcFunc, 301, 58 ; All other
All other | General - Unoccupied | 0 | 0 | 0 | 0 | 0 | 1 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | All other,General - Unoccupied | 301 | 51 | 79 | 1 | 2, 51, "General - Unoccupied"
All other | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | All other,Misc - All others | 301 | 58 | 79 | 1 | 2, 58, "Misc - All others"
All other | Exhaust - Cells with toilet | 0 | 0 | 0 | 0 | 1 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | All other,Exhaust - Cells with toilet | 301 | 27 | 79 | 0 | 2, 27, "Exhaust - Cells with toilet"
All other | Sports/Entertainment - Game arcades | 100 | 0.15 | 0 | 0 | 0 | 2 | F | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | All other,Sports/Entertainment - Game arcades | 301 | 88 | 79 | 0 | 2, 88, "Sports/Entertainment - Game arcades"
Aging Eye/Low-vision (Corridor Area) | General - Corridors | 5 | 0.15 | 0 | 0 | 0 | 1 | F | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Aging Eye/Low-vision (Corridor Area),General - Corridors | 302 | 49 | 1 | 1 | 1, Spc:SpcFunc, 302, 49 ; Aging Eye/Low-vision (Corridor Area)
Aging Eye/Low-vision (Corridor Area) | General - Corridors | 5 | 0.15 | 0 | 0 | 0 | 1 | F | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Aging Eye/Low-vision (Corridor Area),General - Corridors | 302 | 49 | 1 | 1 | 2, 49, "General - Corridors"
Aging Eye/Low-vision (Dining) | Food Service - Cafeteria/fast-food dining | 33 | 0.15 | 0 | 0 | 0 | 2 |  | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Aging Eye/Low-vision (Dining),Food Service - Cafeteria/fast-food dining | 303 | 43 | 2 | 1 | 1, Spc:SpcFunc, 303, 43 ; Aging Eye/Low-vision (Dining)
Aging Eye/Low-vision (Dining) | Food Service - Cafeteria/fast-food dining | 33 | 0.15 | 0 | 0 | 0 | 2 |  | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Aging Eye/Low-vision (Dining),Food Service - Cafeteria/fast-food dining | 303 | 43 | 2 | 1 | 2, 43, "Food Service - Cafeteria/fast-food dining"
Aging Eye/Low-vision (Lobby, Main Entry) | Office - Main entry lobbies | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Aging Eye/Low-vision (Lobby, Main Entry),Office - Main entry lobbies | 304 | 72 | 3 | 1 | 1, Spc:SpcFunc, 304, 72 ; Aging Eye/Low-vision (Lobby, Main Entry)
Aging Eye/Low-vision (Lobby, Main Entry) | Office - Main entry lobbies | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Aging Eye/Low-vision (Lobby, Main Entry),Office - Main entry lobbies | 304 | 72 | 3 | 1 | 2, 72, "Office - Main entry lobbies"
Aging Eye/Low-vision (Lounge/Waiting Area) | General - Break rooms | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Aging Eye/Low-vision (Lounge/Waiting Area),General - Break rooms | 305 | 46 | 4 | 1 | 1, Spc:SpcFunc, 305, 46 ; Aging Eye/Low-vision (Lounge/Waiting Area)
Aging Eye/Low-vision (Lounge/Waiting Area) | General - Break rooms | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Aging Eye/Low-vision (Lounge/Waiting Area),General - Break rooms | 305 | 46 | 4 | 1 | 2, 46, "General - Break rooms"
Aging Eye/Low-vision (Multipurpose Room) | General - Conference/meeting | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Aging Eye/Low-vision (Multipurpose Room),General - Conference/meeting | 306 | 48 | 5 | 1 | 1, Spc:SpcFunc, 306, 48 ; Aging Eye/Low-vision (Multipurpose Room)
Aging Eye/Low-vision (Multipurpose Room) | General - Conference/meeting | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Aging Eye/Low-vision (Multipurpose Room),General - Conference/meeting | 306 | 48 | 5 | 1 | 2, 48, "General - Conference/meeting"
Aging Eye/Low-vision (Religious Worship Area) | Assembly - Places of religious worship | 7 | 0.15 | 0 | 0 | 0 | 1 | F | No | 71.43 | #REF! | #REF! | #REF! | #REF! | #REF! | Aging Eye/Low-vision (Religious Worship Area),Assembly - Places of religious worship | 307 | 8 | 6 | 0 | 1, Spc:SpcFunc, 307, 8 ; Aging Eye/Low-vision (Religious Worship Area)
Aging Eye/Low-vision (Religious Worship Area) | Assembly - Places of religious worship | 7 | 0.15 | 0 | 0 | 0 | 1 | F | No | 71.43 | #REF! | #REF! | #REF! | #REF! | #REF! | Aging Eye/Low-vision (Religious Worship Area),Assembly - Places of religious worship | 307 | 8 | 6 | 0 | 2, 8, "Assembly - Places of religious worship"
Aging Eye/Low-vision (Restroom) | Exhaust - Toilets, public | 0 | 0 | 50 | 70 | 0 | 2 | Exh. Note D | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Aging Eye/Low-vision (Restroom),Exhaust - Toilets, public | 308 | 40 | 7 | 1 | 1, Spc:SpcFunc, 308, 40 ; Aging Eye/Low-vision (Restroom)
Aging Eye/Low-vision (Restroom) | Exhaust - Toilets, public | 0 | 0 | 50 | 70 | 0 | 2 | Exh. Note D | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Aging Eye/Low-vision (Restroom),Exhaust - Toilets, public | 308 | 40 | 7 | 1 | 2, 40, "Exhaust - Toilets, public"
Aging Eye/Low-vision (Stairwell) | General - Corridors | 5 | 0.15 | 0 | 0 | 0 | 1 | F | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Aging Eye/Low-vision (Stairwell),General - Corridors | 309 | 49 | 8 | 1 | 1, Spc:SpcFunc, 309, 49 ; Aging Eye/Low-vision (Stairwell)
Aging Eye/Low-vision (Stairwell) | General - Corridors | 5 | 0.15 | 0 | 0 | 0 | 1 | F | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Aging Eye/Low-vision (Stairwell),General - Corridors | 309 | 49 | 8 | 1 | 2, 49, "General - Corridors"
Audience Seating Area | Assembly - Auditorium seating area | 7 | 0.15 | 0 | 0 | 0 | 1 | F | No | 71.43 | #REF! | #REF! | #REF! | #REF! | #REF! | Audience Seating Area,Assembly - Auditorium seating area | 310 | 1 | 9 | 0 | 1, Spc:SpcFunc, 310, 1 ; Audience Seating Area
Audience Seating Area | Assembly - Auditorium seating area | 7 | 0.15 | 0 | 0 | 0 | 1 | F | No | 71.43 | #REF! | #REF! | #REF! | #REF! | #REF! | Audience Seating Area,Assembly - Auditorium seating area | 310 | 1 | 9 | 0 | 2, 1, "Assembly - Auditorium seating area"
Audience Seating Area | Assembly - Courtrooms | 13 | 0.15 | 0 | 0 | 0 | 1 | F | No | 71.43 | #REF! | #REF! | #REF! | #REF! | #REF! | Audience Seating Area,Assembly - Courtrooms | 310 | 2 | 9 | 0 | 2, 2, "Assembly - Courtrooms"
Audience Seating Area | Assembly - Legislative chambers | 13 | 0.15 | 0 | 0 | 0 | 1 | F | No | 71.43 | #REF! | #REF! | #REF! | #REF! | #REF! | Audience Seating Area,Assembly - Legislative chambers | 310 | 3 | 9 | 0 | 2, 3, "Assembly - Legislative chambers"
Audience Seating Area | Exhaust - Arenas | 0 | 0 | 0 | 0 | 0.5 | 1 | Exh. Note B | No | 71.43 | #REF! | #REF! | #REF! | #REF! | #REF! | Audience Seating Area,Exhaust - Arenas | 310 | 25 | 9 | 0 | 2, 25, "Exhaust - Arenas"
Audience Seating Area | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 71.43 | #REF! | #REF! | #REF! | #REF! | #REF! | Audience Seating Area,Misc - All others | 310 | 58 | 9 | 0 | 2, 58, "Misc - All others"
Audience Seating Area | Sports/Entertainment - Bowling alley (seating) | 7 | 0.15 | 0 | 0 | 0 | 1 |  | No | 71.43 | #REF! | #REF! | #REF! | #REF! | #REF! | Audience Seating Area,Sports/Entertainment - Bowling alley (seating) | 310 | 85 | 9 | 0 | 2, 85, "Sports/Entertainment - Bowling alley (seating)"
Audience Seating Area | Sports/Entertainment - Spectator areas | 100 | 0.15 | 0 | 0 | 0 | 2 | F | No | 71.43 | #REF! | #REF! | #REF! | #REF! | #REF! | Audience Seating Area,Sports/Entertainment - Spectator areas | 310 | 92 | 9 | 0 | 2, 92, "Sports/Entertainment - Spectator areas"
Auditorium Area | Assembly - Auditorium seating area | 7 | 0.15 | 0 | 0 | 0 | 1 | F | No | 71.43 | #REF! | #REF! | #REF! | #REF! | #REF! | Auditorium Area,Assembly - Auditorium seating area | 311 | 1 | 10 | 0 | 1, Spc:SpcFunc, 311, 1 ; Auditorium Area
Auditorium Area | Assembly - Auditorium seating area | 7 | 0.15 | 0 | 0 | 0 | 1 | F | No | 71.43 | #REF! | #REF! | #REF! | #REF! | #REF! | Auditorium Area,Assembly - Auditorium seating area | 311 | 1 | 10 | 0 | 2, 1, "Assembly - Auditorium seating area"
Auditorium Area | Assembly - Courtrooms | 13 | 0.15 | 0 | 0 | 0 | 1 | F | No | 71.43 | #REF! | #REF! | #REF! | #REF! | #REF! | Auditorium Area,Assembly - Courtrooms | 311 | 2 | 10 | 0 | 2, 2, "Assembly - Courtrooms"
Auditorium Area | Assembly - Legislative chambers | 13 | 0.15 | 0 | 0 | 0 | 1 | F | No | 71.43 | #REF! | #REF! | #REF! | #REF! | #REF! | Auditorium Area,Assembly - Legislative chambers | 311 | 3 | 10 | 0 | 2, 3, "Assembly - Legislative chambers"
Auditorium Area | Exhaust - Arenas | 0 | 0 | 0 | 0 | 0.5 | 1 | Exh. Note B | No | 71.43 | #REF! | #REF! | #REF! | #REF! | #REF! | Auditorium Area,Exhaust - Arenas | 311 | 25 | 10 | 0 | 2, 25, "Exhaust - Arenas"
Auditorium Area | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 71.43 | #REF! | #REF! | #REF! | #REF! | #REF! | Auditorium Area,Misc - All others | 311 | 58 | 10 | 0 | 2, 58, "Misc - All others"
Auto Repair / Maintenance Area | Exhaust - Auto repair rooms | 0 | 0 | 0 | 0 | 1.5 | 2 | Exh. Note A | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Auto Repair / Maintenance Area,Exhaust - Auto repair rooms | 312 | 26 | 11 | 0 | 1, Spc:SpcFunc, 312, 26 ; Auto Repair / Maintenance Area
Auto Repair / Maintenance Area | Exhaust - Auto repair rooms | 0 | 0 | 0 | 0 | 1.5 | 2 | Exh. Note A | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Auto Repair / Maintenance Area,Exhaust - Auto repair rooms | 312 | 26 | 11 | 0 | 2, 26, "Exhaust - Auto repair rooms"
Barber, Beauty Salon, Spa Area | Retail - Beauty and nail salons | 17 | 0.4 | 0 | 0 | 0.6 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Barber, Beauty Salon, Spa Area,Retail - Beauty and nail salons | 313 | 79 | 12 | 0 | 1, Spc:SpcFunc, 313, 79 ; Barber, Beauty Salon, Spa Area
Barber, Beauty Salon, Spa Area | Retail - Barbershop | 17 | 0.4 | 0 | 0 | 0.5 | 2 | F | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Barber, Beauty Salon, Spa Area,Retail - Barbershop | 313 | 78 | 12 | 0 | 2, 78, "Retail - Barbershop"
Barber, Beauty Salon, Spa Area | Retail - Beauty and nail salons | 17 | 0.4 | 0 | 0 | 0.6 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Barber, Beauty Salon, Spa Area,Retail - Beauty and nail salons | 313 | 79 | 12 | 0 | 2, 79, "Retail - Beauty and nail salons"
Civic Meeting Place Area | Assembly - Legislative chambers | 13 | 0.15 | 0 | 0 | 0 | 1 | F | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Civic Meeting Place Area,Assembly - Legislative chambers | 314 | 3 | 13 | 0 | 1, Spc:SpcFunc, 314, 3 ; Civic Meeting Place Area
Civic Meeting Place Area | Assembly - Auditorium seating area | 7 | 0.15 | 0 | 0 | 0 | 1 | F | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Civic Meeting Place Area,Assembly - Auditorium seating area | 314 | 1 | 13 | 0 | 2, 1, "Assembly - Auditorium seating area"
Civic Meeting Place Area | Assembly - Courtrooms | 13 | 0.15 | 0 | 0 | 0 | 1 | F | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Civic Meeting Place Area,Assembly - Courtrooms | 314 | 2 | 13 | 0 | 2, 2, "Assembly - Courtrooms"
Civic Meeting Place Area | Assembly - Legislative chambers | 13 | 0.15 | 0 | 0 | 0 | 1 | F | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Civic Meeting Place Area,Assembly - Legislative chambers | 314 | 3 | 13 | 0 | 2, 3, "Assembly - Legislative chambers"
Civic Meeting Place Area | General - Conference/meeting | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Civic Meeting Place Area,General - Conference/meeting | 314 | 48 | 13 | 0 | 2, 48, "General - Conference/meeting"
Civic Meeting Place Area | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Civic Meeting Place Area,Misc - All others | 314 | 58 | 13 | 0 | 2, 58, "Misc - All others"
Classroom, Lecture, Training, Vocational Areas | Education - Classrooms (ages 9-18) | 25 | 0.15 | 0 | 0 | 0 | 1 |  | No | 25 | #REF! | #REF! | #REF! | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Education - Classrooms (ages 9-18) | 315 | 10 | 14 | 0 | 1, Spc:SpcFunc, 315, 10 ; Classroom, Lecture, Training, Vocational Areas
Classroom, Lecture, Training, Vocational Areas | Education - Art classroom | 25 | 0.15 | 0 | 0 | 0.7 | 2 |  | No | 25 | #REF! | #REF! | #REF! | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Education - Art classroom | 315 | 9 | 14 | 0 | 2, 9, "Education - Art classroom"
Classroom, Lecture, Training, Vocational Areas | Education - Classrooms (ages 9-18) | 25 | 0.15 | 0 | 0 | 0 | 1 |  | No | 25 | #REF! | #REF! | #REF! | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Education - Classrooms (ages 9-18) | 315 | 10 | 14 | 0 | 2, 10, "Education - Classrooms (ages 9-18)"
Classroom, Lecture, Training, Vocational Areas | Education - Classrooms (ages 5-8) | 25 | 0.15 | 0 | 0 | 0.7 | 2 |  | No | 25 | #REF! | #REF! | #REF! | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Education - Classrooms (ages 5-8) | 315 | 11 | 14 | 0 | 2, 11, "Education - Classrooms (ages 5-8)"
Classroom, Lecture, Training, Vocational Areas | Education - Computer lab | 25 | 0.15 | 0 | 0 | 0 | 1 |  | No | 25 | #REF! | #REF! | #REF! | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Education - Computer lab | 315 | 12 | 14 | 0 | 2, 12, "Education - Computer lab"
Classroom, Lecture, Training, Vocational Areas | Education - Daycare (through age 4) | 14 | 0.15 | 0 | 0 | 0 | 2 |  | No | 25 | #REF! | #REF! | #REF! | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Education - Daycare (through age 4) | 315 | 13 | 14 | 0 | 2, 13, "Education - Daycare (through age 4)"
Classroom, Lecture, Training, Vocational Areas | Education - Daycare sickroom | 5 | 0.15 | 0 | 0 | 0 | 3 |  | No | 25 | #REF! | #REF! | #REF! | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Education - Daycare sickroom | 315 | 14 | 14 | 0 | 2, 14, "Education - Daycare sickroom"
Classroom, Lecture, Training, Vocational Areas | Education - Lecture hall (fixed seats) | 71 | 0.15 | 0 | 0 | 0 | 1 | F | No | 25 | #REF! | #REF! | #REF! | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Education - Lecture hall (fixed seats) | 315 | 15 | 14 | 0 | 2, 15, "Education - Lecture hall (fixed seats)"
Classroom, Lecture, Training, Vocational Areas | Education - Lecture/postsecondary classroom | 25 | 0.15 | 0 | 0 | 0 | 1 | F | No | 25 | #REF! | #REF! | #REF! | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Education - Lecture/postsecondary classroom | 315 | 16 | 14 | 0 | 2, 16, "Education - Lecture/postsecondary classroom"
Classroom, Lecture, Training, Vocational Areas | Education - Media center | 25 | 0.15 | 0 | 0 | 0 | 1 | A | No | 25 | #REF! | #REF! | #REF! | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Education - Media center | 315 | 17 | 14 | 0 | 2, 17, "Education - Media center"
Classroom, Lecture, Training, Vocational Areas | Education - Multiuse assembly | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 25 | #REF! | #REF! | #REF! | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Education - Multiuse assembly | 315 | 19 | 14 | 0 | 2, 19, "Education - Multiuse assembly"
Classroom, Lecture, Training, Vocational Areas | Education - Music/theater/dance | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 25 | #REF! | #REF! | #REF! | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Education - Music/theater/dance | 315 | 20 | 14 | 0 | 2, 20, "Education - Music/theater/dance"
Classroom, Lecture, Training, Vocational Areas | Education - Science laboratories | 25 | 0.15 | 0 | 0 | 1 | 2 |  | Yes | 25 | #REF! | #REF! | #REF! | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Education - Science laboratories | 315 | 21 | 14 | 0 | 2, 21, "Education - Science laboratories"
Classroom, Lecture, Training, Vocational Areas | Education - University/college laboratories | 25 | 0.15 | 0 | 0 | 1 | 2 |  | Yes | 25 | #REF! | #REF! | #REF! | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Education - University/college laboratories | 315 | 22 | 14 | 0 | 2, 22, "Education - University/college laboratories"
Classroom, Lecture, Training, Vocational Areas | Education - Wood shop | 10 | 0.15 | 0 | 0 | 0.5 | 2 |  | No | 25 | #REF! | #REF! | #REF! | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Education - Wood shop | 315 | 23 | 14 | 0 | 2, 23, "Education - Wood shop"
Classroom, Lecture, Training, Vocational Areas | Education - Metal shop | 10 | 0.15 | 0 | 0 | 0 | 2 | 0 | No | 25 | #REF! | #REF! | #REF! | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Education - Metal shop | 315 | 18 | 14 | 0 | 2, 18, "Education - Metal shop"
Classroom, Lecture, Training, Vocational Areas | Exhaust - Auto repair rooms | 0 | 0 | 0 | 0 | 1.5 | 2 | Exh. Note A | No | 25 | #REF! | #REF! | #REF! | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Exhaust - Auto repair rooms | 315 | 26 | 14 | 0 | 2, 26, "Exhaust - Auto repair rooms"
Classroom, Lecture, Training, Vocational Areas | Exhaust - Woodwork shop/classrooms | 0 | 0 | 0 | 0 | 0.5 | 2 | 0 | No | 25 | #REF! | #REF! | #REF! | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Exhaust - Woodwork shop/classrooms | 315 | 41 | 14 | 0 | 2, 41, "Exhaust - Woodwork shop/classrooms"
Classroom, Lecture, Training, Vocational Areas | Food Service - Kitchen (cooking) | 3 | 0.15 | 0 | 0 | 0.7 | 2 |  | Yes | 25 | #REF! | #REF! | #REF! | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Food Service - Kitchen (cooking) | 315 | 44 | 14 | 0 | 2, 44, "Food Service - Kitchen (cooking)"
Classroom, Lecture, Training, Vocational Areas | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 25 | #REF! | #REF! | #REF! | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Misc - All others | 315 | 58 | 14 | 0 | 2, 58, "Misc - All others"
Classroom, Lecture, Training, Vocational Areas | Retail - Barbershop | 17 | 0.4 | 0 | 0 | 0.5 | 2 | F | No | 25 | #REF! | #REF! | #REF! | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Retail - Barbershop | 315 | 78 | 14 | 0 | 2, 78, "Retail - Barbershop"
Classroom, Lecture, Training, Vocational Areas | Retail - Beauty and nail salons | 17 | 0.4 | 0 | 0 | 0.6 | 2 |  | No | 25 | #REF! | #REF! | #REF! | #REF! | #REF! | Classroom, Lecture, Training, Vocational Areas,Retail - Beauty and nail salons | 315 | 79 | 14 | 0 | 2, 79, "Retail - Beauty and nail salons"
Computer Room | Misc - Computer (not printing) | 5 | 0.15 | 0 | 0 | 0 | 1 | F | Yes | 1.5 | #REF! | #REF! | #REF! | #REF! | #REF! | Computer Room,Misc - Computer (not printing) | 316 | 61 | 15 | 0 | 1, Spc:SpcFunc, 316, 61 ; Computer Room
Computer Room | Education - Computer lab | 25 | 0.15 | 0 | 0 | 0 | 1 |  | No | 1.5 | #REF! | #REF! | #REF! | #REF! | #REF! | Computer Room,Education - Computer lab | 316 | 12 | 15 | 0 | 2, 12, "Education - Computer lab"
Computer Room | Education - Media center | 25 | 0.15 | 0 | 0 | 0 | 1 | A | No | 1.5 | #REF! | #REF! | #REF! | #REF! | #REF! | Computer Room,Education - Media center | 316 | 17 | 15 | 0 | 2, 17, "Education - Media center"
Computer Room | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 1.5 | #REF! | #REF! | #REF! | #REF! | #REF! | Computer Room,Misc - All others | 316 | 58 | 15 | 0 | 2, 58, "Misc - All others"
Computer Room | Misc - Computer (not printing) | 5 | 0.15 | 0 | 0 | 0 | 1 | F | Yes | 1.5 | #REF! | #REF! | #REF! | #REF! | #REF! | Computer Room,Misc - Computer (not printing) | 316 | 61 | 15 | 0 | 2, 61, "Misc - Computer (not printing)"
Computer Room | Office - Telephone/data entry | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 1.5 | #REF! | #REF! | #REF! | #REF! | #REF! | Computer Room,Office - Telephone/data entry | 316 | 76 | 15 | 0 | 2, 76, "Office - Telephone/data entry"
Concourse and Atria Area | Retail - Mall common areas | 17 | 0.15 | 0 | 0 | 0 | 1 | F | No | 16.665 | #REF! | #REF! | #REF! | #REF! | #REF! | Concourse and Atria Area,Retail - Mall common areas | 317 | 81 | 16 | 1 | 1, Spc:SpcFunc, 317, 81 ; Concourse and Atria Area
Concourse and Atria Area | Assembly - Lobbies | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 16.665 | #REF! | #REF! | #REF! | #REF! | #REF! | Concourse and Atria Area,Assembly - Lobbies | 317 | 5 | 16 | 0 | 2, 5, "Assembly - Lobbies"
Concourse and Atria Area | General - Corridors | 5 | 0.15 | 0 | 0 | 0 | 1 | F | No | 16.665 | #REF! | #REF! | #REF! | #REF! | #REF! | Concourse and Atria Area,General - Corridors | 317 | 49 | 16 | 1 | 2, 49, "General - Corridors"
Concourse and Atria Area | Lodging - Lobbies/pre-function | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 16.665 | #REF! | #REF! | #REF! | #REF! | #REF! | Concourse and Atria Area,Lodging - Lobbies/pre-function | 317 | 56 | 16 | 1 | 2, 56, "Lodging - Lobbies/pre-function"
Concourse and Atria Area | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 16.665 | #REF! | #REF! | #REF! | #REF! | #REF! | Concourse and Atria Area,Misc - All others | 317 | 58 | 16 | 1 | 2, 58, "Misc - All others"
Concourse and Atria Area | Misc - Transportation waiting | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 16.665 | #REF! | #REF! | #REF! | #REF! | #REF! | Concourse and Atria Area,Misc - Transportation waiting | 317 | 69 | 16 | 0 | 2, 69, "Misc - Transportation waiting"
Concourse and Atria Area | Office - Main entry lobbies | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 16.665 | #REF! | #REF! | #REF! | #REF! | #REF! | Concourse and Atria Area,Office - Main entry lobbies | 317 | 72 | 16 | 0 | 2, 72, "Office - Main entry lobbies"
Concourse and Atria Area | Retail - Mall common areas | 17 | 0.15 | 0 | 0 | 0 | 1 | F | No | 16.665 | #REF! | #REF! | #REF! | #REF! | #REF! | Concourse and Atria Area,Retail - Mall common areas | 317 | 81 | 16 | 0 | 2, 81, "Retail - Mall common areas"
Convention, Conference, Multipurpose and Meeting Area | General - Conference/meeting | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Convention, Conference, Multipurpose and Meeting Area,General - Conference/meeting | 318 | 48 | 17 | 1 | 1, Spc:SpcFunc, 318, 48 ; Convention, Conference, Multipurpose and Meeting Area
Convention, Conference, Multipurpose and Meeting Area | Assembly - Courtrooms | 13 | 0.15 | 0 | 0 | 0 | 1 | F | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Convention, Conference, Multipurpose and Meeting Area,Assembly - Courtrooms | 318 | 2 | 17 | 0 | 2, 2, "Assembly - Courtrooms"
Convention, Conference, Multipurpose and Meeting Area | Assembly - Legislative chambers | 13 | 0.15 | 0 | 0 | 0 | 1 | F | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Convention, Conference, Multipurpose and Meeting Area,Assembly - Legislative chambers | 318 | 3 | 17 | 0 | 2, 3, "Assembly - Legislative chambers"
Convention, Conference, Multipurpose and Meeting Area | Assembly - Places of religious worship | 7 | 0.15 | 0 | 0 | 0 | 1 | F | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Convention, Conference, Multipurpose and Meeting Area,Assembly - Places of religious worship | 318 | 8 | 17 | 0 | 2, 8, "Assembly - Places of religious worship"
Convention, Conference, Multipurpose and Meeting Area | Education - Lecture hall (fixed seats) | 71 | 0.15 | 0 | 0 | 0 | 1 | F | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Convention, Conference, Multipurpose and Meeting Area,Education - Lecture hall (fixed seats) | 318 | 15 | 17 | 0 | 2, 15, "Education - Lecture hall (fixed seats)"
Convention, Conference, Multipurpose and Meeting Area | Education - Multiuse assembly | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Convention, Conference, Multipurpose and Meeting Area,Education - Multiuse assembly | 318 | 19 | 17 | 0 | 2, 19, "Education - Multiuse assembly"
Convention, Conference, Multipurpose and Meeting Area | General - Conference/meeting | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Convention, Conference, Multipurpose and Meeting Area,General - Conference/meeting | 318 | 48 | 17 | 1 | 2, 48, "General - Conference/meeting"
Convention, Conference, Multipurpose and Meeting Area | Lodging - Multipurpose assembly | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Convention, Conference, Multipurpose and Meeting Area,Lodging - Multipurpose assembly | 318 | 57 | 17 | 1 | 2, 57, "Lodging - Multipurpose assembly"
Convention, Conference, Multipurpose and Meeting Area | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Convention, Conference, Multipurpose and Meeting Area,Misc - All others | 318 | 58 | 17 | 1 | 2, 58, "Misc - All others"
Copy Room | Exhaust - Copy, printing rooms | 0 | 0 | 0 | 0 | 0.5 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Copy Room,Exhaust - Copy, printing rooms | 319 | 28 | 18 | 1 | 1, Spc:SpcFunc, 319, 28 ; Copy Room
Copy Room | Exhaust - Copy, printing rooms | 0 | 0 | 0 | 0 | 0.5 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Copy Room,Exhaust - Copy, printing rooms | 319 | 28 | 18 | 1 | 2, 28, "Exhaust - Copy, printing rooms"
Corridor Area | General - Corridors | 5 | 0.15 | 0 | 0 | 0 | 1 | F | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Corridor Area,General - Corridors | 320 | 49 | 19 | 1 | 1, Spc:SpcFunc, 320, 49 ; Corridor Area
Corridor Area | General - Corridors | 5 | 0.15 | 0 | 0 | 0 | 1 | F | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Corridor Area,General - Corridors | 320 | 49 | 19 | 1 | 2, 49, "General - Corridors"
Corridor Area | Lodging - Lobbies/pre-function | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Corridor Area,Lodging - Lobbies/pre-function | 320 | 56 | 19 | 1 | 2, 56, "Lodging - Lobbies/pre-function"
Corridor Area | Misc - Transportation waiting | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Corridor Area,Misc - Transportation waiting | 320 | 69 | 19 | 0 | 2, 69, "Misc - Transportation waiting"
Corridor Area | Residential - Common corridors | 5 | 0.15 | 0 | 0 | 0 | 1 | F | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Corridor Area,Residential - Common corridors | 320 | 77 | 19 | 1 | 2, 77, "Residential - Common corridors"
Corridor Area | Retail - Mall common areas | 17 | 0.15 | 0 | 0 | 0 | 1 | F | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Corridor Area,Retail - Mall common areas | 320 | 81 | 19 | 0 | 2, 81, "Retail - Mall common areas"
Dining Area (Bar/Lounge and Fine Dining) | Food Service - Restaurant dining rooms | 33 | 0.15 | 0 | 0 | 0 | 2 |  | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Dining Area (Bar/Lounge and Fine Dining),Food Service - Restaurant dining rooms | 321 | 45 | 20 | 1 | 1, Spc:SpcFunc, 321, 45 ; Dining Area (Bar/Lounge and Fine Dining)
Dining Area (Bar/Lounge and Fine Dining) | Food Service - Bars, cocktail lounges | 33 | 0.2 | 0 | 0 | 0 | 2 |  | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Dining Area (Bar/Lounge and Fine Dining),Food Service - Bars, cocktail lounges | 321 | 42 | 20 | 1 | 2, 42, "Food Service - Bars, cocktail lounges"
Dining Area (Bar/Lounge and Fine Dining) | Food Service - Restaurant dining rooms | 33 | 0.15 | 0 | 0 | 0 | 2 |  | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Dining Area (Bar/Lounge and Fine Dining),Food Service - Restaurant dining rooms | 321 | 45 | 20 | 0 | 2, 45, "Food Service - Restaurant dining rooms"
Dining Area (Cafeteria/Fast Food) | Food Service - Cafeteria/fast-food dining | 33 | 0.15 | 0 | 0 | 0 | 2 |  | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Dining Area (Cafeteria/Fast Food),Food Service - Cafeteria/fast-food dining | 322 | 43 | 21 | 1 | 1, Spc:SpcFunc, 322, 43 ; Dining Area (Cafeteria/Fast Food)
Dining Area (Cafeteria/Fast Food) | Food Service - Cafeteria/fast-food dining | 33 | 0.15 | 0 | 0 | 0 | 2 |  | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Dining Area (Cafeteria/Fast Food),Food Service - Cafeteria/fast-food dining | 322 | 43 | 21 | 1 | 2, 43, "Food Service - Cafeteria/fast-food dining"
Dining Area (Family and Leisure) | Food Service - Cafeteria/fast-food dining | 33 | 0.15 | 0 | 0 | 0 | 2 |  | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Dining Area (Family and Leisure),Food Service - Cafeteria/fast-food dining | 323 | 43 | 22 | 1 | 1, Spc:SpcFunc, 323, 43 ; Dining Area (Family and Leisure)
Dining Area (Family and Leisure) | Food Service - Bars, cocktail lounges | 33 | 0.2 | 0 | 0 | 0 | 2 |  | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Dining Area (Family and Leisure),Food Service - Bars, cocktail lounges | 323 | 42 | 22 | 1 | 2, 42, "Food Service - Bars, cocktail lounges"
Dining Area (Family and Leisure) | Food Service - Cafeteria/fast-food dining | 33 | 0.15 | 0 | 0 | 0 | 2 |  | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Dining Area (Family and Leisure),Food Service - Cafeteria/fast-food dining | 323 | 43 | 22 | 0 | 2, 43, "Food Service - Cafeteria/fast-food dining"
Dining Area (Family and Leisure) | Food Service - Restaurant dining rooms | 33 | 0.15 | 0 | 0 | 0 | 2 |  | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Dining Area (Family and Leisure),Food Service - Restaurant dining rooms | 323 | 45 | 22 | 1 | 2, 45, "Food Service - Restaurant dining rooms"
Electrical, Mechanical, Telephone Rooms | Misc - Telephone closets | 5 | 0.15 | 0 | 0 | 0 | 1 |  | No | 1.5 | #REF! | #REF! | #REF! | #REF! | #REF! | Electrical, Mechanical, Telephone Rooms,Misc - Telephone closets | 324 | 68 | 23 | 1 | 1, Spc:SpcFunc, 324, 68 ; Electrical, Mechanical, Telephone Rooms
Electrical, Mechanical, Telephone Rooms | Exhaust - Refrigerating machinery rooms | 0 | 0 | 0 | 0 | 0 | 3 | Exh. Note F | Yes | 1.5 | #REF! | #REF! | #REF! | #REF! | #REF! | Electrical, Mechanical, Telephone Rooms,Exhaust - Refrigerating machinery rooms | 324 | 35 | 23 | 1 | 2, 35, "Exhaust - Refrigerating machinery rooms"
Electrical, Mechanical, Telephone Rooms | General - Unoccupied | 0 | 0 | 0 | 0 | 0 | 1 |  | No | 1.5 | #REF! | #REF! | #REF! | #REF! | #REF! | Electrical, Mechanical, Telephone Rooms,General - Unoccupied | 324 | 51 | 23 | 0 | 2, 51, "General - Unoccupied"
Electrical, Mechanical, Telephone Rooms | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 1.5 | #REF! | #REF! | #REF! | #REF! | #REF! | Electrical, Mechanical, Telephone Rooms,Misc - All others | 324 | 58 | 23 | 1 | 2, 58, "Misc - All others"
Electrical, Mechanical, Telephone Rooms | Misc - Telephone closets | 5 | 0.15 | 0 | 0 | 0 | 1 |  | No | 1.5 | #REF! | #REF! | #REF! | #REF! | #REF! | Electrical, Mechanical, Telephone Rooms,Misc - Telephone closets | 324 | 68 | 23 | 1 | 2, 68, "Misc - Telephone closets"
Exercise/Fitness Center and Gymnasium Areas | Sports/Entertainment - Gym, sports arena (play area) | 100 | 0.15 | 0 | 0 | 0 | 2 | F | No | 10 | #REF! | #REF! | #REF! | #REF! | #REF! | Exercise/Fitness Center and Gymnasium Areas,Sports/Entertainment - Gym, sports arena (play area) | 325 | 89 | 24 | 1 | 1, Spc:SpcFunc, 325, 89 ; Exercise/Fitness Center and Gymnasium Areas
Exercise/Fitness Center and Gymnasium Areas | Education - Multiuse assembly | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 10 | #REF! | #REF! | #REF! | #REF! | #REF! | Exercise/Fitness Center and Gymnasium Areas,Education - Multiuse assembly | 325 | 19 | 24 | 0 | 2, 19, "Education - Multiuse assembly"
Exercise/Fitness Center and Gymnasium Areas | Education - Music/theater/dance | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 10 | #REF! | #REF! | #REF! | #REF! | #REF! | Exercise/Fitness Center and Gymnasium Areas,Education - Music/theater/dance | 325 | 20 | 24 | 0 | 2, 20, "Education - Music/theater/dance"
Exercise/Fitness Center and Gymnasium Areas | Sports/Entertainment - Disco/dance floors | 100 | 0.15 | 0 | 0 | 0 | 2 | F | No | 10 | #REF! | #REF! | #REF! | #REF! | #REF! | Exercise/Fitness Center and Gymnasium Areas,Sports/Entertainment - Disco/dance floors | 325 | 86 | 24 | 0 | 2, 86, "Sports/Entertainment - Disco/dance floors"
Exercise/Fitness Center and Gymnasium Areas | Sports/Entertainment - Gym, sports arena (play area) | 100 | 0.15 | 0 | 0 | 0 | 2 | F | No | 10 | #REF! | #REF! | #REF! | #REF! | #REF! | Exercise/Fitness Center and Gymnasium Areas,Sports/Entertainment - Gym, sports arena (play area) | 325 | 89 | 24 | 1 | 2, 89, "Sports/Entertainment - Gym, sports arena (play area)"
Exercise/Fitness Center and Gymnasium Areas | Sports/Entertainment - Health club/aerobics room | 100 | 0.15 | 0 | 0 | 0 | 2 | F | No | 10 | #REF! | #REF! | #REF! | #REF! | #REF! | Exercise/Fitness Center and Gymnasium Areas,Sports/Entertainment - Health club/aerobics room | 325 | 90 | 24 | 1 | 2, 90, "Sports/Entertainment - Health club/aerobics room"
Exercise/Fitness Center and Gymnasium Areas | Sports/Entertainment - Health club/weight rooms | 100 | 0.15 | 0 | 0 | 0 | 2 | F | No | 10 | #REF! | #REF! | #REF! | #REF! | #REF! | Exercise/Fitness Center and Gymnasium Areas,Sports/Entertainment - Health club/weight rooms | 325 | 91 | 24 | 1 | 2, 91, "Sports/Entertainment - Health club/weight rooms"
Exercise/Fitness Center and Gymnasium Areas | Sports/Entertainment - Swimming (deck) | 100 | 0.15 | 0 | 0 | 0 | 2 | F | No | 10 | #REF! | #REF! | #REF! | #REF! | #REF! | Exercise/Fitness Center and Gymnasium Areas,Sports/Entertainment - Swimming (deck) | 325 | 94 | 24 | 1 | 2, 94, "Sports/Entertainment - Swimming (deck)"
Exercise/Fitness Center and Gymnasium Areas | Sports/Entertainment - Swimming (pool) | 100 | 0.15 | 0 | 0 | 0 | 2 | F | No | 10 | #REF! | #REF! | #REF! | #REF! | #REF! | Exercise/Fitness Center and Gymnasium Areas,Sports/Entertainment - Swimming (pool) | 325 | 95 | 24 | 1 | 2, 95, "Sports/Entertainment - Swimming (pool)"
Financial Transaction Area | Misc - Banks or bank lobbies | 5 | 0.15 | 0 | 0 | 0 | 1 | F | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Financial Transaction Area,Misc - Banks or bank lobbies | 326 | 60 | 25 | 0 | 1, Spc:SpcFunc, 326, 60 ; Financial Transaction Area
Financial Transaction Area | Misc - Bank vaults/safe deposit | 5 | 0.15 | 0 | 0 | 0 | 2 | F | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Financial Transaction Area,Misc - Bank vaults/safe deposit | 326 | 59 | 25 | 0 | 2, 59, "Misc - Bank vaults/safe deposit"
Financial Transaction Area | Misc - Banks or bank lobbies | 5 | 0.15 | 0 | 0 | 0 | 1 | F | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Financial Transaction Area,Misc - Banks or bank lobbies | 326 | 60 | 25 | 0 | 2, 60, "Misc - Banks or bank lobbies"
Financial Transaction Area | Office - Office space | 5 | 0.15 | 0 | 0 | 0 | 1 | F | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Financial Transaction Area,Office - Office space | 326 | 74 | 25 | 0 | 2, 74, "Office - Office space"
Healthcare Facility and Hospitals (Exam/Treatment Room) | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Healthcare Facility and Hospitals (Exam/Treatment Room),Misc - All others | 327 | 58 | 26 | 0 | 1, Spc:SpcFunc, 327, 58 ; Healthcare Facility and Hospitals (Exam/Treatment Room)
Healthcare Facility and Hospitals (Exam/Treatment Room) | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Healthcare Facility and Hospitals (Exam/Treatment Room),Misc - All others | 327 | 58 | 26 | 0 | 2, 58, "Misc - All others"
Healthcare Facility and Hospitals (Exam/Treatment Room) | Exhaust - Animal preparation rooms | [14 empty] | Healthcare Facility and Hospitals (Exam/Treatment Room),Exhaust - Animal preparation rooms | 327 | 100 | 26 | 0 | 2, 100, "Exhaust - Animal preparation rooms"
Healthcare Facility and Hospitals (Exam/Treatment Room) | Exhaust - Animal procedure room | [14 empty] | Healthcare Facility and Hospitals (Exam/Treatment Room),Exhaust - Animal procedure room | 327 | 101 | 26 | 0 | 2, 101, "Exhaust - Animal procedure room"
Healthcare Facility and Hospitals (Imaging Room) | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Healthcare Facility and Hospitals (Imaging Room),Misc - All others | 328 | 58 | 27 | 0 | 1, Spc:SpcFunc, 328, 58 ; Healthcare Facility and Hospitals (Imaging Room)
Healthcare Facility and Hospitals (Imaging Room) | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Healthcare Facility and Hospitals (Imaging Room),Misc - All others | 328 | 58 | 27 | 0 | 2, 58, "Misc - All others"
Healthcare Facility and Hospitals (Imaging Room) | Exhaust - Animal imaging(MRI/CT/PET) | 0 | 0 | 0 | 0 | 0.9 | 3 | 0 | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Healthcare Facility and Hospitals (Imaging Room),Exhaust - Animal imaging(MRI/CT/PET) | 328 | 97 | 27 | 0 | 2, 97, "Exhaust - Animal imaging(MRI/CT/PET)"
Healthcare Facility and Hospitals (Medical Supply Room) | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Healthcare Facility and Hospitals (Medical Supply Room),Misc - All others | 329 | 58 | 28 | 0 | 1, Spc:SpcFunc, 329, 58 ; Healthcare Facility and Hospitals (Medical Supply Room)
Healthcare Facility and Hospitals (Medical Supply Room) | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Healthcare Facility and Hospitals (Medical Supply Room),Misc - All others | 329 | 58 | 28 | 0 | 2, 58, "Misc - All others"
Healthcare Facility and Hospitals (Nursery) | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Healthcare Facility and Hospitals (Nursery),Misc - All others | 330 | 58 | 29 | 0 | 1, Spc:SpcFunc, 330, 58 ; Healthcare Facility and Hospitals (Nursery)
Healthcare Facility and Hospitals (Nursery) | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Healthcare Facility and Hospitals (Nursery),Misc - All others | 330 | 58 | 29 | 0 | 2, 58, "Misc - All others"
Healthcare Facility and Hospitals (Nurse's Station) | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Healthcare Facility and Hospitals (Nurse's Station),Misc - All others | 331 | 58 | 30 | 0 | 1, Spc:SpcFunc, 331, 58 ; Healthcare Facility and Hospitals (Nurse's Station)
Healthcare Facility and Hospitals (Nurse's Station) | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Healthcare Facility and Hospitals (Nurse's Station),Misc - All others | 331 | 58 | 30 | 0 | 2, 58, "Misc - All others"
Healthcare Facility and Hospitals (Imaging Room) | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Healthcare Facility and Hospitals (Imaging Room),Misc - All others | 328 | 58 | 27 | 0 | 1, Spc:SpcFunc, 328, 58 ; Healthcare Facility and Hospitals (Imaging Room)
Healthcare Facility and Hospitals (Imaging Room) | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Healthcare Facility and Hospitals (Imaging Room),Misc - All others | 328 | 58 | 27 | 0 | 2, 58, "Misc - All others"
Healthcare Facility and Hospitals (Operating Room) | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Healthcare Facility and Hospitals (Operating Room),Misc - All others | 332 | 58 | 31 | 0 | 1, Spc:SpcFunc, 332, 58 ; Healthcare Facility and Hospitals (Operating Room)
Healthcare Facility and Hospitals (Operating Room) | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Healthcare Facility and Hospitals (Operating Room),Misc - All others | 332 | 58 | 31 | 0 | 2, 58, "Misc - All others"
Healthcare Facility and Hospitals (Operating Room) | Exhaust - Animal operating rooms | 0 | 0 | 0 | 0 | 3 | 3 | 0 | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Healthcare Facility and Hospitals (Operating Room),Exhaust - Animal operating rooms | 332 | 98 | 31 | 0 | 2, 98, "Exhaust - Animal operating rooms"
Healthcare Facility and Hospitals (Operating Room) | Exhaust - Animal surgery scrub | 0 | 0 | 0 | 0 | 1.5 | 3 | 0 | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Healthcare Facility and Hospitals (Operating Room),Exhaust - Animal surgery scrub | 332 | 102 | 31 | 0 | 2, 102, "Exhaust - Animal surgery scrub"
Healthcare Facility and Hospitals (Operating Room) | Exhaust - Animal Necropsy | 0 | 0 | 0 | 0 | 0.9 | 3 | 0 | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Healthcare Facility and Hospitals (Operating Room),Exhaust - Animal Necropsy | 332 | 103 | 31 | 0 | 2, 103, "Exhaust - Animal Necropsy"
Healthcare Facility and Hospitals (Patient Room) | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Healthcare Facility and Hospitals (Patient Room),Misc - All others | 333 | 58 | 32 | 0 | 1, Spc:SpcFunc, 333, 58 ; Healthcare Facility and Hospitals (Patient Room)
Healthcare Facility and Hospitals (Patient Room) | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Healthcare Facility and Hospitals (Patient Room),Misc - All others | 333 | 58 | 32 | 0 | 2, 58, "Misc - All others"
Healthcare Facility and Hospitals (Patient Room) | Exhaust - Large-animal holding room | 0 | 0 | 0 | 0 | 2.25 | 3 | 0 | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Healthcare Facility and Hospitals (Patient Room),Exhaust - Large-animal holding room | 333 | 104 | 32 | 0 | 2, 104, "Exhaust - Large-animal holding room"
Healthcare Facility and Hospitals (Patient Room) | Exhaust - Small-animal-cage room (static cages) | 0 | 0 | 0 | 0 | 2.25 | 3 | 0 | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Healthcare Facility and Hospitals (Patient Room),Exhaust - Small-animal-cage room (static cages) | 333 | 105 | 32 | 0 | 2, 105, "Exhaust - Small-animal-cage room (static cages)"
Healthcare Facility and Hospitals (Patient Room) | Exhaust - Small-animal-cage room (ventilated cages) | 0 | 0 | 0 | 0 | 1.5 | 3 | 0 | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Healthcare Facility and Hospitals (Patient Room),Exhaust - Small-animal-cage room (ventilated cages) | 333 | 106 | 32 | 0 | 2, 106, "Exhaust - Small-animal-cage room (ventilated cages)"
Healthcare Facility and Hospitals (Physical Therapy Room) | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Healthcare Facility and Hospitals (Physical Therapy Room),Misc - All others | 334 | 58 | 33 | 0 | 1, Spc:SpcFunc, 334, 58 ; Healthcare Facility and Hospitals (Physical Therapy Room)
Healthcare Facility and Hospitals (Physical Therapy Room) | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Healthcare Facility and Hospitals (Physical Therapy Room),Misc - All others | 334 | 58 | 33 | 0 | 2, 58, "Misc - All others"
Healthcare Facility and Hospitals (Recovery Room) | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Healthcare Facility and Hospitals (Recovery Room),Misc - All others | 335 | 58 | 34 | 0 | 1, Spc:SpcFunc, 335, 58 ; Healthcare Facility and Hospitals (Recovery Room)
Healthcare Facility and Hospitals (Recovery Room) | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Healthcare Facility and Hospitals (Recovery Room),Misc - All others | 335 | 58 | 34 | 0 | 2, 58, "Misc - All others"
Healthcare Facility and Hospitals (Recovery Room) | Exhaust - Animal postoperative recovery room | 0 | 0 | 0 | 0 | 1.5 | 3 | 0 | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Healthcare Facility and Hospitals (Recovery Room),Exhaust - Animal postoperative recovery room | 335 | 99 | 34 | 0 | 2, 99, "Exhaust - Animal postoperative recovery room"
High-Rise Residential Living Spaces | NA | 1 | 0.15 | 0 | 0 | 0 | 2 | B | No | 2.5 | #REF! | #REF! | #REF! | #REF! | #REF! | High-Rise Residential Living Spaces,NA | 336 | 96 | 35 | 0 | 1, Spc:SpcFunc, 336, 96 ; High-Rise Residential Living Spaces
High-Rise Residential Living Spaces | NA | 1 | 0.15 | 0 | 0 | 0 | 2 | B | No | 2.5 | #REF! | #REF! | #REF! | #REF! | #REF! | High-Rise Residential Living Spaces,NA | 336 | 96 | 35 | 0 | 2, 96, "NA"
Hotel Function Area | Lodging - Multipurpose assembly | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 71.43 | #REF! | #REF! | #REF! | #REF! | #REF! | Hotel Function Area,Lodging - Multipurpose assembly | 337 | 57 | 36 | 0 | 1, Spc:SpcFunc, 337, 57 ; Hotel Function Area
Hotel Function Area | General - Conference/meeting | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 71.43 | #REF! | #REF! | #REF! | #REF! | #REF! | Hotel Function Area,General - Conference/meeting | 337 | 48 | 36 | 0 | 2, 48, "General - Conference/meeting"
Hotel Function Area | Lodging - Lobbies/pre-function | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 71.43 | #REF! | #REF! | #REF! | #REF! | #REF! | Hotel Function Area,Lodging - Lobbies/pre-function | 337 | 56 | 36 | 0 | 2, 56, "Lodging - Lobbies/pre-function"
Hotel Function Area | Lodging - Multipurpose assembly | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 71.43 | #REF! | #REF! | #REF! | #REF! | #REF! | Hotel Function Area,Lodging - Multipurpose assembly | 337 | 57 | 36 | 0 | 2, 57, "Lodging - Multipurpose assembly"
Hotel Function Area | Sports/Entertainment - Gambling casinos | 100 | 0.15 | 0 | 0 | 0 | 2 | F | No | 71.43 | #REF! | #REF! | #REF! | #REF! | #REF! | Hotel Function Area,Sports/Entertainment - Gambling casinos | 337 | 87 | 36 | 0 | 2, 87, "Sports/Entertainment - Gambling casinos"
Hotel/Motel Guest Room | Lodging - Bedroom/living room | 3 | 0.15 | 0 | 0 | 0 | 1 | F | No | 2.5 | #REF! | #REF! | #REF! | #REF! | #REF! | Hotel/Motel Guest Room,Lodging - Bedroom/living room | 338 | 53 | 37 | 0 | 1, Spc:SpcFunc, 338, 53 ; Hotel/Motel Guest Room
Hotel/Motel Guest Room | Lodging - Barracks sleeping areas | 5 | 0.15 | 0 | 0 | 0 | 1 | F | No | 2.5 | #REF! | #REF! | #REF! | #REF! | #REF! | Hotel/Motel Guest Room,Lodging - Barracks sleeping areas | 338 | 52 | 37 | 0 | 2, 52, "Lodging - Barracks sleeping areas"
Hotel/Motel Guest Room | Lodging - Bedroom/living room | 3 | 0.15 | 0 | 0 | 0 | 1 | F | No | 2.5 | #REF! | #REF! | #REF! | #REF! | #REF! | Hotel/Motel Guest Room,Lodging - Bedroom/living room | 338 | 53 | 37 | 0 | 2, 53, "Lodging - Bedroom/living room"
Kitchen/Food Preparation Area | Food Service - Kitchen (cooking) | 3 | 0.15 | 0 | 0 | 0.7 | 2 |  | Yes | 2.5 | #REF! | #REF! | #REF! | #REF! | #REF! | Kitchen/Food Preparation Area,Food Service - Kitchen (cooking) | 339 | 44 | 38 | 1 | 1, Spc:SpcFunc, 339, 44 ; Kitchen/Food Preparation Area
Kitchen/Food Preparation Area | Food Service - Kitchen (cooking) | 3 | 0.15 | 0 | 0 | 0.7 | 2 |  | Yes | 2.5 | #REF! | #REF! | #REF! | #REF! | #REF! | Kitchen/Food Preparation Area,Food Service - Kitchen (cooking) | 339 | 44 | 38 | 1 | 2, 44, "Food Service - Kitchen (cooking)"
Kitchenette or Residential Kitchen | Exhaust - Kitchenettes | 0 | 0 | 0 | 0 | 0.3 | 2 |  | No | 2.5 | #REF! | #REF! | #REF! | #REF! | #REF! | Kitchenette or Residential Kitchen,Exhaust - Kitchenettes | 340 | 31 | 39 | 1 | 1, Spc:SpcFunc, 340, 31 ; Kitchenette or Residential Kitchen
Kitchenette or Residential Kitchen | Exhaust - Kitchenettes | 0 | 0 | 0 | 0 | 0.3 | 2 |  | No | 2.5 | #REF! | #REF! | #REF! | #REF! | #REF! | Kitchenette or Residential Kitchen,Exhaust - Kitchenettes | 340 | 31 | 39 | 1 | 2, 31, "Exhaust - Kitchenettes"
Laboratory, Scientific | Education - University/college laboratories | 25 | 0.15 | 0 | 0 | 1 | 2 |  | Yes | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Laboratory, Scientific,Education - University/college laboratories | 341 | 22 | 40 | 0 | 1, Spc:SpcFunc, 341, 22 ; Laboratory, Scientific
Laboratory, Scientific | Education - Science laboratories | 25 | 0.15 | 0 | 0 | 1 | 2 |  | Yes | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Laboratory, Scientific,Education - Science laboratories | 341 | 21 | 40 | 0 | 2, 21, "Education - Science laboratories"
Laboratory, Scientific | Education - University/college laboratories | 25 | 0.15 | 0 | 0 | 1 | 2 |  | Yes | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Laboratory, Scientific,Education - University/college laboratories | 341 | 22 | 40 | 0 | 2, 22, "Education - University/college laboratories"
Laboratory, Scientific | Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 5 | 0.15 | 0 | 0 | 0 | 3 |  | Yes | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Laboratory, Scientific,Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 341 | 63 | 40 | 0 | 2, 63, "Misc - General manufacturing (excludes heavy industrial and process using chemicals)"
Laboratory, Scientific | Misc - Pharmacy (preparation area) | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Laboratory, Scientific,Misc - Pharmacy (preparation area) | 341 | 64 | 40 | 0 | 2, 64, "Misc - Pharmacy (preparation area)"
Laboratory, Scientific | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Laboratory, Scientific,Misc - All others | 341 | 58 | 40 | 0 | 2, 58, "Misc - All others"
Laundry Area | Lodging - Laundry rooms, central | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Laundry Area,Lodging - Laundry rooms, central | 342 | 55 | 41 | 1 | 1, Spc:SpcFunc, 342, 55 ; Laundry Area
Laundry Area | Exhaust - Soiled laundry storage rooms | 0 | 0 | 0 | 0 | 1 | 3 | Exh. Note F | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Laundry Area,Exhaust - Soiled laundry storage rooms | 342 | 37 | 41 | 1 | 2, 37, "Exhaust - Soiled laundry storage rooms"
Laundry Area | Lodging - Laundry rooms within dwelling units | 5 | 0.15 | 0 | 0 | 0 | 1 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Laundry Area,Lodging - Laundry rooms within dwelling units | 342 | 54 | 41 | 1 | 2, 54, "Lodging - Laundry rooms within dwelling units"
Laundry Area | Lodging - Laundry rooms, central | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | High-Rise Residential Living Spaces,NA | 342 | 55 | 41 | 1 | 2, 55, "Lodging - Laundry rooms, central"
Laundry Area | Retail - Coin-operated laundries | 17 | 0.3 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Laundry Area,Retail - Coin-operated laundries | 342 | 80 | 41 | 1 | 2, 80, "Retail - Coin-operated laundries"
Library (Reading Area) | Assembly - Libraries (reading rooms and stack areas) | 10 | 0.15 | 0 | 0 | 0 | 1 |  | No | 10 | #REF! | #REF! | #REF! | #REF! | #REF! | Library (Reading Area),Assembly - Libraries (reading rooms and stack areas) | 343 | 4 | 42 | 0 | 1, Spc:SpcFunc, 343, 4 ; Library (Reading Area)
Library (Reading Area) | Assembly - Libraries (reading rooms and stack areas) | 10 | 0.15 | 0 | 0 | 0 | 1 |  | No | 10 | #REF! | #REF! | #REF! | #REF! | #REF! | Library (Reading Area),Assembly - Libraries (reading rooms and stack areas) | 343 | 4 | 42 | 0 | 2, 4, "Assembly - Libraries (reading rooms and stack areas)"
Library (Stacks Area) | Assembly - Libraries (reading rooms and stack areas) | 10 | 0.15 | 0 | 0 | 0 | 1 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Library (Stacks Area),Assembly - Libraries (reading rooms and stack areas) | 344 | 4 | 43 | 0 | 1, Spc:SpcFunc, 344, 4 ; Library (Stacks Area)
Library (Stacks Area) | Assembly - Libraries (reading rooms and stack areas) | 10 | 0.15 | 0 | 0 | 0 | 1 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Library (Stacks Area),Assembly - Libraries (reading rooms and stack areas) | 344 | 4 | 43 | 0 | 2, 4, "Assembly - Libraries (reading rooms and stack areas)"
Lobby, Main Entry | Office - Main entry lobbies | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Lobby, Main Entry,Office - Main entry lobbies | 345 | 72 | 44 | 1 | 1, Spc:SpcFunc, 345, 72 ; Lobby, Main Entry
Lobby, Main Entry | Assembly - Lobbies | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Lobby, Main Entry,Assembly - Lobbies | 345 | 5 | 44 | 0 | 2, 5, "Assembly - Lobbies"
Lobby, Main Entry | Lodging - Lobbies/pre-function | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Lobby, Main Entry,Lodging - Lobbies/pre-function | 345 | 56 | 44 | 1 | 2, 56, "Lodging - Lobbies/pre-function"
Lobby, Main Entry | Misc - Banks or bank lobbies | 5 | 0.15 | 0 | 0 | 0 | 1 | F | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Lobby, Main Entry,Misc - Banks or bank lobbies | 345 | 60 | 44 | 1 | 2, 60, "Misc - Banks or bank lobbies"
Lobby, Main Entry | Office - Main entry lobbies | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Lobby, Main Entry,Office - Main entry lobbies | 345 | 72 | 44 | 0 | 2, 72, "Office - Main entry lobbies"
Locker Room | Exhaust - Locker rooms for athletic or industrial facilities | 0 | 0 | 0 | 0 | 0.5 | 2 |  | No | 10 | #REF! | #REF! | #REF! | #REF! | #REF! | Locker Room,Exhaust - Locker rooms for athletic or industrial facilities | 346 | 32 | 45 | 1 | 1, Spc:SpcFunc, 346, 32 ; Locker Room
Locker Room | Exhaust - All other locker rooms | 0 | 0 | 0 | 0 | 0.25 | 2 |  | No | 10 | #REF! | #REF! | #REF! | #REF! | #REF! | Locker Room,Exhaust - All other locker rooms | 346 | 24 | 45 | 1 | 2, 24, "Exhaust - All other locker rooms"
Locker Room | Exhaust - Locker rooms for athletic or industrial facilities | 0 | 0 | 0 | 0 | 0.5 | 2 |  | No | 10 | #REF! | #REF! | #REF! | #REF! | #REF! | Locker Room,Exhaust - Locker rooms for athletic or industrial facilities | 346 | 32 | 45 | 0 | 2, 32, "Exhaust - Locker rooms for athletic or industrial facilities"
Locker Room | Exhaust - Shower rooms | 0 | 0 | 20 | 50 | 0 | 2 | Exh. Note G,H | No | 10 | #REF! | #REF! | #REF! | #REF! | #REF! | Locker Room,Exhaust - Shower rooms | 346 | 36 | 45 | 1 | 2, 36, "Exhaust - Shower rooms"
Lounge, Breakroom, or Waiting Area | General - Break rooms | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Lounge, Breakroom, or Waiting Area,General - Break rooms | 347 | 46 | 46 | 1 | 1, Spc:SpcFunc, 347, 46 ; Lounge, Breakroom, or Waiting Area
Lounge, Breakroom, or Waiting Area | General - Break rooms | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Lounge, Breakroom, or Waiting Area,General - Break rooms | 347 | 46 | 46 | 1 | 2, 46, "General - Break rooms"
Lounge, Breakroom, or Waiting Area | General - Coffee Stations | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Lounge, Breakroom, or Waiting Area,General - Coffee Stations | 347 | 47 | 46 | 1 | 2, 47, "General - Coffee Stations"
Lounge, Breakroom, or Waiting Area | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Lounge, Breakroom, or Waiting Area,Misc - All others | 347 | 58 | 46 | 1 | 2, 58, "Misc - All others"
Lounge, Breakroom, or Waiting Area | Misc - Transportation waiting | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Lounge, Breakroom, or Waiting Area,Misc - Transportation waiting | 347 | 69 | 46 | 0 | 2, 69, "Misc - Transportation waiting"
Lounge, Breakroom, or Waiting Area | Office - Breakrooms | 33 | 0.15 | 0 | 0 | 0 | 1 |  | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Lounge, Breakroom, or Waiting Area,Office - Breakrooms | 347 | 71 | 46 | 0 | 2, 71, "Office - Breakrooms"
Lounge, Breakroom, or Waiting Area | Office - Reception areas | 5 | 0.15 | 0 | 0 | 0 | 1 | F | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Lounge, Breakroom, or Waiting Area,Office - Reception areas | 347 | 75 | 46 | 0 | 2, 75, "Office - Reception areas"
Manufacturing, Commercial & Industrial Work Area (Low Bay) | Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 5 | 0.15 | 0 | 0 | 0 | 3 |  | Yes | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Manufacturing, Commercial & Industrial Work Area (Low Bay),Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 348 | 63 | 47 | 0 | 1, Spc:SpcFunc, 348, 63 ; Manufacturing, Commercial & Industrial Work Area (Low Bay)
Manufacturing, Commercial & Industrial Work Area (Low Bay) | Exhaust - Copy, printing rooms | 0 | 0 | 0 | 0 | 0.5 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Manufacturing, Commercial & Industrial Work Area (Low Bay),Exhaust - Copy, printing rooms | 348 | 28 | 47 | 0 | 2, 28, "Exhaust - Copy, printing rooms"
Manufacturing, Commercial & Industrial Work Area (Low Bay) | Exhaust - Darkrooms | 0 | 0 | 0 | 0 | 1 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Manufacturing, Commercial & Industrial Work Area (Low Bay),Exhaust - Darkrooms | 348 | 29 | 47 | 0 | 2, 29, "Exhaust - Darkrooms"
Manufacturing, Commercial & Industrial Work Area (Low Bay) | Exhaust - Janitor closets, trash rooms, recycling | 0 | 0 | 0 | 0 | 1 | 3 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Manufacturing, Commercial & Industrial Work Area (Low Bay),Exhaust - Janitor closets, trash rooms, recycling | 348 | 30 | 47 | 0 | 2, 30, "Exhaust - Janitor closets, trash rooms, recycling"
Manufacturing, Commercial & Industrial Work Area (Low Bay) | Exhaust - Paint spray booths | 0 | 0 | 0 | 0 | 0 | 4 | Exh. Note F | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Manufacturing, Commercial & Industrial Work Area (Low Bay),Exhaust - Paint spray booths | 348 | 33 | 47 | 0 | 2, 33, "Exhaust - Paint spray booths"
Manufacturing, Commercial & Industrial Work Area (Low Bay) | Exhaust - Woodwork shop/classrooms | 0 | 0 | 0 | 0 | 0.5 | 2 | 0 | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Manufacturing, Commercial & Industrial Work Area (Low Bay),Exhaust - Woodwork shop/classrooms | 348 | 41 | 47 | 0 | 2, 41, "Exhaust - Woodwork shop/classrooms"
Manufacturing, Commercial & Industrial Work Area (Low Bay) | Lodging - Laundry rooms, central | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Manufacturing, Commercial & Industrial Work Area (Low Bay),Lodging - Laundry rooms, central | 348 | 55 | 47 | 0 | 2, 55, "Lodging - Laundry rooms, central"
Manufacturing, Commercial & Industrial Work Area (Low Bay) | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Manufacturing, Commercial & Industrial Work Area (Low Bay),Misc - All others | 348 | 58 | 47 | 0 | 2, 58, "Misc - All others"
Manufacturing, Commercial & Industrial Work Area (Low Bay) | Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 5 | 0.15 | 0 | 0 | 0 | 3 |  | Yes | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Manufacturing, Commercial & Industrial Work Area (Low Bay),Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 348 | 63 | 47 | 0 | 2, 63, "Misc - General manufacturing (excludes heavy industrial and process using chemicals)"
Manufacturing, Commercial & Industrial Work Area (Low Bay) | Misc - Sorting, packing, light assembly | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Manufacturing, Commercial & Industrial Work Area (Low Bay),Misc - Sorting, packing, light assembly | 348 | 67 | 47 | 0 | 2, 67, "Misc - Sorting, packing, light assembly"
Manufacturing, Commercial & Industrial Work Area (High Bay) | Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 5 | 0.15 | 0 | 0 | 0 | 3 |  | Yes | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Manufacturing, Commercial & Industrial Work Area (High Bay),Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 349 | 63 | 48 | 0 | 1, Spc:SpcFunc, 349, 63 ; Manufacturing, Commercial & Industrial Work Area (High Bay)
Manufacturing, Commercial & Industrial Work Area (High Bay) | Exhaust - Copy, printing rooms | 0 | 0 | 0 | 0 | 0.5 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Manufacturing, Commercial & Industrial Work Area (High Bay),Exhaust - Copy, printing rooms | 349 | 28 | 48 | 0 | 2, 28, "Exhaust - Copy, printing rooms"
Manufacturing, Commercial & Industrial Work Area (High Bay) | Exhaust - Darkrooms | 0 | 0 | 0 | 0 | 1 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Manufacturing, Commercial & Industrial Work Area (High Bay),Exhaust - Darkrooms | 349 | 29 | 48 | 0 | 2, 29, "Exhaust - Darkrooms"
Manufacturing, Commercial & Industrial Work Area (High Bay) | Exhaust - Paint spray booths | 0 | 0 | 0 | 0 | 0 | 4 | Exh. Note F | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Manufacturing, Commercial & Industrial Work Area (High Bay),Exhaust - Paint spray booths | 349 | 33 | 48 | 0 | 2, 33, "Exhaust - Paint spray booths"
Manufacturing, Commercial & Industrial Work Area (High Bay) | Exhaust - Woodwork shop/classrooms | 0 | 0 | 0 | 0 | 0.5 | 2 | 0 | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Manufacturing, Commercial & Industrial Work Area (High Bay),Exhaust - Woodwork shop/classrooms | 349 | 41 | 48 | 0 | 2, 41, "Exhaust - Woodwork shop/classrooms"
Manufacturing, Commercial & Industrial Work Area (High Bay) | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Manufacturing, Commercial & Industrial Work Area (High Bay),Misc - All others | 349 | 58 | 48 | 0 | 2, 58, "Misc - All others"
Manufacturing, Commercial & Industrial Work Area (High Bay) | Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 5 | 0.15 | 0 | 0 | 0 | 3 |  | Yes | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Manufacturing, Commercial & Industrial Work Area (High Bay),Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 349 | 63 | 48 | 0 | 2, 63, "Misc - General manufacturing (excludes heavy industrial and process using chemicals)"
Manufacturing, Commercial & Industrial Work Area (High Bay) | Misc - Sorting, packing, light assembly | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Manufacturing, Commercial & Industrial Work Area (High Bay),Misc - Sorting, packing, light assembly | 349 | 67 | 48 | 0 | 2, 67, "Misc - Sorting, packing, light assembly"
Manufacturing, Commercial & Industrial Work Area (Precision) | Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 5 | 0.15 | 0 | 0 | 0 | 3 |  | Yes | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Manufacturing, Commercial & Industrial Work Area (Precision),Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 350 | 63 | 49 | 0 | 1, Spc:SpcFunc, 350, 63 ; Manufacturing, Commercial & Industrial Work Area (Precision)
Manufacturing, Commercial & Industrial Work Area (Precision) | Exhaust - Copy, printing rooms | 0 | 0 | 0 | 0 | 0.5 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Manufacturing, Commercial & Industrial Work Area (Precision),Exhaust - Copy, printing rooms | 350 | 28 | 49 | 0 | 2, 28, "Exhaust - Copy, printing rooms"
Manufacturing, Commercial & Industrial Work Area (Precision) | Exhaust - Darkrooms | 0 | 0 | 0 | 0 | 1 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Manufacturing, Commercial & Industrial Work Area (Precision),Exhaust - Darkrooms | 350 | 29 | 49 | 0 | 2, 29, "Exhaust - Darkrooms"
Manufacturing, Commercial & Industrial Work Area (Precision) | Exhaust - Paint spray booths | 0 | 0 | 0 | 0 | 0 | 4 | Exh. Note F | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Manufacturing, Commercial & Industrial Work Area (Precision),Exhaust - Paint spray booths | 350 | 33 | 49 | 0 | 2, 33, "Exhaust - Paint spray booths"
Manufacturing, Commercial & Industrial Work Area (Precision) | Exhaust - Woodwork shop/classrooms | 0 | 0 | 0 | 0 | 0.5 | 2 | 0 | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Manufacturing, Commercial & Industrial Work Area (Precision),Exhaust - Woodwork shop/classrooms | 350 | 41 | 49 | 0 | 2, 41, "Exhaust - Woodwork shop/classrooms"
Manufacturing, Commercial & Industrial Work Area (Precision) | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Manufacturing, Commercial & Industrial Work Area (Precision),Misc - All others | 350 | 58 | 49 | 0 | 2, 58, "Misc - All others"
Manufacturing, Commercial & Industrial Work Area (Precision) | Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 5 | 0.15 | 0 | 0 | 0 | 3 |  | Yes | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Manufacturing, Commercial & Industrial Work Area (Precision),Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 350 | 63 | 49 | 0 | 2, 63, "Misc - General manufacturing (excludes heavy industrial and process using chemicals)"
Manufacturing, Commercial & Industrial Work Area (Precision) | Misc - Sorting, packing, light assembly | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Manufacturing, Commercial & Industrial Work Area (Precision),Misc - Sorting, packing, light assembly | 350 | 67 | 49 | 0 | 2, 67, "Misc - Sorting, packing, light assembly"
Museum Area (Exhibition/Display) | Assembly - Museums/galleries | 17 | 0.15 | 0 | 0 | 0 | 1 | F | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Museum Area (Exhibition/Display),Assembly - Museums/galleries | 351 | 7 | 50 | 0 | 1, Spc:SpcFunc, 351, 7 ; Museum Area (Exhibition/Display)
Museum Area (Exhibition/Display) | Assembly - Museums (childrens) | 17 | 0.15 | 0 | 0 | 0 | 1 |  | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Museum Area (Exhibition/Display),Assembly - Museums (childrens) | 351 | 6 | 50 | 0 | 2, 6, "Assembly - Museums (childrens)"
Museum Area (Exhibition/Display) | Assembly - Museums/galleries | 17 | 0.15 | 0 | 0 | 0 | 1 | F | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Museum Area (Exhibition/Display),Assembly - Museums/galleries | 351 | 7 | 50 | 0 | 2, 7, "Assembly - Museums/galleries"
Museum Area (Restoration Room) | Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 5 | 0.15 | 0 | 0 | 0 | 3 |  | Yes | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Museum Area (Restoration Room),Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 352 | 63 | 51 | 0 | 1, Spc:SpcFunc, 352, 63 ; Museum Area (Restoration Room)
Museum Area (Restoration Room) | Education - Art classroom | 25 | 0.15 | 0 | 0 | 0.7 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Museum Area (Restoration Room),Education - Art classroom | 352 | 9 | 51 | 0 | 2, 9, "Education - Art classroom"
Museum Area (Restoration Room) | Education - Science laboratories | 25 | 0.15 | 0 | 0 | 1 | 2 |  | Yes | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Museum Area (Restoration Room),Education - Science laboratories | 352 | 21 | 51 | 0 | 2, 21, "Education - Science laboratories"
Museum Area (Restoration Room) | Education - University/college laboratories | 25 | 0.15 | 0 | 0 | 1 | 2 |  | Yes | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Museum Area (Restoration Room),Education - University/college laboratories | 352 | 22 | 51 | 0 | 2, 22, "Education - University/college laboratories"
Museum Area (Restoration Room) | Education - Wood shop | 10 | 0.15 | 0 | 0 | 0.5 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Museum Area (Restoration Room),Education - Wood shop | 352 | 23 | 51 | 0 | 2, 23, "Education - Wood shop"
Museum Area (Restoration Room) | Exhaust - Copy, printing rooms | 0 | 0 | 0 | 0 | 0.5 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Museum Area (Restoration Room),Exhaust - Copy, printing rooms | 352 | 28 | 51 | 0 | 2, 28, "Exhaust - Copy, printing rooms"
Museum Area (Restoration Room) | Exhaust - Darkrooms | 0 | 0 | 0 | 0 | 1 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Museum Area (Restoration Room),Exhaust - Darkrooms | 352 | 29 | 51 | 0 | 2, 29, "Exhaust - Darkrooms"
Museum Area (Restoration Room) | Exhaust - Woodwork shop/classrooms | 0 | 0 | 0 | 0 | 0.5 | 2 | 0 | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Museum Area (Restoration Room),Exhaust - Woodwork shop/classrooms | 352 | 41 | 51 | 0 | 2, 41, "Exhaust - Woodwork shop/classrooms"
Museum Area (Restoration Room) | General - Occupiable storage rooms for liquids or gels | 2 | 0.15 | 0 | 0 | 0 | 2 | B | Yes | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Museum Area (Restoration Room),General - Occupiable storage rooms for liquids or gels | 352 | 50 | 51 | 0 | 2, 50, "General - Occupiable storage rooms for liquids or gels"
Museum Area (Restoration Room) | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Museum Area (Restoration Room),Misc - All others | 352 | 58 | 51 | 0 | 2, 58, "Misc - All others"
Museum Area (Restoration Room) | Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 5 | 0.15 | 0 | 0 | 0 | 3 |  | Yes | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Museum Area (Restoration Room),Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 352 | 63 | 51 | 0 | 2, 63, "Misc - General manufacturing (excludes heavy industrial and process using chemicals)"
Museum Area (Restoration Room) | Misc - Photo studios | 5 | 0.15 | 0 | 0 | 0 | 1 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Museum Area (Restoration Room),Misc - Photo studios | 352 | 65 | 51 | 0 | 2, 65, "Misc - Photo studios"
Museum Area (Restoration Room) | Misc - Sorting, packing, light assembly | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Museum Area (Restoration Room),Misc - Sorting, packing, light assembly | 352 | 67 | 51 | 0 | 2, 67, "Misc - Sorting, packing, light assembly"
Office Area (<250 square feet) | Office - Office space | 5 | 0.15 | 0 | 0 | 0 | 1 | F | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Office Area (<250 square feet),Office - Office space | 354 | 74 | 53 | 1 | 1, Spc:SpcFunc, 354, 74 ; Office Area (<250 square feet)
Office Area (<250 square feet) | Office - Office space | 5 | 0.15 | 0 | 0 | 0 | 1 | F | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Office Area (<250 square feet),Office - Office space | 354 | 74 | 53 | 1 | 2, 74, "Office - Office space"
Office Area (>250 square feet) | Office - Office space | 5 | 0.15 | 0 | 0 | 0 | 1 | F | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Office Area (>250 square feet),Office - Office space | 353 | 74 | 52 | 1 | 1, Spc:SpcFunc, 353, 74 ; Office Area (>250 square feet)
Office Area (>250 square feet) | Office - Office space | 5 | 0.15 | 0 | 0 | 0 | 1 | F | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Office Area (>250 square feet),Office - Office space | 353 | 74 | 52 | 1 | 2, 74, "Office - Office space"
Parking Garage Area (Parking Zone and Ramps) | Exhaust - Parking garages | 0 | 0 | 0 | 0 | 0.75 | 2 | Exh. Note C | Yes | 2.5 | #REF! | #REF! | #REF! | #REF! | #REF! | Parking Garage Area (Parking Zone and Ramps),Exhaust - Parking garages | 355 | 34 | 54 | 1 | 1, Spc:SpcFunc, 355, 34 ; Parking Garage Area (Parking Zone and Ramps)
Parking Garage Area (Parking Zone and Ramps) | Exhaust - Parking garages | 0 | 0 | 0 | 0 | 0.75 | 2 | Exh. Note C | Yes | 2.5 | #REF! | #REF! | #REF! | #REF! | #REF! | Parking Garage Area (Parking Zone and Ramps),Exhaust - Parking garages | 355 | 34 | 54 | 1 | 2, 34, "Exhaust - Parking garages"
Parking Garage Area (Daylight Adaptation Zones) | Exhaust - Parking garages | 0 | 0 | 0 | 0 | 0.75 | 2 | Exh. Note C | Yes | 2.5 | #REF! | #REF! | #REF! | #REF! | #REF! | Parking Garage Area (Daylight Adaptation Zones),Exhaust - Parking garages | 356 | 34 | 55 | 1 | 1, Spc:SpcFunc, 356, 34 ; Parking Garage Area (Daylight Adaptation Zones)
Parking Garage Area (Daylight Adaptation Zones) | Exhaust - Parking garages | 0 | 0 | 0 | 0 | 0.75 | 2 | Exh. Note C | Yes | 2.5 | #REF! | #REF! | #REF! | #REF! | #REF! | Parking Garage Area (Daylight Adaptation Zones),Exhaust - Parking garages | 356 | 34 | 55 | 1 | 2, 34, "Exhaust - Parking garages"
Pharmacy Area | Misc - Pharmacy (preparation area) | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Pharmacy Area,Misc - Pharmacy (preparation area) | 357 | 64 | 56 | 0 | 1, Spc:SpcFunc, 357, 64 ; Pharmacy Area
Pharmacy Area | Misc - Pharmacy (preparation area) | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Pharmacy Area,Misc - Pharmacy (preparation area) | 357 | 64 | 56 | 0 | 2, 64, "Misc - Pharmacy (preparation area)"
Retail Sales Area (Grocery Sales) | Retail - Supermarket | 17 | 0.2 | 0 | 0 | 0 | 1 | F | No | 8.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Retail Sales Area (Grocery Sales),Retail - Supermarket | 358 | 84 | 57 | 0 | 1, Spc:SpcFunc, 358, 84 ; Retail Sales Area (Grocery Sales)
Retail Sales Area (Grocery Sales) | Retail - Supermarket | 17 | 0.2 | 0 | 0 | 0 | 1 | F | No | 8.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Retail Sales Area (Grocery Sales),Retail - Supermarket | 358 | 84 | 57 | 0 | 2, 84, "Retail - Supermarket"
Retail Sales Area (Retail Merchandise Sales) | Retail - Sales | 17 | 0.2 | 0 | 0 | 0 | 2 |  | No | 8.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Retail Sales Area (Retail Merchandise Sales),Retail - Sales | 359 | 83 | 58 | 0 | 1, Spc:SpcFunc, 359, 83 ; Retail Sales Area (Retail Merchandise Sales)
Retail Sales Area (Retail Merchandise Sales) | Retail - Sales | 17 | 0.2 | 0 | 0 | 0 | 2 |  | No | 8.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Retail Sales Area (Retail Merchandise Sales),Retail - Sales | 359 | 83 | 58 | 0 | 2, 83, "Retail - Sales"
Retail Sales Area (Retail Merchandise Sales) | Retail - Pet shops (animal areas) | 17 | 0.2 | 0 | 0 | 0.9 | 2 |  | No | 8.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Retail Sales Area (Retail Merchandise Sales),Retail - Pet shops (animal areas) | 359 | 82 | 58 | 0 | 2, 82, "Retail - Pet shops (animal areas)"
Retail Sales Area (Fitting Room) | Retail - Sales | 17 | 0.2 | 0 | 0 | 0 | 2 |  | No | 8.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Retail Sales Area (Fitting Room),Retail - Sales | 360 | 83 | 59 | 0 | 1, Spc:SpcFunc, 360, 83 ; Retail Sales Area (Fitting Room)
Retail Sales Area (Fitting Room) | Retail - Sales | 17 | 0.2 | 0 | 0 | 0 | 2 |  | No | 8.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Retail Sales Area (Fitting Room),Retail - Sales | 360 | 83 | 59 | 0 | 2, 83, "Retail - Sales"
Retail Sales Area (Fitting Room) | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 8.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Retail Sales Area (Fitting Room),Misc - All others | 360 | 58 | 59 | 0 | 2, 58, "Misc - All others"
Religious Worship Area | Assembly - Places of religious worship | 7 | 0.15 | 0 | 0 | 0 | 1 | F | No | 71.43 | #REF! | #REF! | #REF! | #REF! | #REF! | Religious Worship Area,Assembly - Places of religious worship | 361 | 8 | 60 | 0 | 1, Spc:SpcFunc, 361, 8 ; Religious Worship Area
Religious Worship Area | Assembly - Places of religious worship | 7 | 0.15 | 0 | 0 | 0 | 1 | F | No | 71.43 | #REF! | #REF! | #REF! | #REF! | #REF! | Religious Worship Area,Assembly - Places of religious worship | 361 | 8 | 60 | 0 | 2, 8, "Assembly - Places of religious worship"
Restrooms | Exhaust - Toilets, public | 0 | 0 | 50 | 70 | 0 | 2 | Exh. Note D | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Restrooms,Exhaust - Toilets, public | 362 | 40 | 61 | 1 | 1, Spc:SpcFunc, 362, 40 ; Restrooms
Restrooms | Exhaust - Shower rooms | 0 | 0 | 20 | 50 | 0 | 2 | Exh. Note G,H | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Restrooms,Exhaust - Shower rooms | 362 | 36 | 61 | 1 | 2, 36, "Exhaust - Shower rooms"
Restrooms | Exhaust - Toilets, private | 0 | 0 | 25 | 50 | 0 | 2 | Exh. Note E | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Restrooms,Exhaust - Toilets, private | 362 | 39 | 61 | 1 | 2, 39, "Exhaust - Toilets, private"
Restrooms | Exhaust - Toilets, public | 0 | 0 | 50 | 70 | 0 | 2 | Exh. Note D | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Restrooms,Exhaust - Toilets, public | 362 | 40 | 61 | 1 | 2, 40, "Exhaust - Toilets, public"
Stairwell | General - Corridors | 5 | 0.15 | 0 | 0 | 0 | 1 | F | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Stairwell,General - Corridors | 363 | 49 | 62 | 1 | 1, Spc:SpcFunc, 363, 49 ; Stairwell
Stairwell | General - Corridors | 5 | 0.15 | 0 | 0 | 0 | 1 | F | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Stairwell,General - Corridors | 363 | 49 | 62 | 0 | 2, 49, "General - Corridors"
Stairwell | General - Unoccupied | 0 | 0 | 0 | 0 | 0 | 1 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Stairwell,General - Unoccupied | 363 | 51 | 62 | 1 | 2, 51, "General - Unoccupied"
Stairwell | Residential - Common corridors | 5 | 0.15 | 0 | 0 | 0 | 1 | F | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Stairwell,Residential - Common corridors | 363 | 77 | 62 | 1 | 2, 77, "Residential - Common corridors"
Storage, Commercial/Industrial (Warehouse) | Misc - Warehouses | 1 | 0.15 | 0 | 0 | 0 | 2 | B | No | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | Storage, Commercial/Industrial (Warehouse),Misc - Warehouses | 364 | 70 | 63 | 0 | 1, Spc:SpcFunc, 364, 70 ; Storage, Commercial/Industrial (Warehouse)
Storage, Commercial/Industrial (Warehouse) | Exhaust - Storage rooms, chemical | 0 | 0 | 0 | 0 | 1.5 | 4 | Exh. Note F | Yes | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | Storage, Commercial/Industrial (Warehouse),Exhaust - Storage rooms, chemical | 364 | 38 | 63 | 0 | 2, 38, "Exhaust - Storage rooms, chemical"
Storage, Commercial/Industrial (Warehouse) | General - Occupiable storage rooms for liquids or gels | 2 | 0.15 | 0 | 0 | 0 | 2 | B | Yes | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | Storage, Commercial/Industrial (Warehouse),General - Occupiable storage rooms for liquids or gels | 364 | 50 | 63 | 0 | 2, 50, "General - Occupiable storage rooms for liquids or gels"
Storage, Commercial/Industrial (Warehouse) | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | Storage, Commercial/Industrial (Warehouse),Misc - All others | 364 | 58 | 63 | 0 | 2, 58, "Misc - All others"
Storage, Commercial/Industrial (Warehouse) | Misc - Warehouses | 1 | 0.15 | 0 | 0 | 0 | 2 | B | No | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | Storage, Commercial/Industrial (Warehouse),Misc - Warehouses | 364 | 70 | 63 | 0 | 2, 70, "Misc - Warehouses"
Storage, Commercial/Industrial (Warehouse) | Office - Occupiable storage rooms for dry materials | 2 | 0.15 | 0 | 0 | 0 | 1 |  | No | 1 | #REF! | #REF! | #REF! | #REF! | #REF! | Storage, Commercial/Industrial (Warehouse),Office - Occupiable storage rooms for dry materials | 364 | 73 | 63 | 0 | 2, 73, "Office - Occupiable storage rooms for dry materials"
Storage, Commercial/Industrial (Refrigerated) | Misc - Freezer and refrigerated spaces (<50F) | 0 | 0 | 0 | 0 | 0 | 2 | E | No | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | Storage, Commercial/Industrial (Refrigerated),Misc - Freezer and refrigerated spaces (<50F) | 365 | 62 | 64 | 0 | 1, Spc:SpcFunc, 365, 62 ; Storage, Commercial/Industrial (Refrigerated)
Storage, Commercial/Industrial (Refrigerated) | Exhaust - Refrigerating machinery rooms | 0 | 0 | 0 | 0 | 0 | 3 | Exh. Note F | Yes | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | Storage, Commercial/Industrial (Refrigerated),Exhaust - Refrigerating machinery rooms | 365 | 35 | 64 | 0 | 2, 35, "Exhaust - Refrigerating machinery rooms"
Storage, Commercial/Industrial (Refrigerated) | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | Storage, Commercial/Industrial (Refrigerated),Misc - All others | 365 | 58 | 64 | 0 | 2, 58, "Misc - All others"
Storage, Commercial/Industrial (Refrigerated) | Misc - Freezer and refrigerated spaces (<50F) | 0 | 0 | 0 | 0 | 0 | 2 | E | No | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | Storage, Commercial/Industrial (Refrigerated),Misc - Freezer and refrigerated spaces (<50F) | 365 | 62 | 64 | 0 | 2, 62, "Misc - Freezer and refrigerated spaces (<50F)"
Storage, Commercial/Industrial (Shipping & Handling) | Misc - Shipping/receiving | 5 | 0.15 | 0 | 0 | 0 | 2 | B | No | 2.5 | #REF! | #REF! | #REF! | #REF! | #REF! | Storage, Commercial/Industrial (Shipping & Handling),Misc - Shipping/receiving | 366 | 66 | 65 | 0 | 1, Spc:SpcFunc, 366, 66 ; Storage, Commercial/Industrial (Shipping & Handling)
Storage, Commercial/Industrial (Shipping & Handling) | Misc - Shipping/receiving | 5 | 0.15 | 0 | 0 | 0 | 2 | B | No | 2.5 | #REF! | #REF! | #REF! | #REF! | #REF! | Storage, Commercial/Industrial (Shipping & Handling),Misc - Shipping/receiving | 366 | 66 | 65 | 0 | 2, 66, "Misc - Shipping/receiving"
Storage, General | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | Storage, General,Misc - All others | 380 | 58 | 66 | 1 | 1, Spc:SpcFunc, 380, 58 ; Storage, General
Storage, General | Exhaust - Janitor closets, trash rooms, recycling | 0 | 0 | 0 | 0 | 1 | 3 |  | No | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | Storage, General,Exhaust - Janitor closets, trash rooms, recycling | 380 | 30 | 66 | 1 | 2, 30, "Exhaust - Janitor closets, trash rooms, recycling"
Storage, General | Exhaust - Storage rooms, chemical | 0 | 0 | 0 | 0 | 1.5 | 4 | Exh. Note F | Yes | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | Storage, General,Exhaust - Storage rooms, chemical | 380 | 38 | 66 | 1 | 2, 38, "Exhaust - Storage rooms, chemical"
Storage, General | General - Occupiable storage rooms for liquids or gels | 2 | 0.15 | 0 | 0 | 0 | 2 | B | Yes | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | Storage, General,General - Occupiable storage rooms for liquids or gels | 380 | 50 | 66 | 1 | 2, 50, "General - Occupiable storage rooms for liquids or gels"
Storage, General | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | Storage, General,Misc - All others | 380 | 58 | 66 | 1 | 2, 58, "Misc - All others"
Sports Arena - Playing Area (> 5,000 Spectators) | Sports/Entertainment - Gym, sports arena (play area) | 100 | 0.15 | 0 | 0 | 0 | 2 | F | No | 40 | #REF! | #REF! | #REF! | #REF! | #REF! | Sports Arena - Playing Area (> 5,000 Spectators),Sports/Entertainment - Gym, sports arena (play area) | 367 | 89 | 67 | 0 | 1, Spc:SpcFunc, 367, 89 ; Sports Arena - Playing Area (> 5,000 Spectators)
Sports Arena - Playing Area (> 5,000 Spectators) | Exhaust - Arenas | 0 | 0 | 0 | 0 | 0.5 | 1 | Exh. Note B | No | 40 | #REF! | #REF! | #REF! | #REF! | #REF! | Sports Arena - Playing Area (> 5,000 Spectators),Exhaust - Arenas | 367 | 25 | 67 | 0 | 2, 25, "Exhaust - Arenas"
Sports Arena - Playing Area (> 5,000 Spectators) | Sports/Entertainment - Gym, sports arena (play area) | 100 | 0.15 | 0 | 0 | 0 | 2 | F | No | 40 | #REF! | #REF! | #REF! | #REF! | #REF! | Sports Arena - Playing Area (> 5,000 Spectators),Sports/Entertainment - Gym, sports arena (play area) | 367 | 89 | 67 | 0 | 2, 89, "Sports/Entertainment - Gym, sports arena (play area)"
Sports Arena - Playing Area (> 5,000 Spectators) | Sports/Entertainment - Swimming (deck) | 100 | 0.15 | 0 | 0 | 0 | 2 | F | No | 40 | #REF! | #REF! | #REF! | #REF! | #REF! | Sports Arena - Playing Area (> 5,000 Spectators),Sports/Entertainment - Swimming (deck) | 367 | 94 | 67 | 0 | 2, 94, "Sports/Entertainment - Swimming (deck)"
Sports Arena - Playing Area (> 5,000 Spectators) | Sports/Entertainment - Swimming (pool) | 100 | 0.15 | 0 | 0 | 0 | 2 | F | No | 40 | #REF! | #REF! | #REF! | #REF! | #REF! | Sports Arena - Playing Area (> 5,000 Spectators),Sports/Entertainment - Swimming (pool) | 367 | 95 | 67 | 0 | 2, 95, "Sports/Entertainment - Swimming (pool)"
Sports Arena - Playing Area (2,000 - 5,000 Spectators) | Sports/Entertainment - Gym, sports arena (play area) | 100 | 0.15 | 0 | 0 | 0 | 2 | F | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Sports Arena - Playing Area (2,000 - 5,000 Spectators),Sports/Entertainment - Gym, sports arena (play area) | 368 | 89 | 68 | 0 | 1, Spc:SpcFunc, 368, 89 ; Sports Arena - Playing Area (2,000 - 5,000 Spectators)
Sports Arena - Playing Area (2,000 - 5,000 Spectators) | Exhaust - Arenas | 0 | 0 | 0 | 0 | 0.5 | 1 | Exh. Note B | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Sports Arena - Playing Area (2,000 - 5,000 Spectators),Exhaust - Arenas | 368 | 25 | 68 | 0 | 2, 25, "Exhaust - Arenas"
Sports Arena - Playing Area (2,000 - 5,000 Spectators) | Sports/Entertainment - Gym, sports arena (play area) | 100 | 0.15 | 0 | 0 | 0 | 2 | F | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Sports Arena - Playing Area (2,000 - 5,000 Spectators),Sports/Entertainment - Gym, sports arena (play area) | 368 | 89 | 68 | 0 | 2, 89, "Sports/Entertainment - Gym, sports arena (play area)"
Sports Arena - Playing Area (2,000 - 5,000 Spectators) | Sports/Entertainment - Swimming (deck) | 100 | 0.15 | 0 | 0 | 0 | 2 | F | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Sports Arena - Playing Area (2,000 - 5,000 Spectators),Sports/Entertainment - Swimming (deck) | 368 | 94 | 68 | 0 | 2, 94, "Sports/Entertainment - Swimming (deck)"
Sports Arena - Playing Area (2,000 - 5,000 Spectators) | Sports/Entertainment - Swimming (pool) | 100 | 0.15 | 0 | 0 | 0 | 2 | F | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Sports Arena - Playing Area (2,000 - 5,000 Spectators),Sports/Entertainment - Swimming (pool) | 368 | 95 | 68 | 0 | 2, 95, "Sports/Entertainment - Swimming (pool)"
Sports Arena - Playing Area (< 2,000 Spectators) | Sports/Entertainment - Gym, sports arena (play area) | 100 | 0.15 | 0 | 0 | 0 | 2 | F | No | 25 | #REF! | #REF! | #REF! | #REF! | #REF! | Sports Arena - Playing Area (< 2,000 Spectators),Sports/Entertainment - Gym, sports arena (play area) | 369 | 89 | 69 | 0 | 1, Spc:SpcFunc, 369, 89 ; Sports Arena - Playing Area (< 2,000 Spectators)
Sports Arena - Playing Area (< 2,000 Spectators) | Exhaust - Arenas | 0 | 0 | 0 | 0 | 0.5 | 1 | Exh. Note B | No | 25 | #REF! | #REF! | #REF! | #REF! | #REF! | Sports Arena - Playing Area (< 2,000 Spectators),Exhaust - Arenas | 369 | 25 | 69 | 0 | 2, 25, "Exhaust - Arenas"
Sports Arena - Playing Area (< 2,000 Spectators) | Sports/Entertainment - Gym, sports arena (play area) | 100 | 0.15 | 0 | 0 | 0 | 2 | F | No | 25 | #REF! | #REF! | #REF! | #REF! | #REF! | Sports Arena - Playing Area (< 2,000 Spectators),Sports/Entertainment - Gym, sports arena (play area) | 369 | 89 | 69 | 0 | 2, 89, "Sports/Entertainment - Gym, sports arena (play area)"
Sports Arena - Playing Area (< 2,000 Spectators) | Sports/Entertainment - Swimming (deck) | 100 | 0.15 | 0 | 0 | 0 | 2 | F | No | 25 | #REF! | #REF! | #REF! | #REF! | #REF! | Sports Arena - Playing Area (< 2,000 Spectators),Sports/Entertainment - Swimming (deck) | 369 | 94 | 69 | 0 | 2, 94, "Sports/Entertainment - Swimming (deck)"
Sports Arena - Playing Area (< 2,000 Spectators) | Sports/Entertainment - Swimming (pool) | 100 | 0.15 | 0 | 0 | 0 | 2 | F | No | 25 | #REF! | #REF! | #REF! | #REF! | #REF! | Sports Arena - Playing Area (< 2,000 Spectators),Sports/Entertainment - Swimming (pool) | 369 | 95 | 69 | 0 | 2, 95, "Sports/Entertainment - Swimming (pool)"
Sports Arena - Playing Area (Recreational) | Sports/Entertainment - Gym, sports arena (play area) | 100 | 0.15 | 0 | 0 | 0 | 2 | F | No | 10 | #REF! | #REF! | #REF! | #REF! | #REF! | Sports Arena - Playing Area (Recreational),Sports/Entertainment - Gym, sports arena (play area) | 370 | 89 | 70 | 0 | 1, Spc:SpcFunc, 370, 89 ; Sports Arena - Playing Area (Recreational)
Sports Arena - Playing Area (Recreational) | Sports/Entertainment - Gym, sports arena (play area) | 100 | 0.15 | 0 | 0 | 0 | 2 | F | No | 10 | #REF! | #REF! | #REF! | #REF! | #REF! | Sports Arena - Playing Area (Recreational),Sports/Entertainment - Gym, sports arena (play area) | 370 | 89 | 70 | 0 | 2, 89, "Sports/Entertainment - Gym, sports arena (play area)"
Sports Arena - Playing Area (Recreational) | Sports/Entertainment - Health club/aerobics room | 100 | 0.15 | 0 | 0 | 0 | 2 | F | No | 10 | #REF! | #REF! | #REF! | #REF! | #REF! | Sports Arena - Playing Area (Recreational),Sports/Entertainment - Health club/aerobics room | 370 | 90 | 70 | 0 | 2, 90, "Sports/Entertainment - Health club/aerobics room"
Sports Arena - Playing Area (Recreational) | Sports/Entertainment - Health club/weight rooms | 100 | 0.15 | 0 | 0 | 0 | 2 | F | No | 10 | #REF! | #REF! | #REF! | #REF! | #REF! | Sports Arena - Playing Area (Recreational),Sports/Entertainment - Health club/weight rooms | 370 | 91 | 70 | 0 | 2, 91, "Sports/Entertainment - Health club/weight rooms"
Sports Arena - Playing Area (Recreational) | Sports/Entertainment - Swimming (deck) | 100 | 0.15 | 0 | 0 | 0 | 2 | F | No | 10 | #REF! | #REF! | #REF! | #REF! | #REF! | Sports Arena - Playing Area (Recreational),Sports/Entertainment - Swimming (deck) | 370 | 94 | 70 | 0 | 2, 94, "Sports/Entertainment - Swimming (deck)"
Sports Arena - Playing Area (Recreational) | Sports/Entertainment - Swimming (pool) | 100 | 0.15 | 0 | 0 | 0 | 2 | F | No | 10 | #REF! | #REF! | #REF! | #REF! | #REF! | Sports Arena - Playing Area (Recreational),Sports/Entertainment - Swimming (pool) | 370 | 95 | 70 | 0 | 2, 95, "Sports/Entertainment - Swimming (pool)"
Theater Area (Motion Picture) | Assembly - Auditorium seating area | 7 | 0.15 | 0 | 0 | 0 | 1 | F | No | 71.43 | #REF! | #REF! | #REF! | #REF! | #REF! | Theater Area (Motion Picture),Assembly - Auditorium seating area | 371 | 1 | 71 | 0 | 1, Spc:SpcFunc, 371, 1 ; Theater Area (Motion Picture)
Theater Area (Motion Picture) | Assembly - Auditorium seating area | 7 | 0.15 | 0 | 0 | 0 | 1 | F | No | 71.43 | #REF! | #REF! | #REF! | #REF! | #REF! | Theater Area (Motion Picture),Assembly - Auditorium seating area | 371 | 1 | 71 | 0 | 2, 1, "Assembly - Auditorium seating area"
Theater Area (Performance) | Sports/Entertainment - Stages, studios | 100 | 0.15 | 0 | 0 | 0 | 2 | F | No | 71.43 | #REF! | #REF! | #REF! | #REF! | #REF! | Theater Area (Performance),Sports/Entertainment - Stages, studios | 372 | 93 | 72 | 0 | 1, Spc:SpcFunc, 372, 93 ; Theater Area (Performance)
Theater Area (Performance) | Education - Music/theater/dance | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 71.43 | #REF! | #REF! | #REF! | #REF! | #REF! | Theater Area (Performance),Education - Music/theater/dance | 372 | 20 | 72 | 0 | 2, 20, "Education - Music/theater/dance"
Theater Area (Performance) | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 71.43 | #REF! | #REF! | #REF! | #REF! | #REF! | Theater Area (Performance),Misc - All others | 372 | 58 | 72 | 0 | 2, 58, "Misc - All others"
Theater Area (Performance) | Sports/Entertainment - Stages, studios | 100 | 0.15 | 0 | 0 | 0 | 2 | F | No | 71.43 | #REF! | #REF! | #REF! | #REF! | #REF! | Theater Area (Performance),Sports/Entertainment - Stages, studios | 372 | 93 | 72 | 0 | 2, 93, "Sports/Entertainment - Stages, studios"
Transportation Function (Baggage Area) | Misc - Transportation waiting | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 16.665 | #REF! | #REF! | #REF! | #REF! | #REF! | Transportation Function (Baggage Area),Misc - Transportation waiting | 373 | 69 | 73 | 0 | 1, Spc:SpcFunc, 373, 69 ; Transportation Function (Baggage Area)
Transportation Function (Baggage Area) | Misc - Sorting, packing, light assembly | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 16.665 | #REF! | #REF! | #REF! | #REF! | #REF! | Transportation Function (Baggage Area),Misc - Sorting, packing, light assembly | 373 | 67 | 73 | 0 | 2, 67, "Misc - Sorting, packing, light assembly"
Transportation Function (Baggage Area) | Misc - Transportation waiting | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 16.665 | #REF! | #REF! | #REF! | #REF! | #REF! | Transportation Function (Baggage Area),Misc - Transportation waiting | 373 | 69 | 73 | 0 | 2, 69, "Misc - Transportation waiting"
Transportation Function (Ticketing Area) | Misc - Transportation waiting | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 16.665 | #REF! | #REF! | #REF! | #REF! | #REF! | Transportation Function (Ticketing Area),Misc - Transportation waiting | 374 | 69 | 74 | 0 | 1, Spc:SpcFunc, 374, 69 ; Transportation Function (Ticketing Area)
Transportation Function (Ticketing Area) | Assembly - Lobbies | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 16.665 | #REF! | #REF! | #REF! | #REF! | #REF! | Transportation Function (Ticketing Area),Assembly - Lobbies | 374 | 5 | 74 | 0 | 2, 5, "Assembly - Lobbies"
Transportation Function (Ticketing Area) | Misc - Transportation waiting | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 16.665 | #REF! | #REF! | #REF! | #REF! | #REF! | Transportation Function (Ticketing Area),Misc - Transportation waiting | 374 | 69 | 74 | 0 | 2, 69, "Misc - Transportation waiting"
Unleased Tenant Area | Office - Office space | 5 | 0.15 | 0 | 0 | 0 | 1 | F | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Unleased Tenant Area,Office - Office space | 375 | 74 | 75 | 0 | 1, Spc:SpcFunc, 375, 74 ; Unleased Tenant Area
Unleased Tenant Area | Retail - Sales | 17 | 0.2 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Unleased Tenant Area,Retail - Sales | 375 | 83 | 75 | 0 | 2, 83, "Retail - Sales"
Unleased Tenant Area | Food Service - Cafeteria/fast-food dining | 33 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Unleased Tenant Area,Food Service - Cafeteria/fast-food dining | 375 | 43 | 75 | 0 | 2, 43, "Food Service - Cafeteria/fast-food dining"
Unleased Tenant Area | Food Service - Restaurant dining rooms | 33 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Unleased Tenant Area,Food Service - Restaurant dining rooms | 375 | 45 | 75 | 0 | 2, 45, "Food Service - Restaurant dining rooms"
Unleased Tenant Area | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Unleased Tenant Area,Misc - All others | 375 | 58 | 75 | 0 | 2, 58, "Misc - All others"
Unleased Tenant Area | Misc - Warehouses | 1 | 0.15 | 0 | 0 | 0 | 2 | B | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Unleased Tenant Area,Misc - Warehouses | 375 | 70 | 75 | 0 | 2, 70, "Misc - Warehouses"
Unleased Tenant Area | Office - Office space | 5 | 0.15 | 0 | 0 | 0 | 1 | F | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Unleased Tenant Area,Office - Office space | 375 | 74 | 75 | 0 | 2, 74, "Office - Office space"
Unoccupied-Exclude from Gross Floor Area | NA | 1 | 0.15 | 0 | 0 | 0 | 2 | B | No | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | Unoccupied-Exclude from Gross Floor Area,NA | 376 | 96 | 76 | 0 | 1, Spc:SpcFunc, 376, 96 ; Unoccupied-Exclude from Gross Floor Area
Unoccupied-Exclude from Gross Floor Area | NA | 1 | 0.15 | 0 | 0 | 0 | 2 | B | No | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | Unoccupied-Exclude from Gross Floor Area,NA | 376 | 96 | 76 | 0 | 2, 96, "NA"
Unoccupied-Include in Gross Floor Area | NA | 1 | 0.15 | 0 | 0 | 0 | 2 | B | No | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | Unoccupied-Include in Gross Floor Area,NA | 377 | 96 | 77 | 0 | 1, Spc:SpcFunc, 377, 96 ; Unoccupied-Include in Gross Floor Area
Unoccupied-Include in Gross Floor Area | NA | 1 | 0.15 | 0 | 0 | 0 | 2 | B | No | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | Unoccupied-Include in Gross Floor Area,NA | 377 | 96 | 77 | 0 | 2, 96, "NA"
Videoconferencing Studio | General - Conference/meeting | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Videoconferencing Studio,General - Conference/meeting | 378 | 48 | 78 | 0 | 1, Spc:SpcFunc, 378, 48 ; Videoconferencing Studio
Videoconferencing Studio | General - Conference/meeting | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Videoconferencing Studio,General - Conference/meeting | 378 | 48 | 78 | 0 | 2, 48, "General - Conference/meeting"
Conference, Multipurpose and Meeting Area | General - Conference/meeting | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Conference, Multipurpose and Meeting Area,General - Conference/meeting | 381 | 48 | 80 | 0 | 1, Spc:SpcFunc, 381, 48 ; Conference, Multipurpose and Meeting Area
Conference, Multipurpose and Meeting Area | General - Conference/meeting | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Conference, Multipurpose and Meeting Area,General - Conference/meeting | 381 | 48 | 80 | 0 | 2, 48, "General - Conference/meeting"
Conference, Multipurpose and Meeting Area | Lodging - Multipurpose assembly | 33 | 0.15 | 0 | 0 | 0 | 1 | F | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Conference, Multipurpose and Meeting Area,Lodging - Multipurpose assembly | 381 | 57 | 80 | 0 | 2, 57, "Lodging - Multipurpose assembly"
Conference, Multipurpose and Meeting Area | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 33.335 | #REF! | #REF! | #REF! | #REF! | #REF! | Conference, Multipurpose and Meeting Area,Misc - All others | 381 | 58 | 80 | 0 | 2, 58, "Misc - All others"
Storage | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | Storage,Misc - All others | 379 | 58 | 81 | 0 | 1, Spc:SpcFunc, 379, 58 ; Storage
Storage | Exhaust - Storage rooms, chemical | 0 | 0 | 0 | 0 | 1.5 | 4 | Exh. Note F | Yes | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | Storage,Exhaust - Storage rooms, chemical | 379 | 38 | 81 | 0 | 2, 38, "Exhaust - Storage rooms, chemical"
Storage | General - Occupiable storage rooms for liquids or gels | 2 | 0.15 | 0 | 0 | 0 | 2 | B | Yes | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | Storage,General - Occupiable storage rooms for liquids or gels | 379 | 50 | 81 | 0 | 2, 50, "General - Occupiable storage rooms for liquids or gels"
Storage | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | Storage,Misc - All others | 379 | 58 | 81 | 0 | 2, 58, "Misc - All others"
Health Care / Assisted Living (Nurse's Station) | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Health Care / Assisted Living (Nurse's Station),Misc - All others | 382 | 58 | 82 | 1 | 1, Spc:SpcFunc, 382, 58 ; Health Care / Assisted Living (Nurse's Station)
Health Care / Assisted Living (Nurse's Station) | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Health Care / Assisted Living (Nurse's Station),Misc - All others | 382 | 58 | 82 | 1 | 2, 58, "Misc - All others"
Health Care / Assisted Living (Physical Therapy Room) | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Health Care / Assisted Living (Physical Therapy Room),Misc - All others | 383 | 58 | 83 | 1 | 1, Spc:SpcFunc, 383, 58 ; Health Care / Assisted Living (Physical Therapy Room)
Health Care / Assisted Living (Physical Therapy Room) | Misc - All others | 5 | 0.15 | 0 | 0 | 0 | 2 |  | No | 5 | #REF! | #REF! | #REF! | #REF! | #REF! | Health Care / Assisted Living (Physical Therapy Room),Misc - All others | 383 | 58 | 83 | 1 | 2, 58, "Misc - All others"
# times referenced above | VentSpcFunc from ventilation list
7 | Assembly - Auditorium seating area
4 | Assembly - Courtrooms
5 | Assembly - Legislative chambers
4 | Assembly - Libraries (reading rooms and stack areas)
3 | Assembly - Lobbies
1 | Assembly - Museums (childrens)
2 | Assembly - Museums/galleries
5 | Assembly - Places of religious worship
2 | Education - Art classroom
2 | Education - Classrooms (ages 9-18)
1 | Education - Classrooms (ages 5-8)
2 | Education - Computer lab
1 | Education - Daycare (through age 4)
1 | Education - Daycare sickroom
2 | Education - Lecture hall (fixed seats)
1 | Education - Lecture/postsecondary classroom
2 | Education - Media center
3 | Education - Multiuse assembly
0 | Education - Music/theater/dance
3 | Education - Science laboratories
4 | Education - University/college laboratories
2 | Education - Wood shop
1 | Exhaust - All other locker rooms
5 | Exhaust - Arenas
3 | Exhaust - Auto repair rooms
1 | Exhaust - Cells with toilet
6 | Exhaust - Copy, printing rooms
4 | Exhaust - Darkrooms
2 | Exhaust - Janitor closets, trash rooms, recycling
2 | Exhaust - Kitchenettes
2 | Exhaust - Locker rooms for athletic or industrial facilities
3 | Exhaust - Paint spray booths
4 | Exhaust - Parking garages
2 | Exhaust - Refrigerating machinery rooms
2 | Exhaust - Shower rooms
1 | Exhaust - Soiled laundry storage rooms
2 | Exhaust - Storage rooms, chemical
0 | Exhaust - Toilets - private
4 | Exhaust - Toilets, public
5 | Exhaust - Woodwork shop/classrooms
2 | Food Service - Bars, cocktail lounges
6 | Food Service - Cafeteria/fast-food dining
3 | Food Service - Kitchen (cooking)
3 | Food Service - Restaurant dining rooms
4 | General - Break rooms
1 | General - Coffee Stations
6 | General - Conference/meeting
9 | General - Corridors
3 | General - Occupiable storage rooms for liquids or gels
3 | General - Unoccupied
1 | Lodging - Barracks sleeping areas
2 | Lodging - Bedroom/living room
1 | Lodging - Laundry rooms within dwelling units
3 | Lodging - Laundry rooms, central
4 | Lodging - Lobbies/pre-function
3 | Lodging - Multipurpose assembly
42 | Misc - All others
1 | Misc - Bank vaults/safe deposit
3 | Misc - Banks or bank lobbies
2 | Misc - Computer (not printing)
2 | Misc - Freezer and refrigerated spaces (<50F)
9 | Misc - General manufacturing (excludes heavy industrial and process using chemicals)
3 | Misc - Pharmacy (preparation area)
1 | Misc - Photo studios
2 | Misc - Shipping/receiving
5 | Misc - Sorting, packing, light assembly
2 | Misc - Telephone closets
7 | Misc - Transportation waiting
2 | Misc - Warehouses
1 | Office - Breakrooms
5 | Office - Main entry lobbies
1 | Office - Occupiable storage rooms for dry materials
6 | Office - Office space
1 | Office - Reception areas
1 | Office - Telephone/data entry
2 | Residential - Common corridors
2 | Retail - Barbershop
3 | Retail - Beauty and nail salons
1 | Retail - Coin-operated laundries
3 | Retail - Mall common areas
1 | Retail - Pet shops (animal areas)
4 | Retail - Sales
2 | Retail - Supermarket
1 | Sports/Entertainment - Bowling alley (seating)
1 | Sports/Entertainment - Disco/dance floors
1 | Sports/Entertainment - Gambling casinos
1 | Sports/Entertainment - Game arcades
10 | Sports/Entertainment - Gym, sports arena (play area)
2 | Sports/Entertainment - Health club/aerobics room
2 | Sports/Entertainment - Health club/weight rooms
1 | Sports/Entertainment - Spectator areas
2 | Sports/Entertainment - Stages, studios
5 | Sports/Entertainment - Swimming (deck)
Note on Y3: David Reddy: Line Feed (Char(10))
Note on M6: David Reddy: IfVentSpcFunc occupancy is 0, then use SpcFunc occupancy
Note on O6: David Reddy: This is the VentPerPerson used for modeling DCV. Removed limit of 15cfm/person, see ticket 3461
Note on P6: David Reddy: Highlighted values are greater than the Ra defined in VentSpcFunc table

## ForCSV-19ValidVentSpcFuncEnums (hidden)
// This table pasted into App5-4C_Ventilation-T24N_2022.csv |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96
; | Number of uses - > | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TABLE ValidVentilationSpaceFunctionEnumerations | [97 empty] | ;
| ValidVentSpcFuncEnum | Assembly - Auditorium seating area | Assembly - Courtrooms | Assembly - Legislative chambers | Assembly - Libraries (reading rooms and stack areas) | Assembly - Lobbies | Assembly - Museums (childrens) | Assembly - Museums/galleries | Assembly - Places of religious worship | Education - Art classroom | Education - Classrooms (ages 9-18) | Education - Classrooms (ages 5-8) | Education - Computer lab | Education - Daycare (through age 4) | Education - Daycare sickroom | Education - Lecture hall (fixed seats) | Education - Lecture/postsecondary classroom | Education - Media center | Education - Metal shop | Education - Multiuse assembly | Education - Music/theater/dance | Education - Science laboratories | Education - University/college laboratories | Education - Wood shop | Exhaust - All other locker rooms | Exhaust - Arenas | Exhaust - Animal operating rooms | Exhaust - Animal postoperative recovery room | Exhaust - Animal preparation rooms | Exhaust - Animal procedure room | Exhaust - Animal surgery scrub | Exhaust - Animal Necropsy | Exhaust - Arenas | Exhaust - Auto repair rooms | Exhaust - Cells with toilet | Exhaust - Copy, printing rooms | Exhaust - Darkrooms | Exhaust - Janitor closets, trash rooms, recycling | Exhaust - Kitchenettes | Exhaust - Large-animal holding room | Exhaust - Locker rooms for athletic or industrial facilities | Exhaust - Paint spray booths | Exhaust - Parking garages | Exhaust - Refrigerating machinery rooms | Exhaust - Shower rooms | Exhaust - Small-animal-cage room (static cages) | Exhaust - Small-animal-cage room (ventilated cages) | Exhaust - Soiled laundry storage rooms | Exhaust - Storage rooms, chemical | Exhaust - Toilets, private | Exhaust - Toilets, public | Exhaust - Woodwork shop/classrooms | Food Service - Bars, cocktail lounges | Food Service - Cafeteria/fast-food dining | Food Service - Kitchen (cooking) | Food Service - Restaurant dining rooms | General - Break rooms | General - Coffee Stations | General - Conference/meeting | General - Corridors | General - Occupiable storage rooms for liquids or gels | General - Unoccupied | Lodging - Barracks sleeping areas | Lodging - Bedroom/living room | Lodging - Laundry rooms within dwelling units | Lodging - Laundry rooms, central | Lodging - Lobbies/pre-function | Lodging - Multipurpose assembly | Misc - All others | Misc - Bank vaults/safe deposit | Misc - Banks or bank lobbies | Misc - Computer (not printing) | Misc - Freezer and refrigerated spaces (<50F) | Misc - General manufacturing (excludes heavy industrial and process using chemicals) | Misc - Pharmacy (preparation area) | Misc - Photo studios | Misc - Shipping/receiving | Misc - Sorting, packing, light assembly | Misc - Telephone closets | Misc - Transportation waiting | Misc - Warehouses | Office - Breakrooms | Office - Main entry lobbies | Office - Occupiable storage rooms for dry materials | Office - Office space | Office - Reception areas | Office - Telephone/data entry | Residential - Common corridors | Retail - Barbershop | Retail - Beauty and nail salons | Retail - Coin-operated laundries | Retail - Mall common areas | Retail - Pet shops (animal areas) | Retail - Sales | Retail - Supermarket | Sports/Entertainment - Bowling alley (seating) | Sports/Entertainment - Disco/dance floors | ; | <- Number of uses
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
#REF!

## ForCSV-22ValidVentSpcFuncEnums (hidden)
; |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96
; | Number of uses - > | 4 | 4 | 4 | 2 | 3 | 1 | 1 | 3 | 2 | 1 | 1 | 2 | 1 | 1 | 2 | 1 | 2 | 1 | 3 | 3 | 3 | 3 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5 | 2 | 1 | 5 | 4 | 1 | 1 | 1 | 1 | 3 | 2 | 2 | 2 | 1 | 1 | 1 | 2 | 1 | 2 | 5 | 2 | 4 | 2 | 3 | 2 | 1 | 5 | 5 | 3 | 3 | 1 | 1 | 1 | 2 | 4 | 2 | 32 | 1 | 2 | 1 | 1 | 5 | 2 | 1 | 1 | 5 | 1 | 5 | 2 | 1 | 3 | 1 | 4 | 1 | 1 | 2 | 2 | 2 | 1 | 2 | 1 | 3 | 1 | 1 | 1
TABLE ValidVentilationSpaceFunctionEnumerations | [97 empty] | ;
| ValidVentSpcFuncEnum | Assembly - Auditorium seating area | Assembly - Courtrooms | Assembly - Legislative chambers | Assembly - Libraries (reading rooms and stack areas) | Assembly - Lobbies | Assembly - Museums (childrens) | Assembly - Museums/galleries | Assembly - Places of religious worship | Education - Art classroom | Education - Classrooms (ages 9-18) | Education - Classrooms (ages 5-8) | Education - Computer lab | Education - Daycare (through age 4) | Education - Daycare sickroom | Education - Lecture hall (fixed seats) | Education - Lecture/postsecondary classroom | Education - Media center | Education - Metal shop | Education - Multiuse assembly | Education - Music/theater/dance | Education - Science laboratories | Education - University/college laboratories | Education - Wood shop | Exhaust - All other locker rooms | Exhaust - Animal imaging(MRI/CT/PET) | Exhaust - Animal operating rooms | Exhaust - Animal postoperative recovery room | Exhaust - Animal preparation rooms | Exhaust - Animal procedure room | Exhaust - Animal surgery scrub | Exhaust - Animal Necropsy | Exhaust - Arenas | Exhaust - Auto repair rooms | Exhaust - Cells with toilet | Exhaust - Copy, printing rooms | Exhaust - Darkrooms | Exhaust - Janitor closets, trash rooms, recycling | Exhaust - Kitchenettes | Exhaust - Large-animal holding room | Exhaust - Locker rooms for athletic or industrial facilities | Exhaust - Paint spray booths | Exhaust - Parking garages | Exhaust - Refrigerating machinery rooms | Exhaust - Shower rooms | Exhaust - Small-animal-cage room (static cages) | Exhaust - Small-animal-cage room (ventilated cages) | Exhaust - Soiled laundry storage rooms | Exhaust - Storage rooms, chemical | Exhaust - Toilets, private | Exhaust - Toilets, public | Exhaust - Woodwork shop/classrooms | Food Service - Bars, cocktail lounges | Food Service - Cafeteria/fast-food dining | Food Service - Kitchen (cooking) | Food Service - Restaurant dining rooms | General - Break rooms | General - Coffee Stations | General - Conference/meeting | General - Corridors | General - Occupiable storage rooms for liquids or gels | General - Unoccupied | Lodging - Barracks sleeping areas | Lodging - Bedroom/living room | Lodging - Laundry rooms within dwelling units | Lodging - Laundry rooms, central | Lodging - Lobbies/pre-function | Lodging - Multipurpose assembly | Misc - All others | Misc - Bank vaults/safe deposit | Misc - Banks or bank lobbies | Misc - Computer (not printing) | Misc - Freezer and refrigerated spaces (<50F) | Misc - General manufacturing (excludes heavy industrial and process using chemicals) | Misc - Pharmacy (preparation area) | Misc - Photo studios | Misc - Shipping/receiving | Misc - Sorting, packing, light assembly | Misc - Telephone closets | Misc - Transportation waiting | Misc - Warehouses | Office - Breakrooms | Office - Main entry lobbies | Office - Occupiable storage rooms for dry materials | Office - Office space | Office - Reception areas | Office - Telephone/data entry | Residential - Common corridors | Retail - Barbershop | Retail - Beauty and nail salons | Retail - Coin-operated laundries | Retail - Mall common areas | Retail - Pet shops (animal areas) | Retail - Sales | Retail - Supermarket | Sports/Entertainment - Bowling alley (seating) | Sports/Entertainment - Disco/dance floors | ; | <- Number of uses
| Aging Eye/Low-vision (Corridor Area) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 1
| Aging Eye/Low-vision (Dining) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 1
| Aging Eye/Low-vision (Lobby, Main Entry) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 1
| Aging Eye/Low-vision (Lounge/Waiting Area) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 1
| Aging Eye/Low-vision (Multipurpose Room) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 1
| Aging Eye/Low-vision (Religious Worship Area) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 1
| Aging Eye/Low-vision (Restroom) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 1
| Aging Eye/Low-vision (Stairwell) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 1
| Audience Seating Area | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | ; | 6
| Auditorium Area | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 5
| Auto Repair / Maintenance Area | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 1
| Barber, Beauty Salon, Spa Area | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 2
| Civic Meeting Place Area | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 5
| Classroom, Lecture, Training, Vocational Areas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 21
| Computer Room | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 5
| Concourse and Atria Area | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | ; | 7
| Convention, Conference, Multipurpose and Meeting Area | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 8
| Copy Room | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 1
| Corridor Area | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | ; | 5
| Dining Area (Bar/Lounge and Fine Dining) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 2
| Dining Area (Cafeteria/Fast Food) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 1
| Dining Area (Family and Leisure) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 3
| Electrical, Mechanical, Telephone Rooms | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 4
| Exercise/Fitness Center and Gymnasium Areas | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | ; | 3
| Financial Transaction Area | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 3
| Healthcare Facility and Hospitals (Exam/Treatment Room) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 3
| Healthcare Facility and Hospitals (Imaging Room) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 2
| Healthcare Facility and Hospitals (Medical Supply Room) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 1
| Healthcare Facility and Hospitals (Nursery) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 1
| Healthcare Facility and Hospitals (Nurse's Station) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 1
| Healthcare Facility and Hospitals (Operating Room) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 4
| Healthcare Facility and Hospitals (Patient Room) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 4
| Healthcare Facility and Hospitals (Physical Therapy Room) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 1
| Healthcare Facility and Hospitals (Recovery Room) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 2
| High-Rise Residential Living Spaces | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| Hotel Function Area | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 3
| Hotel/Motel Guest Room | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 2
| Kitchen/Food Preparation Area | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 1
| Kitchenette or Residential Kitchen | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 1
| Laboratory, Scientific | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 5
| Laundry Area | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 4
| Library (Reading Area) | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 1
| Library (Stacks Area) | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 1
| Lobby, Main Entry | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 4
| Locker Room | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 3
| Lounge, Breakroom, or Waiting Area | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 6
| Manufacturing, Commercial & Industrial Work Area (Low Bay) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 9
| Manufacturing, Commercial & Industrial Work Area (High Bay) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 7
| Manufacturing, Commercial & Industrial Work Area (Precision) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 7
| Museum Area (Exhibition/Display) | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 2
| Museum Area (Restoration Room) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 12
| Office Area (>250 square feet) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 1
| Office Area (<250 square feet) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 1
| Parking Garage Area (Parking Zone and Ramps) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 1
| Parking Garage Area (Daylight Adaptation Zones) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 1
| Pharmacy Area | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 1
| Retail Sales Area (Grocery Sales) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | ; | 1
| Retail Sales Area (Retail Merchandise Sales) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | ; | 2
| Retail Sales Area (Fitting Room) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | ; | 2
| Religious Worship Area | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 1
| Restrooms | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 3
| Stairwell | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 3
| Storage, Commercial/Industrial (Warehouse) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 5
| Storage, Commercial/Industrial (Refrigerated) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 3
| Storage, Commercial/Industrial (Shipping & Handling) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 1
| Sports Arena - Playing Area (> 5,000 Spectators) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 1
| Sports Arena - Playing Area (2,000 - 5,000 Spectators) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 1
| Sports Arena - Playing Area (< 2,000 Spectators) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 1
| Sports Arena - Playing Area (Recreational) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| Theater Area (Motion Picture) | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 1
| Theater Area (Performance) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 2
| Transportation Function (Baggage Area) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 2
| Transportation Function (Ticketing Area) | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 2
| Unleased Tenant Area | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | ; | 6
| Unoccupied-Exclude from Gross Floor Area | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| Unoccupied-Include in Gross Floor Area | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| Videoconferencing Studio | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 1
| All other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 3
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
| Storage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 3
| Health Care / Assisted Living (Nurse's Station) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 1
| Health Care / Assisted Living (Physical Therapy Room) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 1
| #REF! | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | ; | 0
0

## FuncSchGrp Table
// Schedule names by Space:FunctionScheduleGroup
TABLE SpaceFunctionGroups
| FuncGroup | OccSchRef | RecptSchRef | HotWtrHtgSchRef | IntLtgRegSchRef | ProcGasSchRef | CommRfrgEqpSchRef | InfSchRef | AvailSchRef | HtgTstatSchRef | ClgTstatSchRef | ElevSchRef | EscalSchRef | WtrHtrTempSetptSchRef
// | Function Group Name | Occupancy Schedule | Receptacle Schedule | Hot Water Schedule | Regulated Lighting Schedule | Process Gas Schedule | Refrigeration Schedule | Infiltration Schedule | Availability Sched | Heating Setpoint Schedule (F) | Cooling Setpoint Schedule (F) | Elevator Schedule | Escalator Schedule | Water Heater Temperature Setpoint Schedule
| Assembly | AssemblyOccupancy | AssemblyReceptacle | AssemblyServiceHotWater | AssemblyLights | AssemblyGasEquip | AssemblyRefrigeration | AssemblyInfiltration | AssemblyHVACAvail | AssemblyHtgSetpt | AssemblyClgSetpt | AssemblyElevator | AssemblyEscalator | AssemblyWtrHtrSetpt
| Data | DataOccupancy | DataReceptacle | DataServiceHotWater | DataLights | DataGasEquip | DataRefrigeration | DataInfiltration | DataHVACAvail | DataHtgSetpt | DataClgSetpt | DataElevator | DataEscalator | DataWtrHtrSetpt
| Health | HealthOccupancy | HealthReceptacle | HealthServiceHotWater | HealthLights | HealthGasEquip | HealthRefrigeration | HealthInfiltration | HealthHVACAvail | HealthHtgSetpt | HealthClgSetpt | HealthElevator | HealthEscalator | HealthWtrHtrSetpt
| Laboratory | LabOccupancy | LabReceptacle | LabServiceHotWater | LabLights | LabGasEquip | LabRefrigeration | LabInfiltration | LabHVACAvail | LabHtgSetpt | LabClgSetpt | LabElevator | LabEscalator | LabWtrHtrSetpt
| Manufacturing | ManufacturingOccupancy | ManufacturingReceptacle | ManufacturingServiceHotWater | ManufacturingLights | ManufacturingGasEquip | ManufacturingRefrigeration | ManufacturingInfiltration | ManufacturingHVACAvail | ManufacturingHtgSetpt | ManufacturingClgSetpt | ManufacturingElevator | ManufacturingEscalator | ManufacturingWtrHtrSetpt
| Office | OfficeOccupancy | OfficeReceptacle | OfficeServiceHotWater | OfficeLights | OfficeGasEquip | OfficeRefrigeration | OfficeInfiltration | OfficeHVACAvail | OfficeHtgSetpt | OfficeClgSetpt | OfficeElevator | OfficeEscalator | OfficeWtrHtrSetpt
| Parking | ParkingOccupancy | ParkingReceptacle | ParkingServiceHotWater | ParkingLights | ParkingGasEquip | ParkingRefrigeration | ParkingInfiltration | ParkingHVACAvail | ParkingHtgSetpt | ParkingClgSetpt | ParkingElevator | ParkingEscalator | ParkingWtrHtrSetpt
| ResidentialLiving | ResidentialLivingOccupancy | ResidentialLivingReceptacle | ResidentialLivingServiceHotWater | ResidentialLivingLights | ResidentialLivingGasEquip | ResidentialLivingRefrigeration | ResidentialLivingInfiltration | ResidentialLivingHVACAvail | ResidentialLivingHtgSetpt | ResidentialLivingClgSetpt | ResidentialLivingElevator | ResidentialLivingEscalator | ResidentialLivingWtrHtrSetpt
| ResidentialCommon | ResidentialCommonOccupancy | ResidentialCommonReceptacle | ResidentialCommonServiceHotWater | ResidentialCommonLights | ResidentialCommonGasEquip | ResidentialCommonRefrigeration | ResidentialCommonInfiltration | ResidentialCommonHVACAvail | ResidentialCommonHtgSetpt | ResidentialCommonClgSetpt | ResidentialCommonElevator | ResidentialCommonEscalator | ResidentialCommonWtrHtrSetpt
| Restaurant | RestaurantOccupancy | RestaurantReceptacle | RestaurantServiceHotWater | RestaurantLights | RestaurantGasEquip | RestaurantRefrigeration | RestaurantInfiltration | RestaurantHVACAvail | RestaurantHtgSetpt | RestaurantClgSetpt | RestaurantElevator | RestaurantEscalator | RestaurantWtrHtrSetpt
| Retail | RetailOccupancy | RetailReceptacle | RetailServiceHotWater | RetailLights | RetailGasEquip | RetailRefrigeration | RetailInfiltration | RetailHVACAvail | RetailHtgSetpt | RetailClgSetpt | RetailElevator | RetailEscalator | RetailWtrHtrSetpt
| School | SchoolOccupancy | SchoolReceptacle | SchoolServiceHotWater | SchoolLights | SchoolGasEquip | SchoolRefrigeration | SchoolInfiltration | SchoolHVACAvail | SchoolHtgSetpt | SchoolClgSetpt | SchoolElevator | SchoolEscalator | SchoolWtrHtrSetpt
| Warehouse | WarehouseOccupancy | WarehouseReceptacle | WarehouseServiceHotWater | WarehouseLights | WarehouseGasEquip | WarehouseRefrigeration | WarehouseInfiltration | WarehouseHVACAvail | WarehouseHtgSetpt | WarehouseClgSetpt | WarehouseElevator | WarehouseEscalator | WarehouseWtrHtrSetpt
ENDTABLE

## CBC Table (hidden)
| Occupancy |  | Use | CBC Occupancy Load (ft²/occ) |  | CBC Occupancy Load | CBC Based Ventilation (cfm/ft²)7 | Ventilation from Table 121-A (cfm/ft²)
[6 empty] | (occ/1000 ft²)6 |  |  | Code: Standards 120.1(b)
1) | Aircraft Hangars |  |  | 500 |  | 2 | 0.015 | 0.15
2) | Auction Rooms |  |  | See Section 1004.7 |  |  |  | 0.15 | 2. Mechanical ventilation. Each space that is not naturally ventilated under Item 1 above shall be ventilated
3) | Assembly Areas (Concentrated Use) | [7 empty] | with a mechanical system capable of providing an outdoor air rate no less than the larger of:
|  | Auditoriums |  | See Section 1004.7 |  |  |  | 0.15 | A. The conditioned floor area of the space times the applicable ventilation rate from TABLE 120.1-A; or
|  | Bowling Alleys |  | 5 persons per lane |  |  |  | 0.15 | B. 15 cfm per person times the expected number of occupants.
|  | Churches & Chapels (Religious Worship) |  | 7 |  | 142.8571 | 1.0714 | 0.15 | For meeting the requirement in Section 120.1(b)2B for spaces without fixed seating, the expected
|  | Dance Floors |  | 5 |  | 200 | 1.5 | 1.15 | number of occupants shall be either the expected number specified by the building designer or one half
|  | Lobbies |  | 15 |  | 66.6667 | 0.5 | 2.15 | of the maximum occupant load assumed for egress purposes in the CBC, whichever is greater. For
|  | Lodge Rooms |  | 7 |  | 142.8571 | 1.0714 | 3.15 | spaces with fixed seating, the expected number of occupants shall be determined in accordance with the
|  | Reviewing Stands |  | 15 |  | 66.6667 | 0.5 | 4.15 | CBC.
|  | Stadiums |  | See Section 1004.7 |  |  |  | 0.15
|  | Theaters - All |  | See Section 1004.7 |  |  |  | 0.15
|  | Waiting Areas |  | 15 |  | 66.6667 | 0.5 | 4.15
4) | Assembly Areas (Nonconcentrated Use) |  |  | 15 |  | 66.6667 | 0.5 | 4.15
|  | Conference & Meeting Rooms 1 |  | 15 |  | 66.6667 | 0.5 | 4.15
|  | Dining Rooms/Areas |  | 15 |  | 66.6667 | 0.5 | 4.15
|  | Drinking Establishments 2 |  | 15 |  | 66.6667 | 0.5 | 4.15
|  | Exhibit/Display Areas |  | 15 |  | 66.6667 | 0.5 | 4.15
|  | Gymnasiums/Sports Arenas |  | 15 |  | 66.6667 | 0.5 | 4.15
|  | Lounges |  | 15 |  | 66.6667 | 0.5 | 4.15
|  | Stages |  | 15 |  | 66.6667 | 0.5 | 4.15
|  | Gaming, Keno, Slot Machine and Live Games Areas |  | 11 |  | 90.9091 | 0.68182 | 4.15
5) | Auto Repair Workshops |  |  | 100 |  | 10 | 0.075 | 4.15
6) | Barber & Beauty Shops |  |  | 100 |  | 10 | 0.075 | 4.15
7) | Children's Homes & Homes for Aged |  |  | 120 |  | 8.3333 | 0.0625 | 4.15
8) | Classrooms |  |  | 20 |  | 50 | 0.375 | 4.15
9) | Courtrooms |  |  | 40 |  | 25 | 0.1875 | 4.15
10) | Dormitories |  |  | 50 |  | 20 | 0.15 | 4.15
11) | Dry Cleaning (Coin-Operated) |  |  | 100 |  | 10 | 0.075 | 4.15
12) | Dry Cleaning (Commercial) |  |  | 100 |  | 10 | 0.075 | 4.15
13) | Garage, Parking |  |  | 200 |  | 5 | 0.0375 | 4.15
14) | Healthcare Facilities: |  | Sleeping Rooms | 120 |  | 8.3333 | 0.0625 | 4.15
|  |  | Treatment Rooms | 240 |  | 4.1667 | 0.03125 | 4.15
15) | Hotels and Apartments |  |  | 200 |  | 5 | 0.0375 | 4.15
|  |  | Hotel Function Area 3 | 7 |  | 142.8571 | 1.0714 | 4.15
|  |  | Hotel Lobby | 100 |  | 10 | 0.075 | 4.15
|  |  | Hotel Guest Rooms (<500 ft²) | 200 |  | 5 | 0.04 | Footnote 4
|  |  | Hotel Guest rooms (>=500 ft²) | 200 |  | 5 | 0.0375 | 4.15
| Occupancy |  | Use | CBC Occupancy Load (ft²/occ) |  | CBC Occupancy Load | CBC Based Ventilation (cfm/ft²)7 | Ventilation from Table 121-A (cfm/ft²)
(occ/1000 ft²)6
|  |  | Highrise Residential | 200 |  | 5 | 0.04 | Footnote 5
16) | Kitchen(s) |  |  | 200 |  | 5 | 0.0375 | 4.15
17) | Library: |  | Reading Rooms | 50 |  | 20 | 0.15 | 4.15
|  |  | Stack Areas | 100 |  | 10 | 0.075 | 4.15
18) | Locker Rooms |  |  | 50 |  | 20 | 0.15 | 4.15
19) | Manufacturing |  |  | 200 |  | 5 | 0.0375 | 4.15
20) | Mechanical Equipment Room |  |  | 300 |  | 3.3333 | 0.025 | 4.15
21) | Nurseries for Children - Day Care |  |  | 35 |  | 28.5714 | 0.21429 | 4.15
22) | Offices: |  | Office | 100 |  | 10 | 0.075 | 4.15
|  |  | Bank/Financial Institution | 100 |  | 10 | 0.075 | 4.15
|  |  | Medical & Clinical Care | 100 |  | 10 | 0.075 | 4.15
23) | Retail Stores (See Stores)
24) | School Shops & Vocational Rooms |  |  | 50 |  | 20 | 0.15 | 4.15
25) | Skating Rinks: |  | Skate Area | 50 |  | 20 | 0.15 | 4.15
|  |  | On Deck | 15 |  | 66.6667 | 0.5 | 4.15
26) | Stores: |  | Retail Sales, Wholesale Showrooms | 30 |  | 33.3333 | 0.25 | 4.15
|  |  | Basement and Ground Floor | 30 |  | 33.3333 | 0.25 | 4.15
|  |  | Upper Floors | 60 |  | 16.6667 | 0.125 | 4.15
|  |  | Grocery | 30 |  | 33.3333 | 0.25 | 4.15
|  |  | Malls, Arcades, & Atria | 30 |  | 33.3333 | 0.25 | 4.15
27) | Swimming Pools: |  | Pool Area | 50 |  | 20 | 0.15 | 4.15
|  |  | On Deck | 15 |  | 66.6667 | 0.5 | 4.15
28) | Warehouses, Industrial & Commercial Storage/Stockrooms |  |  | 500 |  | 2 | 0.015 | 4.15
29) | All Others -- Including Unknown |  |  | 100 |  | 10 | 0.075 | 4.15
|  |  | Corridors, Restrooms, & Support Areas | 100 |  | 10 | 0.075 | 4.15
|  |  | Commercial & Industrial Work | 100 |  | 10 | 0.075 | 4.15
Footnotes: |  |  |  |  | Equations used to find:
1. Convention, Conference, Meeting Rooms
2. Bars, Cocktail & Smoking Lounges, Casinos
3. See Conference Rooms or Dining Rooms
4. Guestrooms less than 500 ft² use 30 cfm/guestroom
5. Highrise Residential See 1994 UBC Section 1203 Ventilation

## Comparison (hidden)
2013 NACM Space Type | COMNET People | Notes | CBC People | Egress Occupancy Multiplier | CBC Adj Occupancy | Matching CBC Space Function | Recommended Occupancy | FINAL Occupancy | 2008 occupancy usable | occ based ventilation | Table 120.1 A over-rider | min ventilation from (floor & col.L) | CBC allottment | calc cbc density | All ppl
| # per 1000 ft² |  | # per 1000 ft² |  |  |  | # per 1000 ft²
Auditorium Area (Note 10) | 143 |  | n/a | 1 | 999 | n/a | 143 |  | 143 | 2.145 |  | 2.145 | 7 | 142.8571 | 143
Auto Repair Area | 10 |  | 10 | 0.5 | 5 | Auto Repair | 5 |  | 10 | 0.075 | 1.5 | 1.5 | 100 | 10 | 10
Bar, Cocktail Lounge and Casino Areas (Note 10) | 67 |  | 67 | 0.5 | 33.5 | Drinking Establishments | 33.5 |  | 67 | 0.5025 | 0.2 | 0.5025 | 15 | 66.6667 | 67
Beauty Salon Area | 10 |  | 10 | 0.5 | 5 | Barber & Beauty Shops | 5 |  | 10 | 0.075 | 0.4 | 0.4 | 100 | 10 | 10
Classrooms, Lecture, Training, Vocational Areas | 50 |  | 50 | 0.5 | 25 | Classrooms | 25 |  | 50 | 0.375 |  | 0.375 | 20 | 50 | 50
Civic Meeting Place Area (Note 10) | 25 |  | 67 | 0.5 | 33.5 | Lobbies | 33.5 |  | 25 | 0.1875 |  | 0.1875 | 40 | 25 | 67
Commercial and Industrial Storage Areas (conditioned or unconditioned) | 3 |  | 2 | 0.5 | 1 | Warehouses, Industrial & Commercial Storage/Stockrooms | 1 |  | 3 | 0.0225 |  | 0.15 | 300 | 3.3333 | 3
Commercial and Industrial Storage Areas (refrigerated) | 0 |  | n/a |  | 999 |  | 0 |  | 1 | 0 |  | 0.15 | 500 | 2 | 0
Computer Room (Note 11) | 3 | SpcFunc only valid if user-input receptacle load is >= 20W/ft2 | n/a |  | 999 |  | 3 |  | 20 | 0 |  | 0.15 | 50 | 20 | 3
Convention, Conference, Multipurpose and Meeting Center Areas (Note 10) | 67 |  | 67 | 0.5 | 33.5 | Assembly Areas (Nonconcentrated Use) | 33.5 |  | 67 | 0.5025 |  | 0.5025 | 15 | 66.6667 | 67
Corridors, Restrooms, Stairs, and Support Areas | 10 |  | n/a |  | 999 |  | 10 |  | 10 | 0 |  | 0.15 |  |  | 10
Dining Area (Note 10) | 67 |  | n/a |  | 999 |  | 67 |  | 67 | 0 |  | 0.15 | 15 | 66.6667 | 67
Dry Cleaning (Coin Operated) | 10 |  | 10 | 0.5 | 5 | Dry Cleaning (Coin-Operated) | 5 |  | 10 | 0.075 | 0.3 | 0.3 | 100 | 10 | 10
Dry Cleaning (Full Service Commercial) | 10 |  | 10 | 0.5 | 5 | Dry Cleaning (Commercial) | 5 |  | 10 | 0.075 | 0.45 | 0.45 | 100 | 10 | 10
Electrical, Mechanical, Telephone Rooms | 3 |  | 3 | 0.5 | 1.5 | Mechanical Equipment Room | 1.5 |  | 3 | 0.0225 |  | 0.15 | 300 | 3.3333 | 3
Exercise Center, Gymnasium Areas | 67 |  | 67 | 0.5 | 33.5 | Gymnasiums/Sports Arenas | 33.5 |  | 20 | 0.15 |  | 0.15 | 50 | 20 | 67
Exhibit, Museum Areas (Note 10) | 67 |  | 67 | 0.5 | 33.5 | Exhibit/Display Areas | 33.5 |  | 67 | 0.5025 |  | 0.5025 | 15 | 66.6667 | 67
Financial Transaction Area | 10 |  | 10 | 0.5 | 5 | Bank/Financial Institution | 5 |  | 10 | 0.075 |  | 0.15 | 100 | 10 | 10
General Commercial and Industrial Work Areas, High Bay | 10 |  | 5 | 0.5 | 2.5 | Manufacturing | 2.5 |  | 10 | 0.075 |  | 0.15 | 100 | 10 | 10
General Commercial and Industrial Work Areas, Low Bay | 10 |  | 5 | 0.5 | 2.5 | Manufacturing | 2.5 |  | 10 | 0.075 |  | 0.15 | 100 | 10 | 10
General Commercial and Industrial Work Areas, Precision | 10 |  | 5 | 0.5 | 2.5 | Manufacturing | 2.5 |  | 10 | 0.075 |  | 0.15 | 100 | 10 | 10
Grocery Sales Areas (Note 10) | 33 |  | 33 | 0.5 | 16.5 | Grocery | 16.5 |  | 33 | 0.2475 | 0.2 | 0.2475 |  |  | 33
High-Rise Residential Living Spaces (Note 9) | 5 |  | 5 | 1 | 5 | Hotel Guestrooms | 5 |  | 5 | 0.075 | see special note | 0.15 | 200 | 5 | 5
Hotel Function Area (Note 10) | 67 |  | 143 | 0.5 | 71.5 | Hotel Function Area | 71.5 |  | 67 | 0.5025 |  | 0.5025 |  |  | 143
Hotel/Motel Guest Room (Note 9) | 5 |  | 5 | 1 | 5 | Hotel Guestrooms | 5 |  | 5 | 0.075 | see note | 0.15 | 200 | 5 | 5
Housing, Public and Common Areas: Multi-family, Dormitory | 10 |  | 20 | 0.5 | 10 | Dormitories | 10 |  | 10 | 0.075 |  | 0.15 |  |  | 20
Housing, Public and Common Areas: Senior Housing | 10 |  | 8 | 1 | 8 | Children's Homes & Homes for Aged | 8 |  | 10 | 0.15 |  | 0.15 |  |  | 10
Kitchen, Commercial Food Preparation | 5 | GasEquipPwr only valid if hood length > 0. If there is an exhaust hood, set convective fraction to 0 | 5 | 0.5 | 2.5 | Kitchen(s) | 2.5 |  | 5 | 0.0375 |  | 0.15 | 200 | 5 | 5
Kitchenette or Residential Kitchen | 5 |  | 5 | 0.5 | 2.5 | Kitchen(s) | 2.5 |  | 5 | 0.0375 |  | 0.15 | 200 | 5 | 5
Laboratory, Scientific | 10 |  | n/a |  | 999 |  | 10 |  | 10 | 0 | 0.38 | 0.15 | 100 | 10 | 10
Laboratory, Equipment Room | 5 |  | n/a |  | 999 |  | 5 |  | 5 | 0 |  | 0.15 | 200 | 5 | 5
Laundry | 10 |  | n/a |  | 999 |  | 10 |  | 10 | 0 |  | 0.15 | 100 | 10 | 10
Library, Reading Areas | 20 |  | 20 | 0.5 | 10 | Library, Reading Areas | 10 |  | 20 | 0.15 |  | 0.15 | 50 | 20 | 20
Library, Stacks | 10 |  | 10 | 0.5 | 5 | Library, Stacks | 5 |  | 10 | 0.075 |  | 0.15 | 100 | 10 | 10
Lobby, Hotel | 10 |  | 67 | 0.5 | 33.5 | Assembly Areas (Concentrated Use), Lobbies | 33.5 |  | 10 | 0.075 |  | 0.15 | 100 | 10 | 67
Lobby, Main Entry | 10 |  | 67 | 0.5 | 33.5 |  | 33.5 |  | 10 | 0.075 |  | 0.15 | 100 | 10 | 67
Locker/Dressing Room | 20 |  | 20 | 0.5 | 10 | Locker Rooms | 10 |  | 20 | 0.15 |  | 0.15 | 50 | 20 | 20
Lounge, Recreation (Note 10) | 67 |  | 67 | 0.5 | 33.5 | Assembly Areas (Nonconcentrated Use), Lounges | 33.5 |  | 67 | 0.5025 |  | 0.5025 | 15 | 66.6667 | 67
Malls and Atria (Note 10) | 33 |  | 33.3333 | 0.5 | 16.6667 | Stores: Malls, Arcades, & Atria | 16.7 |  | 33 | 0.2475 |  | 0.2475 | 30 | 33.3333 | 33.3333
Medical and Clinical Care | 10 |  | 10 | 0.5 | 5 | Office: Medical and Clinical Care | 5 |  | 10 | 0.075 |  | 0.15 | 100 | 10 | 10
Office (Greater than 250 square feet in floor area) | 10 |  | 10 | 0.5 | 5 | Office | 5 |  | 10 | 0.075 |  | 0.15 | 100 | 10 | 10
Office (250 square feet in floor area or less) | 10 |  | 10 | 0.5 | 5 | Office | 5 |  | 10 | 0.075 |  | 0.15 | 100 | 10 | 10
Parking Garage Building, Parking Area | 10 |  | 5 | 0.5 | 2.5 | Garage, Parking | 2.5 |  | 5 | 0.0375 |  | 0.15 | 200 | 5 | 10
Parking Garage Area Dedicated Ramps | 10 |  | 5 | 0.5 | 2.5 | Garage, Parking | 2.5 |  | 5 | 0.0375 |  | 0.15 | 200 | 5 | 10
Parking Garage Area Daylight Adaptation Zones | 10 |  | 5 | 0.5 | 2.5 | Garage, Parking | 2.5 |  | 5 | 0.0375 |  | 0.15 | 200 | 5 | 10
Police Station and Fire Station | 10 |  | n/a |  | 999 |  | 10 |  | 10 | 0 |  | 0.15 | 100 | 10 | 10
Religious Worship Area (Note 10) | 143 |  | 143 | 1 | 143 | Churches & Chapels (Religious Worship) | 143 |  | 143 | 2.145 |  | 2.145 | 7 | 142.8571 | 143
Retail Merchandise Sales, Wholesale Showroom (Note 10) | 33 |  | 33 | 0.5 | 16.5 | Retail Sales, Wholesale Showrooms | 16.5 |  | 33 | 0.2475 | 0.2 | 0.2475 | 30 | 33.3333 | 33
Sports Arena, Indoor Playing Area | 143 |  | 67 | 0.5 | 33.5 | Gymnasiums/Sports Arenas | 33.5 |  |  | 0 |  | 0.15 |  |  | 143
Theater, Motion Picture (Note 10) | 143 |  | n/a |  | 999 |  | 143 |  | 143 | 0 |  | 0.15 | 7 | 142.8571 | 143
Theater, Performance (Note 10) | 143 |  | n/a |  | 999 |  | 143 |  | 143 | 0 |  | 0.15 | 7 | 142.8571 | 143
Transportation Function (Note 10) | 33 |  | n/a |  | 999 |  | 33 |  | 33 | 0 |  | 0.15 |  |  | 33
Unoccupied-Exclude from Gross Floor Area | 0 |  | n/a |  | 999 |  | 0 |  |  | 0 |  | 0.15 |  |  | 0
Unoccupied-Include in Gross Floor Area | 0 |  | n/a |  | 999 |  | 0 |  |  | 0 |  | 0.15 |  |  | 0
Videoconferencing Studio (Note S1) | 10 |  | n/a |  | 999 |  | 10 |  |  | 0 |  | 0.15 |  |  | 10
Waiting Area | 10 |  | ??? |  |  |  | 10 |  | 10 | 0 |  | 0.15 |  |  | 10
All Others (including unleased tenant space in multi-tenant facilities) | 10 | [5 empty] | 10 |  | 10 | 0 |  | 0.15 |  |  | 10

## 2019 Ventilation List (hidden)
Table 120.1-A - Minimum Ventilation Rates
| Occupancy Category | Area Outdoor Air Rate Ra | Min Air Rate for DCVb | Air Class | Notes
|  | cfm/ft2 | cfm/ft2
Educational Facilities
| Daycare (through age 4) | 0.21 | 0.15 | 2
| Daycare sickroom | 0.15 |  | 3
| Classrooms (ages 5-8) | 0.38 | 0.15 | 1
| Classrooms (ages 9-18) | 0.38 | 0.15 | 1
| Lecture/postsecondary classroom | 0.38 | 0.15 | 1 | F
| Lecture hall (fixed seats) | - |  | 1 | F
| Art classroom | 0.15 |  | 2
| Science laboratories | 0.15 |  | 2
| University/college laboratories | 0.15 |  | 2
| Wood/metal shop | 0.15 |  | 2
| Computer lab | 0.15 |  | 1
| Media center | 0.15 |  | 1 | A
| Music/theater/dance | 1.07* | 0.15 | 1 | F
| Multiuse assembly | 0.5 | 0.15 | 1 | F
Food and Beverage Service
| Restaurant dining rooms | 0.5 | 0.15 | 2
| Cafeteria/fast-food dining | 0.5 | 0.15 | 2
| Bars, cocktail lounges | 0.5 | 0.2 | 2
| Kitchen (cooking) | 0.15 |  | 2
General
| Break rooms | 0.5 | 0.15 | 1 | F
| Coffee Stations | 0.5 | 0.15 | 1 | F
| Conference/meeting | 0.5 | 0.15 | 1 | F
| Corridors | 0.15 |  | 1 | F
| Occupiable storage rooms for liquids or gels | 0.15 |  | 2 | B
Hotels, Motels, Resorts, Dormitories
| Bedroom/living room | 0.15 |  | 1 | F
| Barracks sleeping areas | 0.15 |  | 1 | F
| Laundry rooms, central | 0.15 |  | 2
| Laundry rooms within dwelling units | 0.15 |  | 1
| Lobbies/pre-function | 0.5 | 0.15 | 1 | F
| Multipurpose assembly | 0.5 |  | 1 | F
Office Buildings
| Breakrooms | 0.5 | 0.15 | 1
| Main entry lobbies | 0.5 | 0.15 | 1 | F
| Occupiable storage rooms for dry materials | 0.15 |  | 1
| Office space | 0.15 |  | 1 | F
| Reception areas | 0.15 |  | 1 | F
| Telephone/data entry | 0.15 |  | 1 | F
Miscellaneous Spaces
| Bank vaults/safe deposit | 0.15 |  | 2 | F
| Banks or bank lobbies | 0.15 |  | 1 | F
| Computer (not printing) | 0.15 |  | 1 | F
| Freezer and refrigerated spaces (<50oF) | - |  | 2 | E
| General manufacturing (excludes heavy industrial and process using chemicals) | 0.15 |  | 3
| Pharmacy (preparation area) | 0.15 |  | 2
| Photo studios | 0.15 |  | 1
| Shipping/receiving | 0.15 |  | 2 | B
| Sorting, packing, light assembly | 0.15 |  | 2
| Telephone closets | 0.15 |  | 1
| Transportation waiting | 0.5 | 0.15 | 1 | F
| Warehouses | 0.15 |  | 2 | B
| All others | 0.15 |  | 2
Public Assembly Spaces
| Auditorium seating area | 1.07a | 0.15 | 1 | F
| Places of religious worship | 1.07a | 0.15 | 1 | F
| Courtrooms | 0.19a | 0.15 | 1 | F
| Legislative chambers | 0.19a | 0.15 | 1 | F
| Libraries (reading rooms and stack areas) | 0.15 |  | 1
| Lobbies | 0.5 | 0.15 | 1 | F
| Museums (childrens) | 0.25 | 0.15 | 1
| Museums/galleries | 0.25 | 0.15 | 1 | F
Residential
| Common corridors | 0.15 |  | 1 | F
Retail
| Sales (except as below) | 0.25 | 0.2 | 2
| Mall common areas | 0.25 | 0.15 | 1 | F
| Barbershop | 0.4 |  | 2 | F
| Beauty and nail salons | 0.4 |  | 2
| Pet shops (animal areas) | 0.25 | 0.15 | 2
| Supermarket | 0.25 | 0.2 | 1 | F
| Coin-operated laundries | 0.3 |  | 2
Sports and Entertainment
| Gym, sports arena (play area) | 0.5 | 0.15 | 2 | E
| Spectator areas | 0.5 | 0.15 | 1 | F
| Swimming (pool) | 0.15 |  | 2 | C
| Swimming (deck) | 0.5 | 0.15 | 2 | C
| Disco/dance floors | 1.5 | 0.15 | 2 | F
| Health club/aerobics room | 0.15 |  | 2
| Health club/weight rooms | 0.15 |  | 2
| Bowling alley (seating) | 1.07 | 0.15 | 1
| Gambling casinos | 0.68 | 0.15 | 1
| Game arcades | 0.68 | 0.15 | 1
| Stages, studios | 0.5 | 0.15 | 1 | D, F
General:
a This value assumes non-fixed seating and uses the occupant density assumption in accordance with Section 120.1(c)3.
bIf this column specifies a minimum cfm/ft2 then it shall be used to comply with Section 120.1(d)4E.
Specific Notes:
A - For high-school and college libraries, the values shown for “Public Assembly Spaces - Libraries” shall be used.
B - Rate may not be sufficient where stored materials include those having potentially harmful emissions.
C - Rate does not allow for humidity control. “Deck area” refers to the area surrounding the pool that is capable of being wetted during pool use or when the pool is occupied. Deck area that is not expected to be wetted shall be designated as an occupancy category.
D - Rate does not include special exhaust for stage effects such as dry ice vapors and smoke.
E - Where combustion equipment is intended to be used on the playing surface or in the space, additional dilution ventilation source control, or both shall be provided.
F - Ventilation air for this occupancy category shall be permitted to be reduced to zero when the space is in occupied-standby mode
Table 120.1-B - Minimum Exhaust Rates
[ASHRAE 62.1: TABLE 6.5]
| Occupancy Category | Exhaust Rete, | Exhaust Rate, | Air Class | Notes
|  | cfm/unit | cfm/ft2
| Arenas | - | 0.5 | 1 | B
| Art classrooms | - | 0.7 | 2
| Auto repair rooms | - | 1.5 | 2 | A
| Barber shops | - | 0.5 | 2
| Beauty and nail salons | - | 0.6 | 2
| Cells with toilet | - | 1 | 2
| Copy, printing rooms | - | 0.5 | 2
| Darkrooms | - | 1 | 2
| Educational science laboratories | - | 1 | 2
| Janitor closets, trash rooms, recycling | - | 1 | 3
| Kitchenettes | - | 0.3 | 2
| Kitchens - commercial | - | 0.7 | 2
| Locker rooms for athletic or industrial facilities | - | 0.5 | 2
| All other locker rooms | - | 0.25 | 2
| Shower rooms | 20/50 | - | 2 | G,H
| Paint spray booths | - | - | 4 | F
| Parking garages | - | 0.75 | 2 | C
| Pet shops (animal areas) | - | 0.9 | 2
| Refrigerating machinery rooms | - | - | 3 | F
| Soiled laundry storage rooms | - | 1 | 3 | F
| Storage rooms, chemical | - | 1.5 | 4 | F
| Toilets - private | 25/50 | - | 2 | E
| Toilets, public | 50/70 | - | 2 | D
| Woodwork shop/classrooms | - | 0.5 | 2
Notes:
A - Stands where engines are run shall have exhaust systems that directly connect to the engine exhaust and prevent escape of fumes.
B - Where combustion equipment is intended to be used on the playing surface, additional dilution ventilation, source control, or both shall be provided.
C - Exhaust shall not be required where two or more sides comprise walls that are at least 50% open to the outside.
D - Rate is per water closet, urinal, or both. Provide the higher rate where periods of heavy use are expected to occur. The lower rate shall be permitted to be used otherwise.
E - Rate is for a toilet room intended to be occupied by one person at a time. For continuous systems operation during hours of use, the lower rate shall be permitted to be used. Otherwise the higher rate shall be used.
F - See other applicable standards for exhaust rate.
G - For continuous system operation, the lower rate shall be permitted to be used. Otherwise the higher rate shall be used.
H - Rate is per showerhead
High-Rise Residential Mechanical Ventilation Rate (cfm) shall be Qfan:
Qfan = (0.15 cfm/ft² x Afloor) + (3.5 cfm/bedroom x (Nbr + 1)) - (Vdwellingunit x 2 ach / 60 min/hr x Aext)
where:
Afloor = dwelling unit floor area (ft²)
Nbr = Number of bedrooms
Vdwellingunit = dwelling unit volume (ft³)
Aext = fraction of dwelling unit perimeter wall and roof/ceiling exposed to the outdoors

## 2019 Ventilation List SORT (hidden)
Occupancy Category | Area Outdoor Air Rate Ra | Min Air Rate for DCVb | Continuous Exhaust Rate, | Intermittent Exhaust Rate, | Exhaust Rate, | Air Class | Notes | Baseline ventilation = proposed?
| cfm/ft² | cfm/ft² | cfm/unit | cfm/unit | cfm/ft²
Assembly - Auditorium seating area | 1.07 | 0.15 |  |  |  | 1 | F | No
Assembly - Courtrooms | 0.19 | 0.15 |  |  |  | 1 | F | No
Assembly - Legislative chambers | 0.19 | 0.15 |  |  |  | 1 | F | No
Assembly - Libraries (reading rooms and stack areas) | 0.15 | 0.15 |  |  |  | 1 |  | No
Assembly - Lobbies | 0.5 | 0.15 |  |  |  | 1 | F | No
Assembly - Museums (childrens) | 0.25 | 0.15 |  |  |  | 1 |  | No
Assembly - Museums/galleries | 0.25 | 0.15 |  |  |  | 1 | F | No
Assembly - Places of religious worship | 1.07 | 0.15 |  |  |  | 1 | F | No
Education - Art classroom | 0.15 | 0.15 |  |  | 0.7 | 2 |  | No
Education - Classrooms (ages 9-18) | 0.38 | 0.15 |  |  |  | 1 |  | No
Education - Classrooms (ages 5-8) | 0.38 | 0.15 |  |  |  | 1 |  | No
Education - Computer lab | 0.15 | 0.15 |  |  |  | 1 |  | No
Education - Daycare (through age 4) | 0.21 | 0.15 |  |  |  | 2 |  | No
Education - Daycare sickroom | 0.15 | 0.15 |  |  |  | 3 |  | No
Education - Lecture hall (fixed seats) |  | 0.15 |  |  |  | 1 | F | No
Education - Lecture/postsecondary classroom | 0.38 | 0.15 |  |  |  | 1 | F | No
Education - Media center | 0.15 | 0.15 |  |  |  | 1 | A | No
Education - Metal shop | 0.15 | 0.15 |  |  |  | 2 |  | No
Education - Multiuse assembly | 0.5 | 0.15 |  |  |  | 1 | F | No
Education - Music/theater/dance | 1.07 | 0.15 |  |  |  | 1 | F | No
Education - Science laboratories | 0.15 | 0.15 |  |  | 1 | 2 |  | Yes
Education - University/college laboratories | 0.15 | 0.15 |  |  | 1 | 2 |  | Yes
Education - Wood shop | 0.15 | 0.15 |  |  | 0.5 | 2 |  | No
Exhaust - All other locker rooms | 0 | 0 |  |  | 0.25 | 2 |  | No
Exhaust - Arenas | 0 | 0 |  |  | 0.5 | 1 | Exh. Note B | No
Exhaust - Auto repair rooms | 0 | 0 |  |  | 1.5 | 2 | Exh. Note A | No
Exhaust - Cells with toilet | 0 | 0 |  |  | 1 | 2 |  | No
Exhaust - Copy, printing rooms | 0 | 0 |  |  | 0.5 | 2 |  | No
Exhaust - Darkrooms | 0 | 0 |  |  | 1 | 2 |  | No
Exhaust - Janitor closets, trash rooms, recycling | 0 | 0 |  |  | 1 | 3 |  | No
Exhaust - Kitchenettes | 0 | 0 |  |  | 0.3 | 2 |  | No
Exhaust - Locker rooms for athletic or industrial facilities | 0 | 0 |  |  | 0.5 | 2 |  | No
Exhaust - Paint spray booths | 0 | 0 |  |  |  | 4 | Exh. Note F | No
Exhaust - Parking garages | 0 | 0 |  |  | 0.75 | 2 | Exh. Note C | Yes
Exhaust - Refrigerating machinery rooms | 0 | 0 |  |  |  | 3 | Exh. Note F | Yes
Exhaust - Shower rooms | 0 | 0 | 20 | 50 |  | 2 | Exh. Note G,H | No
Exhaust - Soiled laundry storage rooms | 0 | 0 |  |  | 1 | 3 | Exh. Note F | No
Exhaust - Storage rooms, chemical | 0 | 0 |  |  | 1.5 | 4 | Exh. Note F | Yes
Exhaust - Toilets, private | 0 | 0 | 25 | 50 |  | 2 | Exh. Note E | No
Exhaust - Toilets, public | 0 | 0 | 50 |  |  | 2 | Exh. Note D | No
Exhaust - Woodwork shop/classrooms | 0 | 0 |  |  | 0.5 | 2 |  | No
Food Service - Bars, cocktail lounges | 0.5 | 0.2 |  |  |  | 2 |  | No
Food Service - Cafeteria/fast-food dining | 0.5 | 0.15 |  |  |  | 2 |  | No
Food Service - Kitchen (cooking) | 0.15 | 0.15 |  |  | 0.7 | 2 |  | Yes
Food Service - Restaurant dining rooms | 0.5 | 0.15 |  |  |  | 2 |  | No
General - Break rooms | 0.5 | 0.15 |  |  |  | 1 | F | No
General - Coffee Stations | 0.5 | 0.15 |  |  |  | 1 | F | No
General - Conference/meeting | 0.5 | 0.15 |  |  |  | 1 | F | No
General - Corridors | 0.15 | 0.15 |  |  |  | 1 | F | No
General - Occupiable storage rooms for liquids or gels | 0.15 | 0.15 |  |  |  | 2 | B | Yes
General - Unoccupied | 0 | 0 |  |  |  | 1 |  | No
Lodging - Barracks sleeping areas | 0.15 | 0.15 |  |  |  | 1 | F | No
Lodging - Bedroom/living room | 0.15 | 0.15 |  |  |  | 1 | F | No
Lodging - Laundry rooms within dwelling units | 0.15 | 0.15 |  |  |  | 1 |  | No
Lodging - Laundry rooms, central | 0.15 | 0.15 |  |  |  | 2 |  | No
Lodging - Lobbies/pre-function | 0.5 | 0.15 |  |  |  | 1 | F | No
Lodging - Multipurpose assembly | 0.5 | 0.5 |  |  |  | 1 | F | No
Misc - All others | 0.15 | 0.15 |  |  |  | 2 |  | No
Misc - Bank vaults/safe deposit | 0.15 | 0.15 |  |  |  | 2 | F | No
Misc - Banks or bank lobbies | 0.15 | 0.15 |  |  |  | 1 | F | No
Misc - Computer (not printing) | 0.15 | 0.15 |  |  |  | 1 | F | Yes
Misc - Freezer and refrigerated spaces (<50F) | 0 | 0 |  |  |  | 2 | E | No
Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 0.15 | 0.15 |  |  |  | 3 |  | Yes
Misc - Pharmacy (preparation area) | 0.15 | 0.15 |  |  |  | 2 |  | No
Misc - Photo studios | 0.15 | 0.15 |  |  |  | 1 |  | No
Misc - Shipping/receiving | 0.15 | 0.15 |  |  |  | 2 | B | No
Misc - Sorting, packing, light assembly | 0.15 | 0.15 |  |  |  | 2 |  | No
Misc - Telephone closets | 0.15 | 0.15 |  |  |  | 1 |  | No
Misc - Transportation waiting | 0.5 | 0.15 |  |  |  | 1 | F | No
Misc - Warehouses | 0.15 | 0.15 |  |  |  | 2 | B | No
Office - Breakrooms | 0.5 | 0.15 |  |  |  | 1 |  | No
Office - Main entry lobbies | 0.5 | 0.15 |  |  |  | 1 | F | No
Office - Occupiable storage rooms for dry materials | 0.15 | 0.15 |  |  |  | 1 |  | No
Office - Office space | 0.15 | 0.15 |  |  |  | 1 | F | No
Office - Reception areas | 0.15 | 0.15 |  |  |  | 1 | F | No
Office - Telephone/data entry | 0.15 | 0.15 |  |  |  | 1 | F | No
Residential - Common corridors | 0.15 | 0.15 |  |  |  | 1 | F | No
Retail - Barbershop | 0.4 | 0.4 |  |  | 0.5 | 2 | F | No
Retail - Beauty and nail salons | 0.4 | 0.4 |  |  | 0.6 | 2 |  | No
Retail - Coin-operated laundries | 0.3 | 0.3 |  |  |  | 2 |  | No
Retail - Mall common areas | 0.25 | 0.15 |  |  |  | 1 | F | No
Retail - Pet shops (animal areas) | 0.25 | 0.15 |  |  | 0.9 | 2 |  | No
Retail - Sales | 0.25 | 0.2 |  |  |  | 2 |  | No
Retail - Supermarket | 0.25 | 0.2 |  |  |  | 1 | F | No
Sports/Entertainment - Bowling alley (seating) | 1.07 | 0.15 |  |  |  | 1 |  | No
Sports/Entertainment - Disco/dance floors | 1.5 | 0.15 |  |  |  | 2 | F | No
Sports/Entertainment - Gambling casinos | 0.68 | 0.15 |  |  |  | 1 |  | No
Sports/Entertainment - Game arcades | 0.68 | 0.15 |  |  |  | 1 |  | No
Sports/Entertainment - Gym, sports arena (play area) | 0.5 | 0.15 |  |  |  | 2 | E | No
Sports/Entertainment - Health club/aerobics room | 0.15 | 0.15 |  |  |  | 2 |  | No
Sports/Entertainment - Health club/weight rooms | 0.15 | 0.15 |  |  |  | 2 |  | No
Sports/Entertainment - Spectator areas | 0.5 | 0.15 |  |  |  | 1 | F | No
Sports/Entertainment - Stages, studios | 0.5 | 0.15 |  |  |  | 1 | D, F | No
Sports/Entertainment - Swimming (deck) | 0.5 | 0.15 |  |  |  | 2 | C | No
Sports/Entertainment - Swimming (pool) | 0.15 | 0.15 |  |  |  | 2 | C | No
Sports/Entertainment - Swimming (pool) | 0 | 0 | [5 empty] | No
NA | 0 | 0 |  |  |  | 0 | 0 | Yes
High-Rise Residential Mechanical Ventilation Rate (cfm) shall be Qfan:
Qfan = (0.15 cfm/ft² x Afloor) + (3.5 cfm/bedroom x (Nbr + 1)) - (Vdwellingunit x 2 ach / 60 min/hr x Aext)
where:
Afloor = dwelling unit floor area (ft²)
Nbr = Number of bedrooms
Vdwellingunit = dwelling unit volume (ft³)
Aext = fraction of dwelling unit perimeter wall and roof/ceiling exposed to the outdoors

## 2022 Ventilation List (hidden)
Table 120.1-A - Minimum Ventilation Rates
| Occupancy Category | Total Outdoor Air Rate R | Min Ventilation Air Rate for DCVb | Air Class | Notes
|  | cfm/ft2 | cfm/ft2
Educational Facilities
| Daycare (through age 4) | 0.21 | 0.15 | 2
| Daycare sickroom | 0.15 |  | 3
| Classrooms (ages 5-8) | 0.38 | 0.15 | 1
| Classrooms (ages 9-18) | 0.38 | 0.15 | 1
| Lecture/postsecondary classroom | 0.38 | 0.15 | 1 | F
| Lecture hall (fixed seats) | - |  | 1 | F
| Art classroom | 0.15 |  | 2
| Science laboratories | 0.15 |  | 2
| University/college laboratories | 0.15 |  | 2
| Wood/metal shop | 0.15 |  | 2
| Computer lab | 0.15 |  | 1
| Media center | 0.15 |  | 1 | A
| Music/theater/dance | 1.07* | 0.15 | 1 | F
| Multiuse assembly | 0.5 | 0.15 | 1 | F
Food and Beverage Service
| Restaurant dining rooms | 0.5 | 0.15 | 2
| Cafeteria/fast-food dining | 0.5 | 0.15 | 2
| Bars, cocktail lounges | 0.5 | 0.2 | 2
| Kitchen (cooking) | 0.15 |  | 2
General
| Break rooms | 0.5 | 0.15 | 1 | F
| Coffee Stations | 0.5 | 0.15 | 1 | F
| Conference/meeting | 0.5 | 0.15 | 1 | F
| Corridors | 0.15 |  | 1 | F
| Occupiable storage rooms for liquids or gels | 0.15 |  | 2 | B
Hotels, Motels, Resorts, Dormitories
| Bedroom/living room | 0.15 |  | 1 | F
| Barracks sleeping areas | 0.15 |  | 1 | F
| Laundry rooms, central | 0.15 |  | 2
| Laundry rooms within dwelling units | 0.15 |  | 1
| Lobbies/pre-function | 0.5 | 0.15 | 1 | F
| Multipurpose assembly | 0.5 |  | 1 | F
Office Buildings
| Breakrooms | 0.5 | 0.15 | 1
| Main entry lobbies | 0.5 | 0.15 | 1 | F
| Occupiable storage rooms for dry materials | 0.15 |  | 1
| Office space | 0.15 |  | 1 | F
| Reception areas | 0.15 |  | 1 | F
| Telephone/data entry | 0.15 |  | 1 | F
Miscellaneous Spaces
| Bank vaults/safe deposit | 0.15 |  | 2 | F
| Banks or bank lobbies | 0.15 |  | 1 | F
| Computer (not printing) | 0.15 |  | 1 | F
| Freezer and refrigerated spaces (<50oF) | - |  | 2 | E
| General manufacturing (excludes heavy industrial and process using chemicals) | 0.15 |  | 3
| Pharmacy (preparation area) | 0.15 |  | 2
| Photo studios | 0.15 |  | 1
| Shipping/receiving | 0.15 |  | 2 | B
| Sorting, packing, light assembly | 0.15 |  | 2
| Telephone closets | 0.15 |  | 1
| Transportation waiting | 0.5 | 0.15 | 1 | F
| Warehouses | 0.15 |  | 2 | B
| All others | 0.15 |  | 2
Public Assembly Spaces
| Auditorium seating area | 1.07a | 0.15 | 1 | F
| Places of religious worship | 1.07a | 0.15 | 1 | F
| Courtrooms | 0.19a | 0.15 | 1 | F
| Legislative chambers | 0.19a | 0.15 | 1 | F
| Libraries (reading rooms and stack areas) | 0.15 |  | 1
| Lobbies | 0.5 | 0.15 | 1 | F
| Museums (childrens) | 0.25 | 0.15 | 1
| Museums/galleries | 0.25 | 0.15 | 1 | F
Residential
| Common corridors | 0.15 |  | 1 | F
Retail
| Sales (except as below) | 0.25 | 0.2 | 2
| Mall common areas | 0.25 | 0.15 | 1 | F
| Barbershop | 0.4 |  | 2 | F
| Beauty and nail salons | 0.4 |  | 2
| Pet shops (animal areas) | 0.25 | 0.15 | 2
| Supermarket | 0.25 | 0.2 | 1 | F
| Coin-operated laundries | 0.3 |  | 2
Sports and Entertainment
| Gym, sports arena (play area) | 0.5 | 0.15 | 2 | E
| Spectator areas | 0.5 | 0.15 | 1 | F
| Swimming (pool) | 0.15 |  | 2 | C
| Swimming (deck) | 0.5 | 0.15 | 2 | C
| Disco/dance floors | 1.5 | 0.15 | 2 | F
| Health club/aerobics room | 0.15 |  | 2
| Health club/weight rooms | 0.15 |  | 2
| Bowling alley (seating) | 1.07 | 0.15 | 1
| Gambling casinos | 0.68 | 0.15 | 1
| Game arcades | 0.68 | 0.15 | 1
| Stages, studios | 0.5 | 0.15 | 1 | D, F
General:
a This value assumes non-fixed seating and uses the occupant density assumption in accordance with Section 120.1(c)3.
bIf this column specifies a minimum cfm/ft2 then it shall be used to comply with Section 120.1(d)4E.
Specific Notes:
A - For high-school and college libraries, the values shown for “Public Assembly Spaces - Libraries” shall be used.
B - Rate may not be sufficient where stored materials include those having potentially harmful emissions.
C - Rate does not allow for humidity control. “Deck area” refers to the area surrounding the pool that is capable of being wetted during pool use or when the pool is occupied. Deck area that is not expected to be wetted shall be designated as an occupancy category.
D - Rate does not include special exhaust for stage effects such as dry ice vapors and smoke.
E - Where combustion equipment is intended to be used on the playing surface or in the space, additional dilution ventilation source control, or both shall be provided.
F - Ventilation air for this occupancy category shall be permitted to be reduced to zero when the space is in occupied-standby mode
Table 120.1-B - Minimum Exhaust Rates
[ASHRAE 62.1: TABLE 6.5]
| Occupancy Category | Exhaust Rete, | Exhaust Rate, | Air Class | Notes
|  | cfm/unit | cfm/ft2
| Arenas | - | 0.5 | 1 | B
| Art classrooms | - | 0.7 | 2
| Auto repair rooms | - | 1.5 | 2 | A
| Barber shops | - | 0.5 | 2
| Beauty and nail salons | - | 0.6 | 2
| Cells with toilet | - | 1 | 2
| Copy, printing rooms | - | 0.5 | 2
| Darkrooms | - | 1 | 2
| Educational science laboratories | - | 1 | 2
| Janitor closets, trash rooms, recycling | - | 1 | 3
| Kitchenettes | - | 0.3 | 2
| Kitchens - commercial | - | 0.7 | 2
| Locker rooms for athletic or industrial facilities | - | 0.5 | 2
| All other locker rooms | - | 0.25 | 2
| Shower rooms | 20/50 | - | 2 | G,H
| Paint spray booths | - | - | 4 | F
| Parking garages | - | 0.75 | 2 | C
| Pet shops (animal areas) | - | 0.9 | 2
| Refrigerating machinery rooms | - | - | 3 | F
| Soiled laundry storage rooms | - | 1 | 3 | F
| Storage rooms, chemical | - | 1.5 | 4 | F
| Toilets - private | 25/50 | - | 2 | E
| Toilets, public | 50/70 | - | 2 | D
| Woodwork shop/classrooms | - | 0.5 | 2
Notes:
A - Stands where engines are run shall have exhaust systems that directly connect to the engine exhaust and prevent escape of fumes.
B - Where combustion equipment is intended to be used on the playing surface, additional dilution ventilation, source control, or both shall be provided.
C - Exhaust shall not be required where two or more sides comprise walls that are at least 50% open to the outside.
D - Rate is per water closet, urinal, or both. Provide the higher rate where periods of heavy use are expected to occur. The lower rate shall be permitted to be used otherwise.
E - Rate is for a toilet room intended to be occupied by one person at a time. For continuous systems operation during hours of use, the lower rate shall be permitted to be used. Otherwise the higher rate shall be used.
F - See other applicable standards for exhaust rate.
G - For continuous system operation, the lower rate shall be permitted to be used. Otherwise the higher rate shall be used.
H - Rate is per showerhead
High-Rise Residential Mechanical Ventilation Rate (cfm) shall be Qfan:
Qfan = (0.15 cfm/ft² x Afloor) + (3.5 cfm/bedroom x (Nbr + 1)) - (Vdwellingunit x 2 ach / 60 min/hr x Aext)
where:
Afloor = dwelling unit floor area (ft²)
Nbr = Number of bedrooms
Vdwellingunit = dwelling unit volume (ft³)
Aext = fraction of dwelling unit perimeter wall and roof/ceiling exposed to the outdoors

## 2022 Ventilation List SORT (hidden)
|  | Why Air Rate for DCV in 2019 are all filled even if = 0 in the code table? | [6 empty] | Real values in the table
Occupancy Category | Area Outdoor Air Rate Ra | Min Air Rate for DCVb | Continuous Exhaust Rate, | Intermittent Exhaust Rate, | Exhaust Rate, | Air Class | Notes | Baseline ventilation = proposed? | Min Air Rate for DCVb
| cfm/ft² | cfm/ft² | cfm/unit | cfm/unit | cfm/ft²
Assembly - Auditorium seating area | 1.07 | 0.15 |  |  |  | 1 | F | No | 0.15
Assembly - Courtrooms | 0.19 | 0.15 |  |  |  | 1 | F | No | 0.15
Assembly - Legislative chambers | 0.19 | 0.15 |  |  |  | 1 | F | No | 0.15
Assembly - Libraries (reading rooms and stack areas) | 0.15 | 0.15 |  |  |  | 1 |  | No
Assembly - Lobbies | 0.5 | 0.15 |  |  |  | 1 | F | No | 0.15
Assembly - Museums (childrens) | 0.25 | 0.15 |  |  |  | 1 |  | No | 0.15
Assembly - Museums/galleries | 0.25 | 0.15 |  |  |  | 1 | F | No | 0.15
Assembly - Places of religious worship | 1.07 | 0.15 |  |  |  | 1 | F | No | 0.15
Education - Art classroom | 0.15 | 0.15 |  |  | 0.7 | 2 |  | No
Education - Classrooms (ages 9-18) | 0.38 | 0.15 |  |  |  | 1 |  | No | 0.15
Education - Classrooms (ages 5-8) | 0.38 | 0.15 |  |  |  | 1 |  | No | 0.15
Education - Computer lab | 0.15 | 0.15 |  |  |  | 1 |  | No
Education - Daycare (through age 4) | 0.21 | 0.15 |  |  |  | 2 |  | No | 0.15
Education - Daycare sickroom | 0.15 | 0.15 |  |  |  | 3 |  | No
Education - Lecture hall (fixed seats) |  | 0.15 |  |  |  | 1 | F | No | 0.15
Education - Lecture/postsecondary classroom | 0.38 | 0.15 |  |  |  | 1 | F | No | 0.15
Education - Media center | 0.15 | 0.15 |  |  |  | 1 | A | No
Education - Metal shop | 0.15 | 0.15 |  |  |  | 2 |  | No |  | <- Education - Wood/Metal shop
Education - Multiuse assembly | 0.5 | 0.15 |  |  |  | 1 | F | No | 0.15
Education - Music/theater/dance | 1.07 | 0.15 |  |  |  | 1 | F | No | 0.15
Education - Science laboratories | 0.15 | 0.15 |  |  | 1 | 2 |  | Yes
Education - University/college laboratories | 0.15 | 0.15 |  |  | 1 | 2 |  | Yes
Education - Wood shop | 0.15 | 0.15 |  |  | 0.5 | 2 |  | No |  | <- Education - Wood/Metal shop
Exhaust - All other locker rooms | 0 | 0 |  |  | 0.25 | 2 |  | No
Exhaust - Arenas | 0 | 0 |  |  | 0.5 | 1 | Exh. Note B | No
Exhaust - Auto repair rooms | 0 | 0 |  |  | 1.5 | 2 | Exh. Note A | No
Exhaust - Cells with toilet | 0 | 0 |  |  | 1 | 2 |  | No
Exhaust - Copy, printing rooms | 0 | 0 |  |  | 0.5 | 2 |  | No
Exhaust - Darkrooms | 0 | 0 |  |  | 1 | 2 |  | No
Exhaust - Janitor closets, trash rooms, recycling | 0 | 0 |  |  | 1 | 3 |  | No
Exhaust - Kitchenettes | 0 | 0 |  |  | 0.3 | 2 |  | No
Exhaust - Locker rooms for athletic or industrial facilities | 0 | 0 |  |  | 0.5 | 2 |  | No
Exhaust - Paint spray booths | 0 | 0 |  |  |  | 4 | Exh. Note F | No
Exhaust - Parking garages | 0 | 0 |  |  | 0.75 | 2 | Exh. Note C | Yes
Exhaust - Refrigerating machinery rooms | 0 | 0 |  |  |  | 3 | Exh. Note F | Yes
Exhaust - Shower rooms | 0 | 0 | 20 | 50 |  | 2 | Exh. Note G,H | No
Exhaust - Soiled laundry storage rooms | 0 | 0 |  |  | 1 | 3 | Exh. Note F | No
Exhaust - Storage rooms, chemical | 0 | 0 |  |  | 1.5 | 4 | Exh. Note F | Yes
Exhaust - Toilets, private | 0 | 0 | 25 | 50 |  | 2 | Exh. Note E | No
Exhaust - Toilets, public | 0 | 0 | 50 | 70 |  | 2 | Exh. Note D | No
Exhaust - Woodwork shop/classrooms | 0 | 0 |  |  | 0.5 | 2 |  | No
Food Service - Bars, cocktail lounges | 0.5 | 0.2 |  |  |  | 2 |  | No | 0.2
Food Service - Cafeteria/fast-food dining | 0.5 | 0.15 |  |  |  | 2 |  | No | 0.15
Food Service - Kitchen (cooking) | 0.15 | 0.15 |  |  | 0.7 | 2 |  | Yes
Food Service - Restaurant dining rooms | 0.5 | 0.15 |  |  |  | 2 |  | No | 0.15
General - Break rooms | 0.5 | 0.15 |  |  |  | 1 | F | No | 0.15
General - Coffee Stations | 0.5 | 0.15 |  |  |  | 1 | F | No | 0.15
General - Conference/meeting | 0.5 | 0.15 |  |  |  | 1 | F | No | 0.15
General - Corridors | 0.15 | 0.15 |  |  |  | 1 | F | No
General - Occupiable storage rooms for liquids or gels | 0.15 | 0.15 |  |  |  | 2 | B | Yes
General - Unoccupied | 0 | 0 |  |  |  | 1 |  | No | 0
Lodging - Barracks sleeping areas | 0.15 | 0.15 |  |  |  | 1 | F | No
Lodging - Bedroom/living room | 0.15 | 0.15 |  |  |  | 1 | F | No
Lodging - Laundry rooms within dwelling units | 0.15 | 0.15 |  |  |  | 1 |  | No
Lodging - Laundry rooms, central | 0.15 | 0.15 |  |  |  | 2 |  | No
Lodging - Lobbies/pre-function | 0.5 | 0.15 |  |  |  | 1 | F | No | 0.15
Lodging - Multipurpose assembly | 0.5 | 0.5 |  |  |  | 1 | F | No
Misc - All others | 0.15 | 0.15 |  |  |  | 2 |  | No
Misc - Bank vaults/safe deposit | 0.15 | 0.15 |  |  |  | 2 | F | No
Misc - Banks or bank lobbies | 0.15 | 0.15 |  |  |  | 1 | F | No
Misc - Computer (not printing) | 0.15 | 0.15 |  |  |  | 1 | F | Yes
Misc - Freezer and refrigerated spaces (<50F) | 0 | 0 |  |  |  | 2 | E | No
Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 0.15 | 0.15 |  |  |  | 3 |  | Yes
Misc - Pharmacy (preparation area) | 0.15 | 0.15 |  |  |  | 2 |  | No
Misc - Photo studios | 0.15 | 0.15 |  |  |  | 1 |  | No
Misc - Shipping/receiving | 0.15 | 0.15 |  |  |  | 2 | B | No
Misc - Sorting, packing, light assembly | 0.15 | 0.15 |  |  |  | 2 |  | No
Misc - Telephone closets | 0.15 | 0.15 |  |  |  | 1 |  | No
Misc - Transportation waiting | 0.5 | 0.15 |  |  |  | 1 | F | No | 0.15
Misc - Warehouses | 0.15 | 0.15 |  |  |  | 2 | B | No
Office - Breakrooms | 0.5 | 0.15 |  |  |  | 1 |  | No | 0.15
Office - Main entry lobbies | 0.5 | 0.15 |  |  |  | 1 | F | No | 0.15
Office - Occupiable storage rooms for dry materials | 0.15 | 0.15 |  |  |  | 1 |  | No
Office - Office space | 0.15 | 0.15 |  |  |  | 1 | F | No
Office - Reception areas | 0.15 | 0.15 |  |  |  | 1 | F | No
Office - Telephone/data entry | 0.15 | 0.15 |  |  |  | 1 | F | No
Residential - Common corridors | 0.15 | 0.15 |  |  |  | 1 | F | No
Retail - Barbershop | 0.4 | 0.4 |  |  | 0.5 | 2 | F | No
Retail - Beauty and nail salons | 0.4 | 0.4 |  |  | 0.6 | 2 |  | No
Retail - Coin-operated laundries | 0.3 | 0.3 |  |  |  | 2 |  | No
Retail - Mall common areas | 0.25 | 0.15 |  |  |  | 1 | F | No | 0.15
Retail - Pet shops (animal areas) | 0.25 | 0.15 |  |  | 0.9 | 2 |  | No | 0.15
Retail - Sales | 0.25 | 0.2 |  |  |  | 2 |  | No | 0.2
Retail - Supermarket | 0.25 | 0.2 |  |  |  | 1 | F | No | 0.2
Sports/Entertainment - Bowling alley (seating) | 1.07 | 0.15 |  |  |  | 1 |  | No | 0.15
Sports/Entertainment - Disco/dance floors | 1.5 | 0.15 |  |  |  | 2 | F | No | 0.15
Sports/Entertainment - Gambling casinos | 0.68 | 0.15 |  |  |  | 1 |  | No | 0.15
Sports/Entertainment - Game arcades | 0.68 | 0.15 |  |  |  | 1 |  | No | 0.15
Sports/Entertainment - Gym, sports arena (play area) | 0.5 | 0.15 |  |  |  | 2 | E | No | 0.15
Sports/Entertainment - Health club/aerobics room | 0.15 | 0.15 |  |  |  | 2 |  | No
Sports/Entertainment - Health club/weight rooms | 0.15 | 0.15 |  |  |  | 2 |  | No
Sports/Entertainment - Spectator areas | 0.5 | 0.15 |  |  |  | 1 | F | No | 0.15
Sports/Entertainment - Stages, studios | 0.5 | 0.15 |  |  |  | 1 | D, F | No | 0.15
Sports/Entertainment - Swimming (deck) | 0.5 | 0.15 |  |  |  | 2 | C | No | 0.15
Sports/Entertainment - Swimming (pool) | 0.15 | 0.15 |  |  |  | 2 | C | No
NA | 0 | 0 |  |  |  | 0 | 0 | Yes
High-Rise Residential Mechanical Ventilation Rate (cfm) shall be Qfan:
Qfan = (0.15 cfm/ft² x Afloor) + (3.5 cfm/bedroom x (Nbr + 1)) - (Vdwellingunit x 2 ach / 60 min/hr x Aext)
where:
Afloor = dwelling unit floor area (ft²)
Nbr = Number of bedrooms
Vdwellingunit = dwelling unit volume (ft³)
Aext = fraction of dwelling unit perimeter wall and roof/ceiling exposed to the outdoors

## SpcFuncBkCompat 16-19 (hidden)
Text File Gen
[5 empty] | Record header | comma | 12 spaces | 4 spaces | quote
[5 empty] | 2 | , |  |  | "
SpcFunc - 2016 | SpcFuncIdx - 2016 | SpcFunc - 2019 for backward compatibility | SpcFuncIdx - 2019 | Filter | BemEnums Backward Compat Entry
All Other | 157 | All other | #REF! |  | #REF!
Auditorium Area | 101 | Auditorium Area | #REF! |  | #REF!
Auto Repair Area | 102 | Auto Repair / Maintenance Area | #REF! |  | #REF!
Bar, Cocktail Lounge and Casino Areas | 103 | Dining Area (Bar/Lounge and Fine Dining) | #REF! | 1 | #REF!
Beauty Salon Area | 104 | Beauty Salon Area | #REF! |  | #REF!
Civic Meeting Place Area | 106 | Civic Meeting Place Area | #REF! |  | #REF!
Classrooms, Lecture, Training, Vocational Areas | 105 | Classroom, Lecture, Training, Vocational Areas | #REF! |  | #REF!
Commercial and Industrial Storage Areas (refrigerated) | 108 | Commercial/Industrial Storage (Refrigerated) | #REF! |  | #REF!
Commercial and Industrial Storage Areas (conditioned or unconditioned) | 107 | Commercial/Industrial Storage (Warehouse) | #REF! |  | #REF!
Computer Room | 109 | Computer Room | #REF! |  | #REF!
Malls and Atria | 139 | Concourse and Atria Area | #REF! |  | #REF!
Convention, Conference, Multipurpose and Meeting Center Areas | 110 | Convention, Conference, Multipurpose and Meeting Area | #REF! |  | #REF!
Corridors, Restrooms, Stairs, and Support Areas | 111 | _Invalid from 2016 - Corridors, Restrooms, Stairs, and Support Areas | #REF! |  | #REF!
Dining Area | 112 | Dining Area (Cafetaria/Fast Food) | #REF! |  | #REF!
Dry Cleaning (Coin Operated) | 113 | Laundry Area | #REF! | 1 | #REF!
Dry Cleaning (Full Service Commercial) | 114 | Laundry Area | #REF! | 1 | #REF!
Electrical, Mechanical, Telephone Rooms | 115 | Electrical, Mechanical, Telephone Rooms | #REF! |  | #REF!
Exercise Room | 116 | Exercise/Fitness Center and Gymnasium Areas | #REF! |  | #REF!
Financial Transaction Area | 118 | Financial Transaction Area | #REF! |  | #REF!
Police Station and Fire Station | 146 | _Invalid from 2016 - Police Station and Fire Station | #REF! |  | #REF!
General Commercial and Industrial Work Areas, High Bay | 119 | General/Commercial & Industrial Work Area (High Bay) | #REF! |  | #REF!
General Commercial and Industrial Work Areas, Low Bay | 120 | General/Commercial & Industrial Work Area (Low Bay) | #REF! |  | #REF!
General Commercial and Industrial Work Areas, Precision | 121 | General/Commercial & Industrial Work Area (Precision) | #REF! |  | #REF!
Grocery Sales Areas | 122 | Retail Sales Area (Grocery Sales) | #REF! | 1 | #REF!
High-Rise Residential Living Spaces | 123 | High-Rise Residential Living Spaces | #REF! |  | #REF!
Hotel Function Area | 124 | Hotel Function Area | #REF! |  | #REF!
Hotel/Motel Guest Room | 125 | Hotel/Motel Guest Room | #REF! |  | #REF!
Housing, Public and Common Areas: Multi-family, Dormitory | 126 | _Invalid from 2016 - Housing, Public and Common Areas: Multi-family, Dormitory | #REF! |  | #REF!
Housing, Public and Common Areas: Senior Housing | 127 | _Invalid from 2016 - Housing, Public and Common Areas: Senior Housing | #REF! |  | #REF!
Kitchen, Commercial Food Preparation | 128 | Kitchen/Food Preparation Area | #REF! |  | #REF!
Kitchenette or Residential Kitchen | 129 | Kitchenette or Residential Kitchen | #REF! |  | #REF!
Laundry | 132 | Laundry Area | #REF! |  | #REF!
Library, Reading Areas | 133 | Library (Reading Area) | #REF! |  | #REF!
Library, Stacks | 134 | Library (Stacks Area) | #REF! |  | #REF!
Lobby, Hotel | 135 | Main Entry Lobby | #REF! | 1 | #REF!
Locker/Dressing Room | 137 | Locker Room | #REF! |  | #REF!
Lounge, Recreation | 138 | Lounge, Breakroom, or Waiting Area | #REF! |  | #REF!
Lobby, Main Entry | 136 | Main Entry Lobby | #REF! |  | #REF!
Medical and Clinical Care | 140 | Healthcare Facility and Hospitals (Exam/Treatment Room) | #REF! |  | #REF!
Exhibit, Museum Areas | 117 | Museum Area (Exhibition/Display) | #REF! |  | #REF!
Nurseries for Children - Day Care | 202 | Classroom, Lecture, Training, Vocational Areas | #REF! |  | #REF!
Office (250 square feet in floor area or less) | 142 | Office Area (<250 square feet) | #REF! |  | #REF!
Office (Greater than 250 square feet in floor area) | 141 | Office Area (Open plan office) | #REF! |  | #REF!
Parking Garage Area Daylight Adaptation Zones | 145 | Parking Garage Area (Daylight Adaptation Zones) | #REF! |  | #REF!
Parking Garage Area Dedicated Ramps | 144 | Parking Garage Area (Dedicated Ramps) | #REF! |  | #REF!
Parking Garage Building, Parking Area | 143 | Parking Garage Area (Parking Zone) | #REF! |  | #REF!
Religious Worship Area | 147 | Religious Worship Area | #REF! |  | #REF!
Retail Merchandise Sales, Wholesale Showroom | 148 | Retail Sales Area (Retail Merchandise Sales) | #REF! |  | #REF!
Laboratory, Scientific | 130 | Scientific Laboratory Area | #REF! |  | #REF!
Laboratory, Equipment Room | 131 | Scientific Laboratory Area | #REF! | 1 | #REF!
Gymnasium/Sports Arena | 201 | Sports Arena - Playing Area (Recreational) | #REF! |  | #REF!
Theater, Motion Picture | 150 | Theater Area (Motion Picture) | #REF! |  | #REF!
Theater, Performance | 151 | Theater Area (Performance) | #REF! |  | #REF!
Transportation Function | 152 | Transportation Function (Ticketing Area) | #REF! | 1 | #REF!
Transportation Function, Concourse & Baggage | 155 | Transportation Function (Baggage Area) | #REF! |  | #REF!
Transportation Function, Ticketing | 156 | Transportation Function (Ticketing Area) | #REF! |  | #REF!
Unleased Tenant Area | 203 | Unleased Tenant Area | #REF! |  | #REF!
Unoccupied-Exclude from Gross Floor Area | 99 | Unoccupied-Exclude from Gross Floor Area | #REF! |  | #REF!
Unoccupied-Include in Gross Floor Area | 98 | Unoccupied-Include in Gross Floor Area | #REF! |  | #REF!
Videoconferencing Studio | 153 | Videoconferencing Studio | #REF! |  | #REF!
Waiting Area | 154 | Lounge, Breakroom, or Waiting Area | #REF! |  | #REF!

## SpcFuncBkCompat 22-25
Text File Gen
[5 empty] | Record header | comma | 12 spaces | 4 spaces | quote
[5 empty] | 2 | , |  |  | "
SpcFunc - 2022 | SpcFuncIdx - 2022 | SpcFunc - 2025 for backward compatibility | SpcFuncIdx - 2025 | Filter | BemEnums Backward Compat Entry
All other | Office | All other | Office |  | 2, Office, "All other"
Audience Seating Area | Assembly | Audience Seating Area | Assembly |  | 2, Assembly, "Audience Seating Area"
Auditorium Area | Assembly | Auditorium Area | Assembly |  | 2, Assembly, "Auditorium Area"
Auto Repair / Maintenance Area | Manufacturing | Auto Repair / Maintenance Area | Manufacturing | 1 | 2, Manufacturing, "Auto Repair / Maintenance Area"
Barber, Beauty Salon, Spa Area | Retail | Barber, Beauty Salon, Spa Area | Retail |  | 2, Retail, "Barber, Beauty Salon, Spa Area"
Civic Meeting Place Area | Assembly | Civic Meeting Place Area | Assembly |  | 2, Assembly, "Civic Meeting Place Area"
Classroom, Lecture, Training, Vocational Areas | School | Classroom, Lecture, Training, Vocational Areas | School |  | 2, School, "Classroom, Lecture, Training, Vocational Areas"
Storage, Commercial/Industrial (Refrigerated) | Warehouse | Storage, Commercial/Industrial (Refrigerated) | Warehouse |  | 2, Warehouse, "Storage, Commercial/Industrial (Refrigerated)"
Storage, Commercial/Industrial (Shipping & Handling) | Warehouse | Storage, Commercial/Industrial (Shipping & Handling) | Warehouse |  | 2, Warehouse, "Storage, Commercial/Industrial (Shipping & Handling)"
Storage, Commercial/Industrial (Warehouse) | Warehouse | Storage, Commercial/Industrial (Warehouse) | Warehouse |  | 2, Warehouse, "Storage, Commercial/Industrial (Warehouse)"
Computer Room | Data | Computer Room | Data |  | 2, Data, "Computer Room"
Concourse and Atria Area | Retail | Concourse and Atria Area | Retail |  | 2, Retail, "Concourse and Atria Area"
Convention, Conference, Multipurpose and Meeting Area | Assembly | Convention, Conference, Multipurpose and Meeting Area | Assembly |  | 2, Assembly, "Convention, Conference, Multipurpose and Meeting Area"
Copy Room | Office | Copy Room | Office |  | 2, Office, "Copy Room"
Corridor Area | Office | Corridor Area | Office | 1 | 2, Office, "Corridor Area"
Dining Area (Bar/Lounge and Fine Dining) | Restaurant | Dining Area (Bar/Lounge and Fine Dining) | Restaurant | 1 | 2, Restaurant, "Dining Area (Bar/Lounge and Fine Dining)"
Dining Area (Cafeteria/Fast Food) | Restaurant | Dining Area (Cafeteria/Fast Food) | Restaurant |  | 2, Restaurant, "Dining Area (Cafeteria/Fast Food)"
Dining Area (Family and Leisure) | Restaurant | Dining Area (Family and Leisure) | Restaurant |  | 2, Restaurant, "Dining Area (Family and Leisure)"
Electrical, Mechanical, Telephone Rooms | Warehouse | Electrical, Mechanical, Telephone Rooms | Warehouse |  | 2, Warehouse, "Electrical, Mechanical, Telephone Rooms"
Exercise/Fitness Center and Gymnasium Areas | Retail | Exercise/Fitness Center and Gymnasium Areas | Retail |  | 2, Retail, "Exercise/Fitness Center and Gymnasium Areas"
Financial Transaction Area | Office | Financial Transaction Area | Office |  | 2, Office, "Financial Transaction Area"
Manufacturing, Commercial & Industrial Work Area (High Bay) | Manufacturing | Manufacturing, Commercial & Industrial Work Area (High Bay) | Manufacturing |  | 2, Manufacturing, "Manufacturing, Commercial & Industrial Work Area (High Bay)"
Manufacturing, Commercial & Industrial Work Area (Low Bay) | Manufacturing | Manufacturing, Commercial & Industrial Work Area (Low Bay) | Manufacturing |  | 2, Manufacturing, "Manufacturing, Commercial & Industrial Work Area (Low Bay)"
Manufacturing, Commercial & Industrial Work Area (Precision) | Manufacturing | Manufacturing, Commercial & Industrial Work Area (Precision) | Manufacturing | 1 | 2, Manufacturing, "Manufacturing, Commercial & Industrial Work Area (Precision)"
Healthcare Facility and Hospitals (Exam/Treatment Room) | Health | Healthcare Facility and Hospitals (Exam/Treatment Room) | Health |  | 2, Health, "Healthcare Facility and Hospitals (Exam/Treatment Room)"
Healthcare Facility and Hospitals (Imaging Room) | Health | Healthcare Facility and Hospitals (Imaging Room) | Health |  | 2, Health, "Healthcare Facility and Hospitals (Imaging Room)"
Healthcare Facility and Hospitals (Medical Supply Room) | Health | Healthcare Facility and Hospitals (Medical Supply Room) | Health |  | 2, Health, "Healthcare Facility and Hospitals (Medical Supply Room)"
Healthcare Facility and Hospitals (Nursery) | Health | Healthcare Facility and Hospitals (Nursery) | Health |  | 2, Health, "Healthcare Facility and Hospitals (Nursery)"
Healthcare Facility and Hospitals (Nurse's Station) | Health | Healthcare Facility and Hospitals (Nurse's Station) | Health |  | 2, Health, "Healthcare Facility and Hospitals (Nurse's Station)"
Healthcare Facility and Hospitals (Operating Room) | Health | Healthcare Facility and Hospitals (Operating Room) | Health |  | 2, Health, "Healthcare Facility and Hospitals (Operating Room)"
Healthcare Facility and Hospitals (Patient Room) | Health | Healthcare Facility and Hospitals (Patient Room) | Health |  | 2, Health, "Healthcare Facility and Hospitals (Patient Room)"
Healthcare Facility and Hospitals (Physical Therapy Room) | Health | Healthcare Facility and Hospitals (Physical Therapy Room) | Health |  | 2, Health, "Healthcare Facility and Hospitals (Physical Therapy Room)"
Healthcare Facility and Hospitals (Recovery Room) | Health | Healthcare Facility and Hospitals (Recovery Room) | Health |  | 2, Health, "Healthcare Facility and Hospitals (Recovery Room)"
High-Rise Residential Living Spaces | ResidentialLiving | High-Rise Residential Living Spaces | ResidentialLiving |  | 2, ResidentialLiving, "High-Rise Residential Living Spaces"
Hotel Function Area | Assembly | Hotel Function Area | Assembly | 1 | 2, Assembly, "Hotel Function Area"
Hotel/Motel Guest Room | ResidentialLiving | Hotel/Motel Guest Room | ResidentialLiving |  | 2, ResidentialLiving, "Hotel/Motel Guest Room"
Kitchen/Food Preparation Area | Restaurant | Kitchen/Food Preparation Area | Restaurant |  | 2, Restaurant, "Kitchen/Food Preparation Area"
Kitchenette or Residential Kitchen | Office | Kitchenette or Residential Kitchen | Office |  | 2, Office, "Kitchenette or Residential Kitchen"
Laundry Area | ResidentialCommon | Laundry Area | ResidentialCommon |  | 2, ResidentialCommon, "Laundry Area"
Library (Reading Area) | Office | Library (Reading Area) | Office |  | 2, Office, "Library (Reading Area)"
Library (Stacks Area) | Office | Library (Stacks Area) | Office |  | 2, Office, "Library (Stacks Area)"
Locker Room | Assembly | Locker Room | Assembly |  | 2, Assembly, "Locker Room"
Lounge, Breakroom, or Waiting Area | Assembly | Lounge, Breakroom, or Waiting Area | Assembly |  | 2, Assembly, "Lounge, Breakroom, or Waiting Area"
Lobby, Main Entry | Assembly | Lobby, Main Entry | Assembly |  | 2, Assembly, "Lobby, Main Entry"
Museum Area (Exhibition/Display) | Assembly | Museum Area (Exhibition/Display) | Assembly |  | 2, Assembly, "Museum Area (Exhibition/Display)"
Museum Area (Restoration Room) | Assembly | Museum Area (Restoration Room) | Assembly |  | 2, Assembly, "Museum Area (Restoration Room)"
Office Area (<250 square feet) | Office | Office Area (<250 square feet) | Office |  | 2, Office, "Office Area (<250 square feet)"
Office Area (>250 square feet) | Office | Office Area (>250 square feet) | Office |  | 2, Office, "Office Area (>250 square feet)"
Office Area (>250 square feet) | Office | Office Area (>250 square feet) | Office |  | 2, Office, "Office Area (>250 square feet)"
Parking Garage Area (Daylight Adaptation Zones) | Parking | Parking Garage Area (Daylight Adaptation Zones) | Parking | 1 | 2, Parking, "Parking Garage Area (Daylight Adaptation Zones)"
Parking Garage Area (Parking Zone and Ramps) | Parking | Parking Garage Area (Parking Zone and Ramps) | Parking |  | 2, Parking, "Parking Garage Area (Parking Zone and Ramps)"
Parking Garage Area (Parking Zone and Ramps) | Parking | Parking Garage Area (Parking Zone and Ramps) | Parking |  | 2, Parking, "Parking Garage Area (Parking Zone and Ramps)"
Pharmacy Area | Retail | Pharmacy Area | Retail |  | 2, Retail, "Pharmacy Area"
Religious Worship Area | Assembly | Religious Worship Area | Assembly | 1 | 2, Assembly, "Religious Worship Area"
Restrooms | Office | Restrooms | Office |  | 2, Office, "Restrooms"
Retail Sales Area (Fitting Room) | Retail | Retail Sales Area (Fitting Room) | Retail |  | 2, Retail, "Retail Sales Area (Fitting Room)"
Retail Sales Area (Grocery Sales) | Retail | Retail Sales Area (Grocery Sales) | Retail |  | 2, Retail, "Retail Sales Area (Grocery Sales)"
Retail Sales Area (Retail Merchandise Sales) | Retail | Retail Sales Area (Retail Merchandise Sales) | Retail |  | 2, Retail, "Retail Sales Area (Retail Merchandise Sales)"
Laboratory, Scientific | Laboratory | Laboratory, Scientific | Laboratory |  | 2, Laboratory, "Laboratory, Scientific"
Sports Arena - Playing Area (> 5,000 Spectators) | Retail | Sports Arena - Playing Area (> 5,000 Spectators) | Retail |  | 2, Retail, "Sports Arena - Playing Area (> 5,000 Spectators)"
Sports Arena - Playing Area (2,000 - 5,000 Spectators) | Retail | Sports Arena - Playing Area (2,000 - 5,000 Spectators) | Retail |  | 2, Retail, "Sports Arena - Playing Area (2,000 - 5,000 Spectators)"
Sports Arena - Playing Area (< 2,000 Spectators) | Retail | Sports Arena - Playing Area (< 2,000 Spectators) | Retail |  | 2, Retail, "Sports Arena - Playing Area (< 2,000 Spectators)"
Sports Arena - Playing Area (Recreational) | Retail | Sports Arena - Playing Area (Recreational) | Retail |  | 2, Retail, "Sports Arena - Playing Area (Recreational)"
Stairwell | Office | Stairwell | Office |  | 2, Office, "Stairwell"
Theater Area (Motion Picture) | Assembly | Theater Area (Motion Picture) | Assembly |  | 2, Assembly, "Theater Area (Motion Picture)"
Theater Area (Performance) | Assembly | Theater Area (Performance) | Assembly |  | 2, Assembly, "Theater Area (Performance)"
Transportation Function (Baggage Area) | Assembly | Transportation Function (Baggage Area) | Assembly |  | 2, Assembly, "Transportation Function (Baggage Area)"
Transportation Function (Ticketing Area) | Assembly | Transportation Function (Ticketing Area) | Assembly |  | 2, Assembly, "Transportation Function (Ticketing Area)"
Unleased Tenant Area | Office | Unleased Tenant Area | Office |  | 2, Office, "Unleased Tenant Area"
Unoccupied-Exclude from Gross Floor Area | Unoccupied | Unoccupied-Exclude from Gross Floor Area | Unoccupied |  | 2, Unoccupied, "Unoccupied-Exclude from Gross Floor Area"
Unoccupied-Include in Gross Floor Area | Unoccupied | Unoccupied-Include in Gross Floor Area | Unoccupied |  | 2, Unoccupied, "Unoccupied-Include in Gross Floor Area"
Videoconferencing Studio | Office | Videoconferencing Studio | Office |  | 2, Office, "Videoconferencing Studio"
Aging Eye/Low-vision (Corridor Area) | Office | Aging Eye/Low-vision (Corridor Area) | Office |  | 2, Office, "Aging Eye/Low-vision (Corridor Area)"
Aging Eye/Low-vision (Dining) | Restaurant | Aging Eye/Low-vision (Dining) | Restaurant |  | 2, Restaurant, "Aging Eye/Low-vision (Dining)"
Aging Eye/Low-vision (Lounge/Waiting Area) | Assembly | Aging Eye/Low-vision (Lounge/Waiting Area) | Assembly |  | 2, Assembly, "Aging Eye/Low-vision (Lounge/Waiting Area)"
Aging Eye/Low-vision (Lobby, Main Entry) | Assembly | Aging Eye/Low-vision (Lobby, Main Entry) | Assembly |  | 2, Assembly, "Aging Eye/Low-vision (Lobby, Main Entry)"
Aging Eye/Low-vision (Multipurpose Room) | Assembly | Aging Eye/Low-vision (Multipurpose Room) | Assembly |  | 2, Assembly, "Aging Eye/Low-vision (Multipurpose Room)"
Aging Eye/Low-vision (Religious Worship Area) | Assembly | Aging Eye/Low-vision (Religious Worship Area) | Assembly |  | 2, Assembly, "Aging Eye/Low-vision (Religious Worship Area)"
Aging Eye/Low-vision (Restroom) | Office | Aging Eye/Low-vision (Restroom) | Office |  | 2, Office, "Aging Eye/Low-vision (Restroom)"
Aging Eye/Low-vision (Stairwell) | Office | Aging Eye/Low-vision (Stairwell) | Office |  | 2, Office, "Aging Eye/Low-vision (Stairwell)"
Conference, Multipurpose and Meeting Area | Assembly | Convention, Conference, Multipurpose and Meeting Area | Assembly |  | 2, Assembly, "Conference, Multipurpose and Meeting Area"
Storage | Warehouse | Storage, General | Warehouse |  | 2, Warehouse, "Storage"

## 2016SpcFunc (hidden)
Copied Input Data Model.txt
SpcFunc | SpcFuncIdx
Unoccupied-Include in Gross Floor Area | 98
Unoccupied-Exclude from Gross Floor Area | 99
Auditorium Area | 101
Auto Repair Area | 102
Bar, Cocktail Lounge and Casino Areas | 103
Beauty Salon Area | 104
Civic Meeting Place Area | 106
Classrooms, Lecture, Training, Vocational Areas | 105
Commercial and Industrial Storage Areas (conditioned or unconditioned) | 107
Commercial and Industrial Storage Areas (refrigerated) | 108
Computer Room | 109
Convention, Conference, Multipurpose and Meeting Center Areas | 110
Corridors, Restrooms, Stairs, and Support Areas | 111
Dining Area | 112
Dry Cleaning (Coin Operated) | 113
Dry Cleaning (Full Service Commercial) | 114
Electrical, Mechanical, Telephone Rooms | 115
Exercise Room | 116
Exhibit, Museum Areas | 117
Financial Transaction Area | 118
General Commercial and Industrial Work Areas, High Bay | 119
General Commercial and Industrial Work Areas, Low Bay | 120
General Commercial and Industrial Work Areas, Precision | 121
Grocery Sales Areas | 122
Gymnasium/Sports Arena | 201
High-Rise Residential Living Spaces | 123
Hotel Function Area | 124
Hotel/Motel Guest Room | 125
Housing, Public and Common Areas: Multi-family, Dormitory | 126
Housing, Public and Common Areas: Senior Housing | 127
Kitchen, Commercial Food Preparation | 128
Kitchenette or Residential Kitchen | 129
Laboratory, Equipment Room | 131
Laboratory, Scientific | 130
Laundry | 132
Library, Reading Areas | 133
Library, Stacks | 134
Lobby, Hotel | 135
Lobby, Main Entry | 136
Locker/Dressing Room | 137
Lounge, Recreation | 138
Malls and Atria | 139
Medical and Clinical Care | 140
Nurseries for Children - Day Care | 202
Office (250 square feet in floor area or less) | 142
Office (Greater than 250 square feet in floor area) | 141
Parking Garage Area Daylight Adaptation Zones | 145
Parking Garage Area Dedicated Ramps | 144
Parking Garage Building, Parking Area | 143
Police Station and Fire Station | 146
Religious Worship Area | 147
Retail Merchandise Sales, Wholesale Showroom | 148
Theater, Motion Picture | 150
Theater, Performance | 151
Transportation Function | 152
Transportation Function, Concourse & Baggage | 155
Transportation Function, Ticketing | 156
Unleased Tenant Area | 203
Videoconferencing Studio | 153
Waiting Area | 154
All Other | 157

## 2019SpcFunc BEMEnums Gen (hidden)
Text File Gen
|  | Record header | comma | 12 spaces | 4 spaces | quote
|  | 2 | , |  |  | "
SpcFunc | SpcFuncIdx | BEMEnums Entry
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF! | #REF! | #REF!
#REF!

## 2022SpcFunc BEMEnums Gen
Text File Gen
|  | Record header | comma | 12 spaces | 4 spaces | quote
|  | 2 | , |  |  | "
SpcFunc | SpcFuncIdx | BEMEnums Entry
Aging Eye/Low-vision (Corridor Area) | Office | 2, Office, "Aging Eye/Low-vision (Corridor Area)"
Aging Eye/Low-vision (Dining) | Restaurant | 2, Restaurant, "Aging Eye/Low-vision (Dining)"
Aging Eye/Low-vision (Lobby, Main Entry) | Assembly | 2, Assembly, "Aging Eye/Low-vision (Lobby, Main Entry)"
Aging Eye/Low-vision (Lounge/Waiting Area) | Assembly | 2, Assembly, "Aging Eye/Low-vision (Lounge/Waiting Area)"
Aging Eye/Low-vision (Multipurpose Room) | Assembly | 2, Assembly, "Aging Eye/Low-vision (Multipurpose Room)"
Aging Eye/Low-vision (Religious Worship Area) | Assembly | 2, Assembly, "Aging Eye/Low-vision (Religious Worship Area)"
Aging Eye/Low-vision (Restroom) | Office | 2, Office, "Aging Eye/Low-vision (Restroom)"
Aging Eye/Low-vision (Stairwell) | Office | 2, Office, "Aging Eye/Low-vision (Stairwell)"
Audience Seating Area | Assembly | 2, Assembly, "Audience Seating Area"
Auditorium Area | Assembly | 2, Assembly, "Auditorium Area"
Auto Repair / Maintenance Area | Manufacturing | 2, Manufacturing, "Auto Repair / Maintenance Area"
Barber, Beauty Salon, Spa Area | Retail | 2, Retail, "Barber, Beauty Salon, Spa Area"
Civic Meeting Place Area | Assembly | 2, Assembly, "Civic Meeting Place Area"
Classroom, Lecture, Training, Vocational Areas | School | 2, School, "Classroom, Lecture, Training, Vocational Areas"
Computer Room | Data | 2, Data, "Computer Room"
Concourse and Atria Area | Retail | 2, Retail, "Concourse and Atria Area"
Convention, Conference, Multipurpose and Meeting Area | Assembly | 2, Assembly, "Convention, Conference, Multipurpose and Meeting Area"
Copy Room | Office | 2, Office, "Copy Room"
Corridor Area | Office | 2, Office, "Corridor Area"
Dining Area (Bar/Lounge and Fine Dining) | Restaurant | 2, Restaurant, "Dining Area (Bar/Lounge and Fine Dining)"
Dining Area (Cafeteria/Fast Food) | Restaurant | 2, Restaurant, "Dining Area (Cafeteria/Fast Food)"
Dining Area (Family and Leisure) | Restaurant | 2, Restaurant, "Dining Area (Family and Leisure)"
Electrical, Mechanical, Telephone Rooms | Warehouse | 2, Warehouse, "Electrical, Mechanical, Telephone Rooms"
Exercise/Fitness Center and Gymnasium Areas | Retail | 2, Retail, "Exercise/Fitness Center and Gymnasium Areas"
Financial Transaction Area | Office | 2, Office, "Financial Transaction Area"
Healthcare Facility and Hospitals (Exam/Treatment Room) | Health | 2, Health, "Healthcare Facility and Hospitals (Exam/Treatment Room)"
Healthcare Facility and Hospitals (Imaging Room) | Health | 2, Health, "Healthcare Facility and Hospitals (Imaging Room)"
Healthcare Facility and Hospitals (Medical Supply Room) | Health | 2, Health, "Healthcare Facility and Hospitals (Medical Supply Room)"
Healthcare Facility and Hospitals (Nursery) | Health | 2, Health, "Healthcare Facility and Hospitals (Nursery)"
Healthcare Facility and Hospitals (Nurse's Station) | Health | 2, Health, "Healthcare Facility and Hospitals (Nurse's Station)"
Healthcare Facility and Hospitals (Operating Room) | Health | 2, Health, "Healthcare Facility and Hospitals (Operating Room)"
Healthcare Facility and Hospitals (Patient Room) | Health | 2, Health, "Healthcare Facility and Hospitals (Patient Room)"
Healthcare Facility and Hospitals (Physical Therapy Room) | Health | 2, Health, "Healthcare Facility and Hospitals (Physical Therapy Room)"
Healthcare Facility and Hospitals (Recovery Room) | Health | 2, Health, "Healthcare Facility and Hospitals (Recovery Room)"
High-Rise Residential Living Spaces | ResidentialLiving | 2, ResidentialLiving, "High-Rise Residential Living Spaces"
Hotel Function Area | Assembly | 2, Assembly, "Hotel Function Area"
Hotel/Motel Guest Room | ResidentialLiving | 2, ResidentialLiving, "Hotel/Motel Guest Room"
Kitchen/Food Preparation Area | Restaurant | 2, Restaurant, "Kitchen/Food Preparation Area"
Kitchenette or Residential Kitchen | Office | 2, Office, "Kitchenette or Residential Kitchen"
Laboratory, Scientific | Laboratory | 2, Laboratory, "Laboratory, Scientific"
Laundry Area | ResidentialCommon | 2, ResidentialCommon, "Laundry Area"
Library (Reading Area) | Office | 2, Office, "Library (Reading Area)"
Library (Stacks Area) | Office | 2, Office, "Library (Stacks Area)"
Lobby, Main Entry | Assembly | 2, Assembly, "Lobby, Main Entry"
Locker Room | Assembly | 2, Assembly, "Locker Room"
Lounge, Breakroom, or Waiting Area | Assembly | 2, Assembly, "Lounge, Breakroom, or Waiting Area"
Manufacturing, Commercial & Industrial Work Area (Low Bay) | Manufacturing | 2, Manufacturing, "Manufacturing, Commercial & Industrial Work Area (Low Bay)"
Manufacturing, Commercial & Industrial Work Area (High Bay) | Manufacturing | 2, Manufacturing, "Manufacturing, Commercial & Industrial Work Area (High Bay)"
Manufacturing, Commercial & Industrial Work Area (Precision) | Manufacturing | 2, Manufacturing, "Manufacturing, Commercial & Industrial Work Area (Precision)"
Museum Area (Exhibition/Display) | Assembly | 2, Assembly, "Museum Area (Exhibition/Display)"
Museum Area (Restoration Room) | Assembly | 2, Assembly, "Museum Area (Restoration Room)"
Office Area (>250 square feet) | Office | 2, Office, "Office Area (>250 square feet)"
Office Area (<250 square feet) | Office | 2, Office, "Office Area (<250 square feet)"
Parking Garage Area (Parking Zone and Ramps) | Parking | 2, Parking, "Parking Garage Area (Parking Zone and Ramps)"
Parking Garage Area (Daylight Adaptation Zones) | Parking | 2, Parking, "Parking Garage Area (Daylight Adaptation Zones)"
Pharmacy Area | Retail | 2, Retail, "Pharmacy Area"
Retail Sales Area (Grocery Sales) | Retail | 2, Retail, "Retail Sales Area (Grocery Sales)"
Retail Sales Area (Retail Merchandise Sales) | Retail | 2, Retail, "Retail Sales Area (Retail Merchandise Sales)"
Retail Sales Area (Fitting Room) | Retail | 2, Retail, "Retail Sales Area (Fitting Room)"
Religious Worship Area | Assembly | 2, Assembly, "Religious Worship Area"
Restrooms | Office | 2, Office, "Restrooms"
Stairwell | Office | 2, Office, "Stairwell"
Storage, Commercial/Industrial (Warehouse) | Warehouse | 2, Warehouse, "Storage, Commercial/Industrial (Warehouse)"
Storage, Commercial/Industrial (Refrigerated) | Warehouse | 2, Warehouse, "Storage, Commercial/Industrial (Refrigerated)"
Storage, Commercial/Industrial (Shipping & Handling) | Warehouse | 2, Warehouse, "Storage, Commercial/Industrial (Shipping & Handling)"
Sports Arena - Playing Area (> 5,000 Spectators) | Retail | 2, Retail, "Sports Arena - Playing Area (> 5,000 Spectators)"
Sports Arena - Playing Area (2,000 - 5,000 Spectators) | Retail | 2, Retail, "Sports Arena - Playing Area (2,000 - 5,000 Spectators)"
Sports Arena - Playing Area (< 2,000 Spectators) | Retail | 2, Retail, "Sports Arena - Playing Area (< 2,000 Spectators)"
Sports Arena - Playing Area (Recreational) | Retail | 2, Retail, "Sports Arena - Playing Area (Recreational)"
Theater Area (Motion Picture) | Assembly | 2, Assembly, "Theater Area (Motion Picture)"
Theater Area (Performance) | Assembly | 2, Assembly, "Theater Area (Performance)"
Transportation Function (Baggage Area) | Assembly | 2, Assembly, "Transportation Function (Baggage Area)"
Transportation Function (Ticketing Area) | Assembly | 2, Assembly, "Transportation Function (Ticketing Area)"
Unleased Tenant Area | Office | 2, Office, "Unleased Tenant Area"
Unoccupied-Exclude from Gross Floor Area | Unoccupied | 2, Unoccupied, "Unoccupied-Exclude from Gross Floor Area"
Unoccupied-Include in Gross Floor Area | Unoccupied | 2, Unoccupied, "Unoccupied-Include in Gross Floor Area"
Videoconferencing Studio | Office | 2, Office, "Videoconferencing Studio"
All other | Office | 2, Office, "All other"
Storage | Warehouse | 2, Warehouse, "Storage"
Health Care / Assisted Living (Nurse's Station) | ResidentialCommon | 2, ResidentialCommon, "Health Care / Assisted Living (Nurse's Station)"
Health Care / Assisted Living (Physical Therapy Room) | ResidentialCommon | 2, ResidentialCommon, "Health Care / Assisted Living (Physical Therapy Room)"

## 2025 Ventilation List
Table 120.1-A - Minimum Ventilation Rates
| Occupancy Category | Minimum Occupant Load Density | Area-based Minimum Ventilation Ra | Air Class | Notes
|  | persons/1000 ft2 | cfm/ft2
Educational Facilities
| Daycare (through age 4) | 14 | 0.15 | 2
| Daycare sickroom | 5 | 0.15 | 3
| Classrooms (ages 5-8) | 25 | 0.15 | 1
| Classrooms (ages 9-18) | 25 | 0.15 | 1
| Lecture/postsecondary classroom | 25 | 0.15 | 1 | F
| Lecture hall (fixed seats) | 71 | 0.15 | 1 | F
| Art classroom | 25 | 0.15 | 2
| Science laboratories | 25 | 0.15 | 2
| University/college laboratories | 25 | 0.15 | 2
| Wood/metal shop | 10 | 0.15 | 2
| Computer lab | 25 | 0.15 | 1
| Media center | 25 | 0.15 | 1 | A
| Music/theater/dance | 33 | 0.15 | 1 | F
| Multiuse assembly | 33 | 0.15 | 1 | F
Food and Beverage Service
| Restaurant dining rooms | 33 | 0.15 | 2
| Cafeteria/fast-food dining | 33 | 0.15 | 2
| Bars, cocktail lounges | 33 | 0.2 | 2
| Kitchen (cooking) | 3 | 0.15 | 2
General
| Break rooms | 33 | 0.15 | 1 | F
| Coffee Stations | 33 | 0.15 | 1 | F
| Conference/meeting | 33 | 0.15 | 1 | F
| Corridors | 5 | 0.15 | 1 | F
| Occupiable storage rooms for liquids or gels | 2 | 0.15 | 2 | B
Hotels, Motels, Resorts, Dormitories
| Bedroom/living room | 3 | 0.15 | 1 | F
| Barracks sleeping areas | 5 | 0.15 | 1 | F
| Laundry rooms, central | 5 | 0.15 | 2
| Laundry rooms within dwelling units | 5 | 0.15 | 1
| Lobbies/pre-function | 33 | 0.15 | 1 | F
| Multipurpose assembly | 33 | 0.15 | 1 | F
Office Buildings
| Breakrooms | 33 | 0.15 | 1
| Main entry lobbies | 33 | 0.15 | 1 | F
| Occupiable storage rooms for dry materials | 2 | 0.15 | 1
| Office space | 5 | 0.15 | 1 | F
| Reception areas | 5 | 0.15 | 1 | F
| Telephone/data entry | 33 | 0.15 | 1 | F
Miscellaneous Spaces
| Bank vaults/safe deposit | 5 | 0.15 | 2 | F
| Banks or bank lobbies | 5 | 0.15 | 1 | F
| Computer (not printing) | 5 | 0.15 | 1 | F
| Freezer and refrigerated spaces (<50oF) | 0 | 0 | 2 | E
| General manufacturing (excludes heavy industrial and process using chemicals) | 5 | 0.15 | 3
| Pharmacy (preparation area) | 5 | 0.15 | 2
| Photo studios | 5 | 0.15 | 1
| Shipping/receiving | 5 | 0.15 | 2 | B
| Sorting, packing, light assembly | 5 | 0.15 | 2
| Telephone closets | 5 | 0.15 | 1
| Transportation waiting | 33 | 0.15 | 1 | F
| Warehouses | 1 | 0.15 | 2 | B
| All others | 5 | 0.15 | 2
Public Assembly Spaces
| Auditorium seating area | 7 | 0.15 | 1 | F
| Places of religious worship | 7 | 0.15 | 1 | F
| Courtrooms | 13 | 0.15 | 1 | F
| Legislative chambers | 13 | 0.15 | 1 | F
| Libraries (reading rooms and stack areas) | 10 | 0.15 | 1
| Lobbies | 33 | 0.15 | 1 | F
| Museums (childrens) | 17 | 0.15 | 1
| Museums/galleries | 17 | 0.15 | 1 | F
Residential
| Common corridors | 5 | 0.15 | 1 | F
Retail
| Sales (except as below) | 17 | 0.2 | 2
| Mall common areas | 17 | 0.15 | 1 | F
| Barbershop | 17 | 0.4 | 2 | F
| Beauty and nail salons | 17 | 0.4 | 2
| Pet shops (animal areas) | 17 | 0.2 | 2
| Supermarket | 17 | 0.2 | 1 | F
| Coin-operated laundries | 17 | 0.3 | 2
Sports and Entertainment
| Gym, sports arena (play area) | 10 | 0.15 | 2 | E
| Spectator areas | 33 | 0.15 | 1 | F
| Swimming (pool) | 10 | 0.15 | 2 | C
| Swimming (deck) | 33 | 0.15 | 2 | C
| Disco/dance floors | 100 | 0.15 | 2 | F
| Health club/aerobics room | 10 | 0.15 | 2
| Health club/weight rooms | 10 | 0.15 | 2
| Bowling alley (seating) | 7 | 0.15 | 1
| Gambling casinos | 45 | 0.15 | 1
| Game arcades | 45 | 0.15 | 1
| Stages, studios | 33 | 0.15 | 1 | D, F
General:
1. The minimum occupant density is one half of the maximum occupant load assumed for egress purposes in the CBC
Specific Notes:
A - For high-school and college libraries, the values shown for “Public Assembly Spaces - Libraries” shall be used.
B - Rate may not be sufficient where stored materials include those having potentially harmful emissions.
C - Rate does not allow for humidity control. “Deck area” refers to the area surrounding the pool that is capable of being wetted during pool use or when the pool is occupied. Deck area that is not expected to be wetted shall be designated as an occupancy category.
D - Rate does not include special exhaust for stage effects such as dry ice vapors and smoke.
E - Where combustion equipment is intended to be used on the playing surface or in the space, additional dilution ventilation source control, or both shall be provided.
F - Ventilation air for this occupancy category shall be permitted to be reduced to zero when the space is in occupied-standby mode
Table 120.1-B - Minimum Exhaust Rates
[ASHRAE 62.1: TABLE 6.5]
| Occupancy Category | Exhaust Rete, | Exhaust Rate, | Air Class | Notes
|  | cfm/unit | cfm/ft2
| Animal imaging(MRI/CT/PET) | - | 0.9 | 3
| Animal operating rooms | - | 3 | 3
| Animal postoperative recovery room | - | 1.5 | 3
| Animal preparation rooms | - | 1.5 | 3
| Animal procedure room | - | 2.25 | 3
| Animal surgery scrub | - | 1.5 | 3
| Large-animal holding room | - | 2.25 | 3
| Animal Necropsy | - | 2.25 | 3
| Small-animal-cage room (static cages) | - | 2.25 | 3
| Small-animal-cage room (ventilated cages) | - | 1.5 | 3
| Arenas | - | 0.5 | 1 | B
| Art classrooms | - | 0.7 | 2
| Auto repair rooms | - | 1.5 | 2 | A
| Barber shops | - | 0.5 | 2
| Beauty and nail salons | - | 0.6 | 2
| Cells with toilet | - | 1 | 2
| Copy, printing rooms | - | 0.5 | 2
| Darkrooms | - | 1 | 2
| Educational science laboratories | - | 1 | 2
| Janitor closets, trash rooms, recycling | - | 1 | 3
| Kitchenettes | - | 0.3 | 2
| Kitchens - commercial | - | 0.7 | 2
| Locker rooms for athletic or industrial facilities | - | 0.5 | 2
| All other locker rooms | - | 0.25 | 2
| Shower rooms | 20/50 | - | 2 | G,H
| Paint spray booths | - | - | 4 | F
| Parking garages | - | 0.75 | 2 | C
| Pet shops (animal areas) | - | 0.9 | 2
| Refrigerating machinery rooms | - | - | 3 | F
| Soiled laundry storage rooms | - | 1 | 3 | F
| Storage rooms, chemical | - | 1.5 | 4 | F
| Toilets - private | 25/50 | - | 2 | E
| Toilets, public | 50/70 | - | 2 | D
| Woodwork shop/classrooms | - | 0.5 | 2
Notes:
A - Stands where engines are run shall have exhaust systems that directly connect to the engine exhaust and prevent escape of fumes.
B - Where combustion equipment is intended to be used on the playing surface, additional dilution ventilation, source control, or both shall be provided.
C - Exhaust shall not be required where two or more sides comprise walls that are at least 50% open to the outside.
D - Rate is per water closet, urinal, or both. Provide the higher rate where periods of heavy use are expected to occur. The lower rate shall be permitted to be used otherwise.
E - Rate is for a toilet room intended to be occupied by one person at a time. For continuous systems operation during hours of use, the lower rate shall be permitted to be used. Otherwise the higher rate shall be used.
F - See other applicable standards for exhaust rate.
G - For continuous system operation, the lower rate shall be permitted to be used. Otherwise the higher rate shall be used.
H - Rate is per showerhead

## 2025 Ventilation List SORT
Occupancy Category | Minimum Occupant Load Density | Area-based Minimum Ventilation Ra | Continuous Exhaust Rate, | Intermittent Exhaust Rate, | Exhaust Rate, | Air Class | Notes | Baseline ventilation = proposed?
| persons/1000 ft² | cfm/ft² | cfm/unit | cfm/unit | cfm/ft²
Assembly - Auditorium seating area | 7 | 0.15 |  |  |  | 1 | F | No
Assembly - Courtrooms | 13 | 0.15 |  |  |  | 1 | F | No
Assembly - Legislative chambers | 13 | 0.15 |  |  |  | 1 | F | No
Assembly - Libraries (reading rooms and stack areas) | 10 | 0.15 |  |  |  | 1 |  | No
Assembly - Lobbies | 33 | 0.15 |  |  |  | 1 | F | No
Assembly - Museums (childrens) | 17 | 0.15 |  |  |  | 1 |  | No
Assembly - Museums/galleries | 17 | 0.15 |  |  |  | 1 | F | No
Assembly - Places of religious worship | 7 | 0.15 |  |  |  | 1 | F | No
Education - Art classroom | 25 | 0.15 |  |  | 0.7 | 2 |  | No
Education - Classrooms (ages 9-18) | 25 | 0.15 |  |  |  | 1 |  | No
Education - Classrooms (ages 5-8) | 25 | 0.15 |  |  |  | 1 |  | No
Education - Computer lab | 25 | 0.15 |  |  |  | 1 |  | No
Education - Daycare (through age 4) | 14 | 0.15 |  |  |  | 2 |  | No
Education - Daycare sickroom | 5 | 0.15 |  |  |  | 3 |  | No
Education - Lecture hall (fixed seats) | 71 | 0.15 |  |  |  | 1 | F | No
Education - Lecture/postsecondary classroom | 25 | 0.15 |  |  |  | 1 | F | No
Education - Media center | 25 | 0.15 |  |  |  | 1 | A | No
Education - Metal shop | 10 | 0.15 |  |  |  | 2 |  | No | <- Education - Wood/Metal shop
Education - Multiuse assembly | 33 | 0.15 |  |  |  | 1 | F | No
Education - Music/theater/dance | 33 | 0.15 |  |  |  | 1 | F | No
Education - Science laboratories | 25 | 0.15 |  |  | 1 | 2 |  | Yes
Education - University/college laboratories | 25 | 0.15 |  |  | 1 | 2 |  | Yes
Education - Wood shop | 10 | 0.15 |  |  | 0.5 | 2 |  | No | <- Education - Wood/Metal shop
Exhaust - All other locker rooms |  |  |  |  | 0.25 | 2 |  | No
Exhaust - Animal imaging(MRI/CT/PET) |  |  |  |  | 0.9 | 3 |  | No
Exhaust - Animal operating rooms |  |  |  |  | 3 | 3 |  | No
Exhaust - Animal postoperative recovery room |  |  |  |  | 1.5 | 3 |  | No
Exhaust - Animal preparation rooms |  |  |  |  | 1.5 | 3 |  | No
Exhaust - Animal procedure room |  |  |  |  | 2.25 | 3 |  | No
Exhaust - Animal surgery scrub |  |  |  |  | 1.5 | 3 |  | No
Exhaust - Animal Necropsy |  |  |  |  | 2.25 | 3 |  | No
Exhaust - Arenas |  |  |  |  | 0.5 | 1 | Exh. Note B | No
Exhaust - Auto repair rooms |  |  |  |  | 1.5 | 2 | Exh. Note A | No
Exhaust - Cells with toilet |  |  |  |  | 1 | 2 |  | No
Exhaust - Copy, printing rooms |  |  |  |  | 0.5 | 2 |  | No
Exhaust - Darkrooms |  |  |  |  | 1 | 2 |  | No
Exhaust - Janitor closets, trash rooms, recycling |  |  |  |  | 1 | 3 |  | No
Exhaust - Kitchenettes |  |  |  |  | 0.3 | 2 |  | No
Exhaust - Large-animal holding room |  |  |  |  | 2.25 | 3 |  | No
Exhaust - Locker rooms for athletic or industrial facilities |  |  |  |  | 0.5 | 2 |  | No
Exhaust - Paint spray booths | [5 empty] | 4 | Exh. Note F | No
Exhaust - Parking garages |  |  |  |  | 0.75 | 2 | Exh. Note C | Yes
Exhaust - Refrigerating machinery rooms | [5 empty] | 3 | Exh. Note F | Yes
Exhaust - Shower rooms |  |  | 20 | 50 |  | 2 | Exh. Note G,H | No
Exhaust - Small-animal-cage room (static cages) |  |  |  |  | 2.25 | 3 |  | No
Exhaust - Small-animal-cage room (ventilated cages) |  |  |  |  | 1.5 | 3 |  | No
Exhaust - Soiled laundry storage rooms |  |  |  |  | 1 | 3 | Exh. Note F | No
Exhaust - Storage rooms, chemical |  |  |  |  | 1.5 | 4 | Exh. Note F | Yes
Exhaust - Toilets, private |  |  | 25 | 50 |  | 2 | Exh. Note E | No
Exhaust - Toilets, public |  |  | 50 | 70 |  | 2 | Exh. Note D | No
Exhaust - Woodwork shop/classrooms |  |  |  |  | 0.5 | 2 |  | No
Food Service - Bars, cocktail lounges | 33 | 0.2 |  |  |  | 2 |  | No
Food Service - Cafeteria/fast-food dining | 33 | 0.15 |  |  |  | 2 |  | No
Food Service - Kitchen (cooking) | 3 | 0.15 |  |  | 0.7 | 2 |  | Yes
Food Service - Restaurant dining rooms | 33 | 0.15 |  |  |  | 2 |  | No
General - Break rooms | 33 | 0.15 |  |  |  | 1 | F | No
General - Coffee Stations | 33 | 0.15 |  |  |  | 1 | F | No
General - Conference/meeting | 33 | 0.15 |  |  |  | 1 | F | No
General - Corridors | 5 | 0.15 |  |  |  | 1 | F | No
General - Occupiable storage rooms for liquids or gels | 2 | 0.15 |  |  |  | 2 | B | Yes
General - Unoccupied | [5 empty] | 1 |  | No
Lodging - Barracks sleeping areas | 5 | 0.15 |  |  |  | 1 | F | No
Lodging - Bedroom/living room | 3 | 0.15 |  |  |  | 1 | F | No
Lodging - Laundry rooms within dwelling units | 5 | 0.15 |  |  |  | 1 |  | No
Lodging - Laundry rooms, central | 5 | 0.15 |  |  |  | 2 |  | No
Lodging - Lobbies/pre-function | 33 | 0.15 |  |  |  | 1 | F | No
Lodging - Multipurpose assembly | 33 | 0.15 |  |  |  | 1 | F | No
Misc - All others | 5 | 0.15 |  |  |  | 2 |  | No
Misc - Bank vaults/safe deposit | 5 | 0.15 |  |  |  | 2 | F | No
Misc - Banks or bank lobbies | 5 | 0.15 |  |  |  | 1 | F | No
Misc - Computer (not printing) | 5 | 0.15 |  |  |  | 1 | F | Yes
Misc - Freezer and refrigerated spaces (<50F) | 0 | 0 |  |  |  | 2 | E | No
Misc - General manufacturing (excludes heavy industrial and process using chemicals) | 5 | 0.15 |  |  |  | 3 |  | Yes
Misc - Pharmacy (preparation area) | 5 | 0.15 |  |  |  | 2 |  | No
Misc - Photo studios | 5 | 0.15 |  |  |  | 1 |  | No
Misc - Shipping/receiving | 5 | 0.15 |  |  |  | 2 | B | No
Misc - Sorting, packing, light assembly | 5 | 0.15 |  |  |  | 2 |  | No
Misc - Telephone closets | 5 | 0.15 |  |  |  | 1 |  | No
Misc - Transportation waiting | 33 | 0.15 |  |  |  | 1 | F | No
Misc - Warehouses | 1 | 0.15 |  |  |  | 2 | B | No
Office - Breakrooms | 33 | 0.15 |  |  |  | 1 |  | No
Office - Main entry lobbies | 33 | 0.15 |  |  |  | 1 | F | No
Office - Occupiable storage rooms for dry materials | 2 | 0.15 |  |  |  | 1 |  | No
Office - Office space | 5 | 0.15 |  |  |  | 1 | F | No
Office - Reception areas | 5 | 0.15 |  |  |  | 1 | F | No
Office - Telephone/data entry | 33 | 0.15 |  |  |  | 1 | F | No
Residential - Common corridors | 5 | 0.15 |  |  |  | 1 | F | No
Retail - Barbershop | 17 | 0.4 |  |  | 0.5 | 2 | F | No
Retail - Beauty and nail salons | 17 | 0.4 |  |  | 0.6 | 2 |  | No
Retail - Coin-operated laundries | 17 | 0.3 |  |  |  | 2 |  | No
Retail - Mall common areas | 17 | 0.15 |  |  |  | 1 | F | No
Retail - Pet shops (animal areas) | 17 | 0.2 |  |  | 0.9 | 2 |  | No
Retail - Sales | 17 | 0.2 |  |  |  | 2 |  | No
Retail - Supermarket | 17 | 0.2 |  |  |  | 1 | F | No
Sports/Entertainment - Bowling alley (seating) | 7 | 0.15 |  |  |  | 1 |  | No
Sports/Entertainment - Disco/dance floors | 100 | 0.15 |  |  |  | 2 | F | No
Sports/Entertainment - Gambling casinos | 45 | 0.15 |  |  |  | 1 |  | No
Sports/Entertainment - Game arcades | 45 | 0.15 |  |  |  | 1 |  | No
Sports/Entertainment - Gym, sports arena (play area) | 10 | 0.15 |  |  |  | 2 | E | No
Sports/Entertainment - Health club/aerobics room | 10 | 0.15 |  |  |  | 2 |  | No
Sports/Entertainment - Health club/weight rooms | 10 | 0.15 |  |  |  | 2 |  | No
Sports/Entertainment - Spectator areas | 33 | 0.15 |  |  |  | 1 | F | No
Sports/Entertainment - Stages, studios | 33 | 0.15 |  |  |  | 1 | D, F | No
Sports/Entertainment - Swimming (deck) | 33 | 0.15 |  |  |  | 2 | C | No
Sports/Entertainment - Swimming (pool) | 10 | 0.15 |  |  |  | 2 | C | No
NA | 0 | 0 |  |  |  | 0 | 0 | Yes