## Stations
Station Information | [13 empty] | Annual Heating and Humidification Design Conditions | [15 empty] | Annual Cooling, Dehumidification, and Enthalpy Design Conditions | [31 empty] | Extreme Annual Design Conditions | [26 empty] | Temperatures, Degree-Days, and Degree-Hours | [103 empty] | Wind Speed | [12 empty] | Precipitation | [51 empty] | Monthly Design Dry Bulb and Mean Coincident Wet Bulb Temperatures | [95 empty] | Monthly Design Wet Bulb and Mean Coincident Dry Bulb Temperatures | [95 empty] | Mean Daily Temperature Range | [59 empty] | Clear-Sky Solar Irradiance | [47 empty] | All-Sky Solar Radiation | [23 empty] | Historical Trends
Region | Country | Prov State | Station Name | WMO | WBAN | Lat | Lon | Elev | StdP | TZ Offset | TZ Code | Period | Climate Zone | Coldest Month | Heating DB |  | Humidification DP/MCDB and HR | [5 empty] | Coldest Month WS/MCDB |  |  |  | MCWS/PCWD to 99.6% DB |  | Wind Shelter Factor | Hottest Month | Hottest Month DB Range | Cooling DB/MCWB | [5 empty] | Evaporation WB/MCDB | [5 empty] | MCWS/PCWD to 0.4% DB |  | Dehumidification DP/MCDB and HR | [8 empty] | Enthalpy/MCDB | [5 empty] | Extreme Max WB | Extreme Annual WS |  |  | Extreme Annual DB |  |  |  | n-Year Return Period Values of Extreme DB | [7 empty] | Extreme Annual WB |  |  |  | n-Year Return Period Values of Extreme WB | [7 empty] | Average Daily Temperature | [12 empty] | Standard Deviation of Average Daily Temperature | [12 empty] | Heating Degree Days 50°F (HDD50) | [12 empty] | Heating Degree Days 65°F (HDD65) | [12 empty] | Cooling Degree Days 50°F (CDD50) | [12 empty] | Cooling Degree Days 65°F (CDD65) | [12 empty] | Cooling Degree Hours 74°F (CDH74) | [12 empty] | Cooling Degree Hours 80°F (CDH80) | [12 empty] | Average Wind Speed | [12 empty] | Average Precipitation | [12 empty] | Maximum Precipitation | [12 empty] | Minimum Precipitation | [12 empty] | Standard Deviation of Precipitation | [12 empty] | 0.4% Monthly Design Dry Bulb Temperature | [11 empty] | Mean Wet Bulb Coincident with 0.4% Monthly Design Dry Bulb Temperature | [11 empty] | 2% Monthly Design Dry Bulb Temperature | [11 empty] | Mean Wet Bulb Coincident with 2% Monthly Design Dry Bulb Temperature | [11 empty] | 5% Monthly Design Dry Bulb Temperature | [11 empty] | Mean Wet Bulb Coincident with 5% Monthly Design Dry Bulb Temperature | [11 empty] | 10% Monthly Design Dry Bulb Temperature | [11 empty] | Mean Wet Bulb Coincident with 10% Monthly Design Dry Bulb Temperature | [11 empty] | 0.4% Monthly Design Wet Bulb Temperature | [11 empty] | Mean Dry Bulb Coincident with 0.4% Monthly Design Wet Bulb Temperature | [11 empty] | 2% Monthly Design Wet Bulb Temperature | [11 empty] | Mean Dry Bulb Coincident with 2% Monthly Design Wet Bulb Temperature | [11 empty] | 5% Monthly Design Wet Bulb Temperature | [11 empty] | Mean Dry Bulb Coincident with 5% Monthly Design Wet Bulb Temperature | [11 empty] | 10% Monthly Design Wet Bulb Temperature | [11 empty] | Mean Dry Bulb Coincident with 10% Monthly Design Wet Bulb Temperature | [11 empty] | Mean Daily Dry Bulb Temperature Range | [11 empty] | Mean Daily Dry Bulb Temperature Range Coincident with 5% Design Dry Bulb Temperature | [11 empty] | Mean Daily Wet Bulb Temperature Range Coincident with 5% Design Dry Bulb Temperature | [11 empty] | Mean Daily Dry Bulb Temperature Range Coincident with 5% Design Wet Bulb Temperature | [11 empty] | Mean Daily Wet Bulb Temperature Range Coincident with 5% Design Wet Bulb Temperature | [11 empty] | Clear-Sky Optical Depth for Beam Irradiance (taub) | [11 empty] | Clear-Sky Optical Depth for Diffuse Irradiance (taud) | [11 empty] | Clear-Sky Noon Beam Normal Irradiance on 21st Day | [11 empty] | Clear-Sky Noon Diffuse Horizontal Irradiance on 21st Day | [11 empty] | All-Sky Average Monthly Global Horizontal Radiation | [11 empty] | All-Sky Standard Deviation of Monthly Global Horizontal Radiation | [11 empty] | Station Only | [9 empty] | Regional
[17 empty] | 99.6% |  |  | 99.0% |  |  | 0.4% |  | 1% | [6 empty] | 0.4% |  | 1% |  | 2% |  | 0.4% |  | 1% |  | 2% |  |  |  | 0.4% |  |  | 1% |  |  | 2% |  |  | 0.4% |  | 1% |  | 2% | [5 empty] | Mean |  | Standard Deviation |  | n=5 years |  | n=10 years |  | n=20 years |  | n=50 years |  | Mean |  | Standard Deviation |  | n=5 years |  | n=10 years |  | n=20 years |  | n=50 years | [494 empty] | DBAvg | Heating |  | Cooling |  |  | Degree-Days |  |  |  | DBAvg | Heating |  | Cooling |  |  | Degree-Days |  |  |  | Neighbors
[15 empty] | 99.6% | 99.0% | DP | HR | MCDB | DP | HR | MCDB | WS | MCDB | WS | MCDB | MCWS | PCWD |  |  |  | DB | MCWB | DB | MCWB | DB | MCWB | WB | MCDB | WB | MCDB | WB | MCDB | MCWS | PCWD | DP | HR | MCDB | DP | HR | MCDB | DP | HR | MCDB | Enth | MCDB | Enth | MCDB | Enth | MCDB |  | 1% | 2.5% | 5% | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Annual | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Annual | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Annual | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Annual | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Annual | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Annual | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Annual | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Annual | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Annual | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Annual | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Annual | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Annual | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Annual | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  | 99% DB | 99% DP | 1% DB | 1% WB | 1% DP | HDD50 | HDD65 | CDD60 | CDD65 |  | 99% DB | 99% DP | 1% DB | 1% WB | 1% DP | HDD50 | HDD65 | CDD60 | CDD65
Region | Country | Prov_State | Station_Name | WMO | WBAN | Lat | Lon | Elev | StdP | TZ_Offset | TZ_Code | Period | Climate_Zone | Coldest_Month | DB996 | DB990 | DP996 | HR_DP996 | MCDB_DP996 | DP990 | HR_DP996 | MCDB_DP990 | WS004 | MCDB_WS004 | WS010 | MCDB_WS010 | MCWS_DB996 | PCWC_DB996 | WSF | Hottest_Month | MDBR_HM | DB004 | MCWB_DB004 | DB010 | MCWB_DB010 | DB020 | MCWB_DB020 | WB004 | MCDB_WB004 | WB010 | MCDB_WB010 | WB020 | MCDB_WB020 | MCWS_DB004 | PCWD_DB004 | DP004 | HR_DP004 | MCDB_DP004 | DP010 | HR_DP010 | MCDB_DP010 | DP020 | HR_DP020 | MCDB_DP020 | Enth004 | MCDB_Enth004 | Enth010 | MCDB_Enth010 | Enth020 | MCDB_Enth020 | WBExtMax | WSExt010 | WSExt025 | WSExt_050 | DBMeanMin | DBMeanMax | DBStdDevMeanMin | DBStdDevMeanMax | DB5yrMin | DB5yrMax | DB10yrMin | DB10yrMax | DB20yrMin | DB20yrMax | DB50yrMin | DB50yrMax | WBMeanMin | WBStdDevMeanMax | WBStdDevMeanMin | WBMeanMax | WB5yrMin | WB5yrMax | WB10yrMin | WB10yrMax | WB20yrMin | WB20yrMax | WB50yrMin | WB50yrMax | DBAvg_Yr | DBAvg_Jan | DBAvg_Feb | DBAvg_Mar | DBAvg_Apr | DBAvg_May | DBAvg_Jun | DBAvg_Jul | DBAvg_Aug | DBAvg_Sep | DBAvg_Oct | DBAvg_Nov | DBAvg_Dec | DBStdDev_Yr | DBStdDev_Jan | DBStdDev_Feb | DBStdDev_Mar | DBStdDev_Apr | DBStdDev_May | DBStdDev_Jun | DBStdDev_Jul | DBStdDev_Aug | DBStdDev_Sep | DBStdDev_Oct | DBStdDev_Nov | DBStdDev_Dec | HDD50_Yr | HDD50_Jan | HDD50_Feb | HDD50_Mar | HDD50_Apr | HDD50_May | HDD50_Jun | HDD50_Jul | HDD50_Aug | HDD50_Sep | HDD50_Oct | HDD50_Nov | HDD50_Dec | HDD65_Yr | HDD65_Jan | HDD65_Feb | HDD65_Mar | HDD65_Apr | HDD65_May | HDD65_Jun | HDD65_Jul | HDD65_Aug | HDD65_Sep | HDD65_Oct | HDD65_Nov | HDD65_Dec | CDD50_Yr | CDD50_Jan | CDD50_Feb | CDD50_Mar | CDD50_Apr | CDD50_May | CDD50_Jun | CDD50_Jul | CDD50_Aug | CDD50_Sep | CDD50_Oct | CDD50_Nov | CDD50_Dec | CDD65_Yr | CDD65_Jan | CDD65_Feb | CDD65_Mar | CDD65_Apr | CDD65_May | CDD65_Jun | CDD65_Jul | CDD65_Aug | CDD65_Sep | CDD65_Oct | CDD65_Nov | CDD65_Dec | CDD74_Yr | CDD74_Jan | CDD74_Feb | CDD74_Mar | CDD74_Apr | CDD74_May | CDD74_Jun | CDD74_Jul | CDD74_Aug | CDD74_Sep | CDD74_Oct | CDD74_Nov | CDD74_Dec | CDH80_Yr | CDH80_Jan | CDH80_Feb | CDH80_Mar | CDH80_Apr | CDH80_May | CDH80_Jun | CDH80_Jul | CDH80_Aug | CDH80_Sep | CDH80_Oct | CDH80_Nov | CDH80_Dec | WSAvg_Yr | WSAvg_Jan | WSAvg_Feb | WSAvg_Mar | WSAvg_Apr | WSAvg_May | WSAvg_Jun | WSAvg_Jul | WSAvg_Aug | WSAvg_Sep | WSAvg_Oct | WSAvg_Nov | WSAvg_Dec | PrecipAvg_Yr | PrecipAvg_Jan | PrecipAvg_Feb | PrecipAvg_Mar | PrecipAvg_Apr | PrecipAvg_May | PrecipAvg_Jun | PrecipAvg_Jul | PrecipAvg_Aug | PrecipAvg_Sep | PrecipAvg_Oct | PrecipAvg_Nov | PrecipAvg_Dec | PrecipMax_Yr | PrecipMax_Jan | PrecipMax_Feb | PrecipMax_Mar | PrecipMax_Apr | PrecipMax_May | PrecipMax_Jun | PrecipMax_Jul | PrecipMax_Aug | PrecipMax_Sep | PrecipMax_Oct | PrecipMax_Nov | PrecipMax_Dec | PrecipMin_Yr | PrecipMin_Jan | PrecipMin_Feb | PrecipMin_Mar | PrecipMin_Apr | PrecipMin_May | PrecipMin_Jun | PrecipMin_Jul | PrecipMin_Aug | PrecipMin_Sep | PrecipMin_Oct | PrecipMin_Nov | PrecipMin_Dec | PrecipStdDev_Yr | PrecipStdDev_Jan | PrecipStdDev_Feb | PrecipStdDev_Mar | PrecipStdDev_Apr | PrecipStdDev_May | PrecipStdDev_Jun | PrecipStdDev_Jul | PrecipStdDev_Aug | PrecipStdDev_Sep | PrecipStdDev_Oct | PrecipStdDev_Nov | PrecipStdDev_Dec | DB004_Jan | DB004_Feb | DB004_Mar | DB004_Apr | DB004_May | DB004_Jun | DB004_Jul | DB004_Aug | DB004_Sep | DB004_Oct | DB004_Nov | DB004_Dec | MCWB_DB004_Jan | MCWB_DB004_Feb | MCWB_DB004_Mar | MCWB_DB004_Apr | MCWB_DB004_May | MCWB_DB004_Jun | MCWB_DB004_Jul | MCWB_DB004_Aug | MCWB_DB004_Sep | MCWB_DB004_Oct | MCWB_DB004_Nov | MCWB_DB004_Dec | DB020_Jan | DB020_Feb | DB020_Mar | DB020_Apr | DB020_May | DB020_Jun | DB020_Jul | DB020_Aug | DB020_Sep | DB020_Oct | DB020_Nov | DB020_Dec | MCWB_DB020_Jan | MCWB_DB020_Feb | MCWB_DB020_Mar | MCWB_DB020_Apr | MCWB_DB020_May | MCWB_DB020_Jun | MCWB_DB020_Jul | MCWB_DB020_Aug | MCWB_DB020_Sep | MCWB_DB020_Oct | MCWB_DB020_Nov | MCWB_DB020_Dec | DB050_Jan | DB050_Feb | DB050_Mar | DB050_Apr | DB050_May | DB050_Jun | DB050_Jul | DB050_Aug | DB050_Sep | DB050_Oct | DB050_Nov | DB050_Dec | MCWB_DB050_Jan | MCWB_DB050_Feb | MCWB_DB050_Mar | MCWB_DB050_Apr | MCWB_DB050_May | MCWB_DB050_Jun | MCWB_DB050_Jul | MCWB_DB050_Aug | MCWB_DB050_Sep | MCWB_DB050_Oct | MCWB_DB050_Nov | MCWB_DB050_Dec | DB100_Jan | DB100_Feb | DB100_Mar | DB100_Apr | DB100_May | DB100_Jun | DB100_Jul | DB100_Aug | DB100_Sep | DB100_Oct | DB100_Nov | DB100_Dec | MCWB_DB100_Jan | MCWB_DB100_Feb | MCWB_DB100_Mar | MCWB_DB100_Apr | MCWB_DB100_May | MCWB_DB100_Jun | MCWB_DB100_Jul | MCWB_DB100_Aug | MCWB_DB100_Sep | MCWB_DB100_Oct | MCWB_DB100_Nov | MCWB_DB100_Dec | WB004_Jan | WB004_Feb | WB004_Mar | WB004_Apr | WB004_May | WB004_Jun | WB004_Jul | WB004_Aug | WB004_Sep | WB004_Oct | WB004_Nov | WB004_Dec | MCDB_WB004_Jan | MCDB_WB004_Feb | MCDB_WB004_Mar | MCDB_WB004_Apr | MCDB_WB004_May | MCDB_WB004_Jun | MCDB_WB004_Jul | MCDB_WB004_Aug | MCDB_WB004_Sep | MCDB_WB004_Oct | MCDB_WB004_Nov | MCDB_WB004_Dec | WB020_Jan | WB020_Feb | WB020_Mar | WB020_Apr | WB020_May | WB020_Jun | WB020_Jul | WB020_Aug | WB020_Sep | WB020_Oct | WB020_Nov | WB020_Dec | MCDB_WB020_Jan | MCDB_WB020_Feb | MCDB_WB020_Mar | MCDB_WB020_Apr | MCDB_WB020_May | MCDB_WB020_Jun | MCDB_WB020_Jul | MCDB_WB020_Aug | MCDB_WB020_Sep | MCDB_WB020_Oct | MCDB_WB020_Nov | MCDB_WB020_Dec | WB050_Jan | WB050_Feb | WB050_Mar | WB050_Apr | WB050_May | WB050_Jun | WB050_Jul | WB050_Aug | WB050_Sep | WB050_Oct | WB050_Nov | WB050_Dec | MCDB_WB050_Jan | MCDB_WB050_Feb | MCDB_WB050_Mar | MCDB_WB050_Apr | MCDB_WB050_May | MCDB_WB050_Jun | MCDB_WB050_Jul | MCDB_WB050_Aug | MCDB_WB050_Sep | MCDB_WB050_Oct | MCDB_WB050_Nov | MCDB_WB050_Dec | WB100_Jan | WB100_Feb | WB100_Mar | WB100_Apr | WB100_May | WB100_Jun | WB100_Jul | WB100_Aug | WB100_Sep | WB100_Oct | WB100_Nov | WB100_Dec | MCDB_WB100_Jan | MCDB_WB100_Feb | MCDB_WB100_Mar | MCDB_WB100_Apr | MCDB_WB100_May | MCDB_WB100_Jun | MCDB_WB100_Jul | MCDB_WB100_Aug | MCDB_WB100_Sep | MCDB_WB100_Oct | MCDB_WB100_Nov | MCDB_WB100_Dec | MDBR_Jan | MDBR_Feb | MDBR_Mar | MDBR_Apr | MDBR_May | MDBR_Jun | MDBR_Jul | MDBR_Aug | MDBR_Sep | MDBR_Oct | MDBR_Nov | MDBR_Dec | MDBR_DB050_Jan | MDBR_DB050_Feb | MDBR_DB050_Mar | MDBR_DB050_Apr | MDBR_DB050_May | MDBR_DB050_Jun | MDBR_DB050_Jul | MDBR_DB050_Aug | MDBR_DB050_Sep | MDBR_DB050_Oct | MDBR_DB050_Nov | MDBR_DB050_Dec | MWBR_DB050_Jan | MWBR_DB050_Feb | MWBR_DB050_Mar | MWBR_DB050_Apr | MWBR_DB050_May | MWBR_DB050_Jun | MWBR_DB050_Jul | MWBR_DB050_Aug | MWBR_DB050_Sep | MWBR_DB050_Oct | MWBR_DB050_Nov | MWBR_DB050_Dec | MCDB_WB050_Jan | MCDB_WB050_Feb | MCDB_WB050_Mar | MCDB_WB050_Apr | MCDB_WB050_May | MCDB_WB050_Jun | MCDB_WB050_Jul | MCDB_WB050_Aug | MCDB_WB050_Sep | MCDB_WB050_Oct | MCDB_WB050_Nov | MCDB_WB050_Dec | MWBR_WB050_Jan | MWBR_WB050_Feb | MWBR_WB050_Mar | MWBR_WB050_Apr | MWBR_WB050_May | MWBR_WB050_Jun | MWBR_WB050_Jul | MWBR_WB050_Aug | MWBR_WB050_Sep | MWBR_WB050_Oct | MWBR_WB050_Nov | MWBR_WB050_Dec | Taub_Jan | Taub_Feb | Taub_Mar | Taub_Apr | Taub_May | Taub_Jun | Taub_Jul | Taub_Aug | Taub_Sep | Taub_Oct | Taub_Nov | Taub_Dec | Taud_Jan | Taud_Feb | Taud_Mar | Taud_Apr | Taud_May | Taud_Jun | Taud_Jul | Taud_Aug | Taud_Sep | Taud_Oct | Taud_Nov | Taud_Dec | DNINoon_Jan | DNINoon_Feb | DNINoon_Mar | DNINoon_Apr | DNINoon_May | DNINoon_Jun | DNINoon_Jul | DNINoon_Aug | DNINoon_Sep | DNINoon_Oct | DNINoon_Nov | DNINoon_Dec | DHINoon_Jan | DHINoon_Feb | DHINoon_Mar | DHINoon_Apr | DHINoon_May | DHINoon_Jun | DHINoon_Jul | DHINoon_Aug | DHINoon_Sep | DHINoon_Oct | DHINoon_Nov | DHINoon_Dec | GHRAvg_Jan | GHRAvg_Feb | GHRAvg_Mar | GHRAvg_Apr | GHRAvg_May | GHRAvg_Jun | GHRAvg_Jul | GHRAvg_Aug | GHRAvg_Sep | GHRAvg_Oct | GHRAvg_Nov | GHRAvg_Dec | GHRStdDev_Jan | GHRStdDev_Feb | GHRStdDev_Mar | GHRStdDev_Apr | GHRStdDev_May | GHRStdDev_Jun | GHRStdDev_Jul | GHRStdDev_Aug | GHRStdDev_Sep | GHRStdDev_Oct | GHRStdDev_Nov | GHRStdDev_Dec | StDBAvg | StHtgDB990 | StHtgDP990 | StClgDB010 | StClgWB010 | StClgDP010 | StHDD50 | StHDD65 | StCDD60 | StCDD65 | RegDBAvg | RegHtgDB990 | RegHtgDP990 | RegClgDB010 | RegClgWB010 | RegClgDP010 | RegHDD50 | RegHDD65 | RegCDD60 | RegCDD65 | Neighbors
4 | USA | CA | AUBURN | 720267 | 23224 | 38.955 | -121.082 | 1531 | 13.9 | -8 | NAP | 04-19 | 3A | 12 | 32 | 34.1 | 15.8 | 13 | 48.7 | 19.1 | 15.2 | 47 | 19.7 | 47.4 | 17.7 | 48.6 | 2.5 | 100 | 0.422 | 7 | 24.5 | 98.8 | 66.9 | 95 | 65.2 | 92.5 | 64.6 | 69.3 | 92.1 | 67.9 | 89.8 | 66.4 | 87.8 | 6.1 | 260 | 61.5 | 86.2 | 76.9 | 59.4 | 80 | 76.4 | 57.2 | 73.9 | 73.4 | 34.2 | 91.6 | 32.9 | 90.1 | 31.7 | 87.7 | 82 | 15.6 | 12.6 | 11 | 27.2 | 103.9 | 3.5 | 6.4 | 24.6 | 108.5 | 22.6 | 112.2 | 20.6 | 115.8 | 18 | 120.4 | 25.3 | 72.4 | 2.9 | 3.4 | 23.1 | 74.8 | 21.4 | 76.7 | 19.8 | 78.6 | 17.6 | 81.1 | 61 | 47.3 | 49 | 52.4 | 55.8 | 63.1 | 71.8 | 78.8 | 77.6 | 72.9 | 62.7 | 53.3 | 46.1 | 13.19 | 5.45 | 6.23 | 6.49 | 7.24 | 7.39 | 7.81 | 5.66 | 5.4 | 7.39 | 6.9 | 6.42 | 5.08 | 456 | 117 | 86 | 49 | 22 | 2 | 0 | 0 | 0 | 0 | 1 | 37 | 142 | 2916 | 547 | 449 | 393 | 291 | 125 | 26 | 0 | 0 | 19 | 126 | 353 | 587 | 4462 | 35 | 58 | 123 | 195 | 408 | 655 | 892 | 857 | 687 | 396 | 136 | 20 | 1447 | 0 | 0 | 2 | 15 | 67 | 231 | 427 | 392 | 256 | 55 | 2 | 0 | 16844 | 1 | 7 | 16 | 139 | 751 | 2843 | 5287 | 4567 | 2705 | 508 | 20 | 0 | 8098 | 0 | 1 | 1 | 20 | 226 | 1317 | 2813 | 2318 | 1274 | 127 | 1 | 0 | 5 | 4.2 | 5.4 | 5.7 | 5.7 | 5.5 | 5.2 | 5.3 | 5 | 4.9 | 4.3 | 4 | 4.3 | 35.4 | 6.2 | 5.2 | 5.7 | 2.7 | 0.7 | 0.3 | 0 | 0.2 | 0.7 | 2.3 | 5.9 | 5.4 | 64.9 | 17 | 17.6 | 15.3 | 7.7 | 2.8 | 1.1 | 0.9 | 1.6 | 3.7 | 13.9 | 13.5 | 14.2 | 11.8 | 0.5 | 0.3 | 1.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 11.9 | 4.3 | 4.1 | 3.6 | 2.3 | 0.7 | 0.3 | 0.2 | 0.4 | 1.1 | 2.8 | 3.8 | 3.7 | 69.8 | 71.9 | 75.4 | 82.2 | 90.6 | 99.8 | 102.1 | 100.1 | 98.8 | 89.8 | 77 | 64.2 | 51.3 | 56.1 | 58.7 | 62.8 | 65.9 | 68.4 | 69.6 | 66.1 | 65.1 | 61.6 | 57.8 | 49.8 | 64 | 66.5 | 72.1 | 78.9 | 84.5 | 95.4 | 98.8 | 97.1 | 93.1 | 82.4 | 72.8 | 61.1 | 49.9 | 53.6 | 56.7 | 60.8 | 62.9 | 66.6 | 67.5 | 65 | 62.8 | 59.2 | 56 | 49.6 | 61.2 | 63.6 | 68.3 | 73.1 | 81.8 | 91 | 95.2 | 93.1 | 90.7 | 79.5 | 69.8 | 57.1 | 49.5 | 51.2 | 54.8 | 57.6 | 61.2 | 64.6 | 65.6 | 64.6 | 62.5 | 57.3 | 54.6 | 48.7 | 56.7 | 60.6 | 64 | 69.8 | 78.7 | 88.1 | 91.5 | 90.7 | 88.2 | 75.3 | 63.8 | 54.7 | 48.3 | 50 | 52.5 | 56.5 | 59.9 | 63.4 | 65.1 | 63.7 | 61.9 | 56.4 | 52.3 | 48.8 | 55.4 | 58 | 60.3 | 65.3 | 67.8 | 71.8 | 72.8 | 68.8 | 67 | 64.2 | 62.4 | 56.7 | 59.9 | 63.6 | 72.9 | 79.4 | 85.7 | 94.4 | 97.8 | 93.3 | 86.1 | 78.6 | 72.4 | 58.3 | 53.7 | 55.5 | 57.8 | 62.1 | 65.3 | 69.2 | 69.5 | 67.4 | 65.2 | 62 | 58.8 | 54.3 | 58.6 | 63.9 | 68.8 | 75.6 | 83.3 | 89.9 | 93.7 | 91.3 | 88.1 | 78.8 | 67.6 | 55.8 | 51.9 | 53.5 | 55.7 | 59.3 | 63 | 67.1 | 68.2 | 66.1 | 63.8 | 60.1 | 56.4 | 52.4 | 56.2 | 59.8 | 65.1 | 71.1 | 77.9 | 87 | 91.4 | 89.8 | 87 | 74.5 | 64.4 | 54.3 | 50.1 | 51.8 | 53.8 | 57.1 | 61 | 65.2 | 66.6 | 64.9 | 62.3 | 58.2 | 54.3 | 50.1 | 55.8 | 57.4 | 62 | 67.4 | 75.3 | 83.4 | 88.7 | 87.8 | 84.8 | 71 | 61.2 | 54.1 | 15.5 | 16.1 | 16.6 | 18.4 | 21 | 24.1 | 24.5 | 24.3 | 23.2 | 20.4 | 17.1 | 15.1 | 22 | 22.3 | 21.8 | 22.8 | 24.6 | 26.9 | 25.7 | 25 | 24.9 | 24 | 22.9 | 19 | 13.1 | 14 | 13.3 | 13.4 | 12 | 11 | 10.1 | 10.4 | 11.2 | 11.3 | 12.3 | 11.6 | 17.4 | 18.6 | 19.3 | 20.9 | 23 | 24.8 | 24.2 | 24 | 23.7 | 20.5 | 19.3 | 12.3 | 11.8 | 12.5 | 12.3 | 12.9 | 11.7 | 10.8 | 9.9 | 10.3 | 10.9 | 10.5 | 11.7 | 9.2 | 0.309 | 0.31 | 0.338 | 0.342 | 0.357 | 0.349 | 0.348 | 0.332 | 0.341 | 0.332 | 0.31 | 0.323 | 2.514 | 2.525 | 2.433 | 2.424 | 2.404 | 2.441 | 2.443 | 2.478 | 2.459 | 2.483 | 2.525 | 2.45 | 276 | 292 | 292 | 296 | 292 | 293 | 293 | 296 | 287 | 279 | 273 | 259 | 24 | 27 | 33 | 36 | 37 | 36 | 36 | 33 | 32 | 28 | 24 | 24 | 702 | 997 | 1417 | 1881 | 2300 | 2622 | 2616 | 2347 | 1892 | 1327 | 843 | 613 | 119 | 138 | 167 | 181 | 165 | 121 | 91 | 81 | 72 | 96 | 67 | 105 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.72 | N/A | -1.96 | N/A | N/A | N/A | N/A | -205 | 248 | 76 | 41
4 | USA | CA | EL CENTRO NAF | 722810 | 23199 | 32.817 | -115.683 | -42 | 14.72 | -8 | NAP | 06-19 | 2B | 12 | 35.5 | 38.5 | 3.6 | 6.6 | 57.7 | 7.8 | 8.2 | 61 | 31.5 | 62.4 | 27.2 | 64.4 | 5 | 260 | 0.487 | 8 | 27.1 | 111.9 | 70.7 | 109.6 | 70.5 | 107.6 | 70.3 | 78.9 | 95.1 | 77.8 | 94.9 | 76.8 | 94.8 | 7 | 140 | 75.1 | 131.7 | 86.4 | 73.3 | 123.7 | 86.7 | 71.2 | 114.9 | 88 | 42.3 | 94.6 | 41.2 | 94.4 | 40 | 94.9 | 82.9 | 29.3 | 25.9 | 22.3 | 30.1 | 117 | 3.6 | 1.8 | 27.5 | 118.3 | 25.4 | 119.3 | 23.4 | 120.3 | 20.8 | 121.6 | 24.6 | 81.1 | 2.9 | 1.2 | 22.5 | 81.9 | 20.8 | 82.6 | 19.2 | 83.3 | 17.1 | 84.2 | 74.5 | 56.7 | 60.5 | 67.2 | 72.5 | 78.1 | 87.5 | 93.2 | 93.4 | 87.5 | 75.8 | 65.2 | 55.4 | 14.28 | 5.47 | 5.7 | 6.19 | 6.06 | 6.26 | 5.2 | 3.48 | 3.64 | 5.76 | 5.72 | 6.11 | 5.08 | 29 | 14 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 11 | 842 | 260 | 143 | 50 | 10 | 1 | 0 | 0 | 0 | 0 | 4 | 74 | 300 | 8962 | 221 | 297 | 533 | 675 | 870 | 1124 | 1340 | 1345 | 1125 | 798 | 456 | 178 | 4302 | 2 | 17 | 119 | 235 | 406 | 674 | 875 | 880 | 675 | 338 | 79 | 2 | 66996 | 136 | 473 | 1770 | 3190 | 5695 | 10746 | 14658 | 14686 | 10258 | 4211 | 1106 | 67 | 43102 | 8 | 101 | 712 | 1563 | 3328 | 7302 | 10350 | 10387 | 6725 | 2226 | 398 | 2 | 7.9 | 5.9 | 7.6 | 8.9 | 10.8 | 11 | 9.1 | 7.7 | 6.9 | 7.1 | 7.4 | 6.4 | 6.3 | 2.5 | 0.5 | 0.5 | 0.3 | 0.1 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 5.9 | 3.5 | 2.5 | 1.9 | 0.6 | 0.6 | 0.2 | 0.9 | 0.9 | 1.4 | 1.1 | 1 | 1.3 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 0.8 | 0.6 | 0.4 | 0.1 | 0.1 | 0 | 0.2 | 0.3 | 0.3 | 0.4 | 0.3 | 0.4 | 80.8 | 86.6 | 94.5 | 100.4 | 106.8 | 115.3 | 114.3 | 114.1 | 110.6 | 101.6 | 91.4 | 79.4 | 54.4 | 57.5 | 60.4 | 62.9 | 64.7 | 68.3 | 70.8 | 71 | 69.9 | 65 | 60.7 | 57.2 | 77.8 | 83.1 | 90.7 | 96.1 | 102.4 | 110.7 | 111.3 | 111.6 | 107.6 | 97.4 | 88.4 | 75.8 | 53.7 | 56.6 | 59.4 | 61.7 | 64 | 68 | 71.6 | 71.3 | 69.5 | 63.6 | 59.2 | 54.4 | 74.8 | 80 | 87.5 | 92.5 | 99.2 | 107.6 | 109.1 | 109.3 | 105.5 | 94.7 | 85 | 72.3 | 52.4 | 56.1 | 57.9 | 60.2 | 63.6 | 67.6 | 71.5 | 71.4 | 69.4 | 62.8 | 58.4 | 52.7 | 71.5 | 76.3 | 84 | 89 | 95.6 | 104.4 | 106.9 | 106.9 | 102.7 | 91.7 | 80.9 | 68.7 | 52.3 | 54.5 | 57.2 | 59.4 | 62.6 | 67.3 | 71.4 | 71.6 | 69.4 | 62.4 | 57.2 | 51.4 | 59.9 | 62 | 62.8 | 66.4 | 69.2 | 76.4 | 79.6 | 80.6 | 79.7 | 72.8 | 63.9 | 61.3 | 70.8 | 79.9 | 88.4 | 92.1 | 95.8 | 97.8 | 97.1 | 95 | 93.8 | 85.9 | 82.3 | 73.9 | 57.3 | 59 | 61.1 | 63.9 | 67.2 | 74.5 | 78.5 | 79.4 | 77.5 | 69.9 | 61.4 | 58.4 | 68.6 | 77.3 | 86.1 | 89.7 | 94.7 | 97.5 | 96.4 | 94.5 | 93.2 | 86.6 | 82.4 | 69 | 55.4 | 57 | 59.6 | 62.1 | 65.4 | 72.3 | 77.5 | 78.1 | 75.7 | 66.9 | 59.8 | 55.9 | 67.8 | 75.8 | 83.7 | 88.6 | 93.4 | 97.3 | 95.7 | 94.4 | 92.9 | 88.1 | 81.1 | 66.5 | 53.5 | 55.4 | 58.2 | 60.4 | 63.9 | 69.9 | 76.6 | 77 | 73.9 | 64.2 | 58.3 | 53.4 | 67.9 | 73.8 | 81.2 | 86.2 | 92.4 | 96.5 | 95.4 | 94.5 | 93 | 87.9 | 78.7 | 65.4 | 27.7 | 27.8 | 29 | 29.3 | 29.9 | 32.5 | 27.1 | 27.1 | 27.7 | 28.9 | 28.5 | 25.8 | 32.7 | 33.4 | 33.7 | 33.6 | 35.1 | 35.6 | 29.9 | 29.5 | 30.2 | 32.3 | 33.1 | 30.4 | 16.8 | 16.2 | 14.7 | 13.7 | 12.9 | 13.4 | 11.4 | 11.6 | 11.7 | 13.1 | 15.9 | 16.1 | 24.8 | 29.3 | 31.2 | 31.9 | 33.2 | 33.1 | 24.3 | 23.9 | 24.5 | 26.3 | 28.8 | 24.1 | 13.9 | 15.1 | 14.1 | 13.4 | 12.4 | 13.5 | 10.6 | 10.5 | 11.7 | 11.5 | 14.6 | 13.7 | 0.291 | 0.296 | 0.314 | 0.331 | 0.349 | 0.35 | 0.394 | 0.389 | 0.351 | 0.321 | 0.295 | 0.291 | 2.514 | 2.519 | 2.456 | 2.411 | 2.379 | 2.38 | 2.365 | 2.371 | 2.437 | 2.491 | 2.533 | 2.542 | 297 | 306 | 307 | 304 | 297 | 295 | 281 | 282 | 290 | 292 | 293 | 291 | 27 | 30 | 34 | 37 | 39 | 39 | 39 | 38 | 34 | 30 | 26 | 25 | 1108 | 1411 | 1875 | 2291 | 2551 | 2671 | 2427 | 2260 | 1990 | 1597 | 1211 | 1001 | 58 | 101 | 70 | 61 | 77 | 94 | 100 | 91 | 72 | 68 | 53 | 55 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.86 | N/A | -2.32 | 1.06 | N/A | N/A | N/A | -137 | 313 | 164 | 23
4 | USA | CA | MARCH AFB | 722860 | 23119 | 33.9 | -117.25 | 1536 | 13.9 | -8 | NAP | 94-19 | 3B | 12 | 31.5 | 34.4 | 1.3 | 6.2 | 60.9 | 6.6 | 8.1 | 61.6 | 24.8 | 54.8 | 20.7 | 54.6 | 1.4 | 320 | 0.435 | 8 | 31.6 | 101.4 | 67.6 | 98.8 | 66.7 | 95.8 | 66.1 | 71.9 | 93.1 | 70.5 | 91.3 | 69.2 | 89.1 | 10.4 | 300 | 66.4 | 102.9 | 75.4 | 64.2 | 95.2 | 74.2 | 63 | 91.1 | 73 | 36.5 | 92.8 | 35.2 | 90.9 | 34.1 | 89.1 | 78.8 | 17.9 | 15.7 | 13.2 | 25.4 | 107.2 | 4.5 | 2.7 | 22.2 | 109.2 | 19.5 | 110.8 | 17 | 112.3 | 13.7 | 114.3 | 22.8 | 74.6 | 4 | 1.9 | 20 | 76 | 17.7 | 77.1 | 15.4 | 78.2 | 12.5 | 79.6 | 63.9 | 52.8 | 52.8 | 56.7 | 59.7 | 65.1 | 71.6 | 77.7 | 78.9 | 75 | 66.2 | 57.8 | 51.7 | 11.17 | 5.68 | 5.81 | 5.61 | 6.17 | 6.1 | 5.52 | 4.68 | 5.11 | 6.19 | 6.01 | 6.01 | 5.45 | 138 | 36 | 33 | 9 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 46 | 1944 | 378 | 344 | 262 | 179 | 74 | 10 | 0 | 0 | 4 | 57 | 224 | 412 | 5213 | 123 | 110 | 218 | 296 | 468 | 647 | 858 | 897 | 749 | 502 | 245 | 100 | 1543 | 1 | 1 | 5 | 21 | 76 | 207 | 393 | 432 | 303 | 94 | 10 | 0 | 21579 | 94 | 119 | 325 | 696 | 1311 | 2849 | 4895 | 5438 | 3760 | 1602 | 440 | 50 | 11479 | 10 | 18 | 80 | 252 | 586 | 1478 | 2804 | 3253 | 2120 | 740 | 136 | 2 | 5.3 | 4.7 | 5 | 5 | 5.8 | 6.1 | 6 | 6 | 5.6 | 5.1 | 4.9 | 4.5 | 4.8 | 11.6 | 2.4 | 3 | 1.6 | 0.7 | 0.2 | 0.1 | 0.2 | 0.1 | 0.2 | 0.4 | 1 | 1.7 | 22.2 | 11.3 | 11.2 | 6.6 | 2.4 | 2 | 0.7 | 1.5 | 0.4 | 1.5 | 5.5 | 2.1 | 8.5 | 4.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 5.3 | 2.9 | 2.5 | 1.5 | 0.6 | 0.4 | 0.2 | 0.3 | 0.1 | 0.3 | 1 | 0.5 | 1.8 | 81.2 | 82.8 | 87.3 | 92.6 | 97.4 | 102.4 | 104 | 105.5 | 103.7 | 97.6 | 89.2 | 78.9 | 54.3 | 54.9 | 58.6 | 58.9 | 64 | 65.9 | 69.7 | 69 | 66.7 | 61.8 | 57.3 | 52.5 | 76.7 | 77.9 | 81.6 | 86.5 | 91.4 | 96.6 | 99.4 | 101.6 | 99.3 | 92.5 | 84.1 | 74.8 | 52.2 | 53.5 | 57.3 | 58 | 62.3 | 65.4 | 68 | 67.7 | 66.4 | 59.7 | 55.7 | 51 | 72.4 | 72.5 | 77.3 | 82.1 | 86.9 | 92.7 | 96.6 | 98.7 | 95.9 | 88.5 | 79.3 | 70.3 | 51.1 | 52.2 | 55.9 | 57 | 61 | 64.9 | 67.7 | 67.2 | 65.8 | 59.1 | 53.9 | 49.7 | 67.9 | 67 | 72.7 | 77.2 | 81.6 | 89.1 | 93.3 | 95.3 | 91.9 | 83.7 | 74.1 | 65.5 | 49.7 | 50.7 | 54.5 | 55.9 | 60.6 | 64.4 | 67.2 | 66.7 | 65.1 | 58.8 | 52.3 | 49 | 59.5 | 59.9 | 63.4 | 64.1 | 67.4 | 70.9 | 73.2 | 74.4 | 73 | 68.8 | 61.1 | 59.6 | 66.4 | 67.4 | 78 | 82.2 | 90.9 | 93.1 | 94 | 92 | 92.9 | 79.8 | 68.8 | 63.8 | 56.8 | 57.1 | 60.5 | 61.5 | 65.2 | 68.4 | 71.4 | 72 | 71 | 65.9 | 58.9 | 56.7 | 64.3 | 66.5 | 73.7 | 78.5 | 85.1 | 89.9 | 92.8 | 94 | 90.5 | 80.2 | 71.8 | 62.8 | 54.8 | 55.3 | 58.6 | 59.4 | 63.6 | 67 | 70.2 | 70.3 | 69.2 | 63.6 | 57.3 | 54.4 | 62.6 | 65.5 | 70.9 | 74.6 | 81.8 | 87.3 | 91 | 92.3 | 86.7 | 77.2 | 70.3 | 60.7 | 53.1 | 53.7 | 56.6 | 57.5 | 61.8 | 65.6 | 68.9 | 68.8 | 67.6 | 61.7 | 55.7 | 52.2 | 61.6 | 62.4 | 67.9 | 71.1 | 77.5 | 84.2 | 88.8 | 89.9 | 85.3 | 74.4 | 68 | 59.6 | 25.8 | 24.6 | 27 | 28.1 | 27.1 | 30.2 | 30.9 | 31.6 | 30.3 | 29.5 | 29 | 25.7 | 35.5 | 37 | 37.1 | 38.9 | 37.7 | 37.2 | 34.1 | 34.6 | 35.4 | 39.3 | 38.8 | 35.1 | 16.9 | 17.2 | 16.7 | 15.7 | 14 | 12.9 | 11.7 | 12.3 | 12.3 | 14.9 | 17.1 | 16.8 | 24.4 | 25.9 | 30.3 | 31.5 | 32.2 | 32.8 | 30.4 | 30.7 | 29.4 | 29 | 29.5 | 22.7 | 13.7 | 14.1 | 15.2 | 14 | 12.4 | 11.8 | 10.8 | 11.4 | 10.7 | 11.9 | 14.5 | 13.1 | 0.29 | 0.299 | 0.319 | 0.333 | 0.346 | 0.347 | 0.375 | 0.359 | 0.341 | 0.327 | 0.297 | 0.298 | 2.573 | 2.558 | 2.482 | 2.449 | 2.444 | 2.454 | 2.437 | 2.467 | 2.503 | 2.515 | 2.588 | 2.578 | 296 | 304 | 304 | 302 | 298 | 296 | 287 | 291 | 293 | 289 | 291 | 286 | 25 | 28 | 33 | 36 | 36 | 36 | 36 | 35 | 32 | 29 | 24 | 23 | 1033 | 1318 | 1774 | 2158 | 2370 | 2545 | 2426 | 2291 | 1960 | 1501 | 1148 | 935 | 70 | 126 | 86 | 92 | 121 | 124 | 114 | 65 | 63 | 88 | 55 | 64 | N/A | -1.89 | -3.56 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.13 | N/A | -3.04 | 1.26 | N/A | N/A | N/A | -196 | 400 | 205 | 52
4 | USA | CA | PALM SPRINGS | 722868 | 93138 | 33.822 | -116.504 | 409 | 14.48 | -8 | NAP | 98-19 | 1B | 12 | 41.2 | 43.9 | -0.1 | 5.5 | 64.6 | 4.3 | 6.9 | 66.2 | 23.3 | 61.4 | 18.9 | 61.8 | 4 | 330 | 0.442 | 7 | 25.8 | 112.4 | 70.2 | 109.7 | 70.2 | 107.8 | 69.8 | 78.3 | 97.9 | 76.9 | 97.2 | 75.3 | 97.6 | 10 | 320 | 72.8 | 123.6 | 90.4 | 70.3 | 113.4 | 90.9 | 67.1 | 101.1 | 91.8 | 42.1 | 96.9 | 40.4 | 96.9 | 38.9 | 97.5 | 89.8 | 22.9 | 19.9 | 17.8 | 35.6 | 117.5 | 3.1 | 2.7 | 33.3 | 119.4 | 31.5 | 121 | 29.7 | 122.5 | 27.4 | 124.5 | 29 | 81.3 | 2.6 | 3.7 | 27.1 | 84 | 25.6 | 86.2 | 24.2 | 88.3 | 22.3 | 91 | 75.4 | 59.2 | 61.2 | 67.4 | 72.3 | 79.5 | 88.1 | 93.9 | 93.2 | 87.7 | 77.2 | 66.3 | 57.6 | 14.15 | 6.12 | 6.57 | 7.11 | 7.18 | 7.23 | 6.27 | 4.27 | 4.34 | 6.05 | 6.54 | 6.79 | 5.52 | 12 | 6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 723 | 197 | 142 | 58 | 19 | 2 | 0 | 0 | 0 | 0 | 3 | 64 | 238 | 9275 | 290 | 314 | 540 | 670 | 914 | 1142 | 1362 | 1340 | 1131 | 843 | 488 | 241 | 4510 | 16 | 35 | 133 | 239 | 450 | 692 | 897 | 875 | 681 | 381 | 102 | 9 | 67829 | 181 | 405 | 1576 | 2955 | 6127 | 10909 | 15128 | 14611 | 10351 | 4478 | 1014 | 94 | 43740 | 23 | 93 | 622 | 1438 | 3604 | 7386 | 10812 | 10343 | 6731 | 2330 | 349 | 9 | 6.5 | 5 | 5.3 | 6.5 | 8 | 8.9 | 8.1 | 7.2 | 6.5 | 6.5 | 6.1 | 5.2 | 4.8 | 4.9 | 1 | 0.8 | 0.5 | 0.1 | 0.1 | 0 | 0.2 | 0.4 | 0.4 | 0.2 | 0.7 | 0.7 | 13.7 | 4.3 | 5.4 | 2.1 | 1 | 1.1 | 0.8 | 2.6 | 4.3 | 4.2 | 1.9 | 6.3 | 2.9 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 1.3 | 1.1 | 0.6 | 0.2 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.4 | 1.2 | 0.8 | 82.4 | 86.9 | 95.2 | 100.6 | 108.4 | 115 | 116.9 | 115.1 | 110.5 | 101.9 | 92.1 | 81.2 | 54.5 | 56.5 | 61 | 63.8 | 69.3 | 68 | 74 | 71.4 | 68.7 | 65.2 | 59.4 | 55.1 | 79 | 82.8 | 90.5 | 96.5 | 103.6 | 110.5 | 112.7 | 111.4 | 107.7 | 98.8 | 88.1 | 76.6 | 53.7 | 55.3 | 59.8 | 61.6 | 65.2 | 68 | 70.8 | 71 | 68.8 | 64 | 58.4 | 53.7 | 75.2 | 79.4 | 87.1 | 92.5 | 100 | 107.7 | 109.7 | 108.9 | 105.1 | 94.9 | 84 | 72.8 | 52.3 | 54.6 | 58.3 | 60.5 | 65.8 | 67.4 | 71.2 | 70.8 | 67.9 | 62.4 | 57.3 | 52 | 72.1 | 75 | 82.9 | 88.5 | 96.7 | 104.5 | 107.6 | 106.4 | 102 | 91.4 | 80.4 | 69.9 | 51.4 | 53 | 57.2 | 59.1 | 63.5 | 66.8 | 70.9 | 70.7 | 67.6 | 61.6 | 56 | 50.8 | 59.3 | 60.4 | 64.8 | 67.8 | 73.5 | 78.4 | 80.5 | 81 | 77.6 | 70.8 | 62.6 | 59.3 | 73.4 | 75.4 | 84.8 | 91.9 | 97.9 | 98.3 | 100.2 | 100.3 | 94.1 | 86.8 | 82.3 | 72.2 | 57.1 | 57.9 | 62.1 | 64.1 | 70.2 | 74 | 78.2 | 78.6 | 75.7 | 68.3 | 60.3 | 56.8 | 68.6 | 73.7 | 83.3 | 90.6 | 96.9 | 98.8 | 97.6 | 98.7 | 94.6 | 89.9 | 81.5 | 68.9 | 55.2 | 56.2 | 60.2 | 62.1 | 67.3 | 71.5 | 76.8 | 77 | 74 | 65.9 | 58.8 | 54.7 | 68.2 | 73 | 81.8 | 87.4 | 94.2 | 99.7 | 97.4 | 97.9 | 94.9 | 89.1 | 79.8 | 67.2 | 53.4 | 54.8 | 58.7 | 60.4 | 65.4 | 69.5 | 75.3 | 75.3 | 72.1 | 63.9 | 57.2 | 52.8 | 68.4 | 71.3 | 79.6 | 84.2 | 91.6 | 98.3 | 98.2 | 98 | 94.1 | 86.7 | 76.8 | 66 | 21.3 | 21.7 | 24 | 25 | 26.3 | 29 | 25.8 | 25.7 | 25.3 | 24 | 22.5 | 20.8 | 25.4 | 27.1 | 28.6 | 29.9 | 30.3 | 31.9 | 28.8 | 28.1 | 28.1 | 27.4 | 26.5 | 24.8 | 11.3 | 11.3 | 10 | 9.9 | 9.3 | 8.3 | 8.1 | 8.6 | 8.2 | 10 | 11.3 | 11.4 | 20.7 | 23.2 | 26.8 | 27.8 | 28.6 | 29 | 22.1 | 20.8 | 20.9 | 24 | 23.8 | 20.9 | 9.8 | 10.3 | 10.1 | 10.1 | 10 | 11 | 10.4 | 11.7 | 9.7 | 9.5 | 10.8 | 10.2 | 0.307 | 0.312 | 0.331 | 0.35 | 0.365 | 0.368 | 0.401 | 0.391 | 0.359 | 0.349 | 0.313 | 0.315 | 2.49 | 2.488 | 2.422 | 2.381 | 2.369 | 2.376 | 2.372 | 2.385 | 2.447 | 2.423 | 2.512 | 2.496 | 288 | 298 | 300 | 297 | 292 | 289 | 279 | 281 | 287 | 280 | 284 | 278 | 27 | 30 | 35 | 38 | 39 | 39 | 39 | 37 | 34 | 32 | 26 | 26 | 1054 | 1349 | 1823 | 2234 | 2509 | 2684 | 2438 | 2279 | 1988 | 1559 | 1171 | 954 | 71 | 118 | 85 | 72 | 100 | 101 | 116 | 98 | 74 | 78 | 49 | 58 | 1.08 | N/A | -3.69 | 1.51 | -1.48 | N/A | N/A | -176 | 482 | 310 | 1.04 | N/A | -2.92 | 1.12 | N/A | N/A | N/A | -167 | 367 | 193 | 47
4 | USA | CA | RIVERSIDE | 722869 | 03171 | 33.952 | -117.439 | 804 | 14.27 | -8 | NAP | 98-19 | 3B | 12 | 36.6 | 38.9 | 1.1 | 6 | 61.7 | 6.6 | 8 | 64.5 | 26.6 | 62.4 | 23.4 | 63.1 | 2.6 | 60 | 0.398 | 8 | 29.2 | 100.7 | 69.1 | 98.3 | 68.6 | 95.1 | 67.4 | 72.9 | 93.6 | 71.4 | 91.9 | 70.1 | 90 | 10.3 | 270 | 66.2 | 99.3 | 80.2 | 64.2 | 92.6 | 78.6 | 63.2 | 89.4 | 77.3 | 36.8 | 93.7 | 35.6 | 91.9 | 34.5 | 90.5 | 84 | 18.6 | 16.1 | 13.6 | 32.2 | 107.8 | 2.4 | 3.8 | 30.4 | 110.5 | 29 | 112.7 | 27.7 | 114.9 | 25.9 | 117.6 | 28.4 | 75 | 1.7 | 1.4 | 27.2 | 76 | 26.1 | 76.8 | 25.2 | 77.6 | 23.9 | 78.6 | 66.3 | 56.4 | 56.4 | 59.6 | 62.6 | 67.3 | 72.8 | 78.8 | 79.2 | 76.4 | 69 | 61.2 | 55.2 | 10.34 | 6.35 | 6.37 | 6.15 | 6.14 | 5.37 | 5.16 | 4.81 | 4.73 | 6.01 | 6.14 | 6.36 | 5.58 | 46 | 14 | 10 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 16 | 1357 | 277 | 252 | 188 | 117 | 35 | 3 | 0 | 0 | 1 | 29 | 147 | 308 | 5989 | 212 | 188 | 302 | 378 | 535 | 683 | 891 | 905 | 792 | 588 | 339 | 176 | 1823 | 9 | 10 | 22 | 44 | 105 | 236 | 426 | 440 | 343 | 151 | 34 | 3 | 20881 | 179 | 249 | 452 | 739 | 1227 | 2466 | 4581 | 4837 | 3697 | 1776 | 575 | 103 | 10632 | 29 | 62 | 137 | 283 | 528 | 1209 | 2533 | 2759 | 2038 | 843 | 200 | 11 | 4.9 | 4.9 | 4.6 | 4.8 | 5.2 | 5.5 | 5.5 | 5.4 | 4.9 | 4.4 | 4.3 | 4.4 | 4.7 | 11.6 | 2.4 | 3 | 1.6 | 0.7 | 0.2 | 0.1 | 0.2 | 0.1 | 0.2 | 0.4 | 1 | 1.7 | 22.2 | 11.3 | 11.2 | 6.6 | 2.4 | 2 | 0.7 | 1.5 | 0.4 | 1.5 | 5.5 | 2.1 | 8.5 | 4.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 5.3 | 2.9 | 2.5 | 1.5 | 0.6 | 0.4 | 0.2 | 0.3 | 0.1 | 0.3 | 1 | 0.5 | 1.8 | 83.6 | 85.9 | 89.8 | 93.4 | 97.2 | 101.1 | 103.5 | 104.4 | 104.4 | 98.9 | 91 | 81.4 | 54.8 | 56 | 59 | 60.2 | 64.5 | 67.5 | 70.2 | 69.5 | 68.6 | 64 | 58.5 | 54.6 | 79.1 | 81.4 | 83.7 | 87.7 | 90.9 | 95.2 | 99.2 | 100.1 | 99.8 | 93.7 | 85.8 | 77 | 53.4 | 54.7 | 57.2 | 59 | 63.1 | 67.3 | 70.5 | 69.8 | 68.6 | 61.2 | 57 | 52.5 | 74.9 | 76.4 | 79.2 | 82.2 | 86.3 | 91 | 95.9 | 97.2 | 95.9 | 89.7 | 81 | 72.5 | 52.1 | 53.6 | 56.4 | 57.9 | 62.5 | 66.4 | 69.4 | 69 | 67.6 | 60.6 | 55.4 | 50.9 | 70.9 | 70.3 | 74 | 77.4 | 81.2 | 87.7 | 92.6 | 93.3 | 91.4 | 84.2 | 75.5 | 68 | 51 | 51.7 | 55.2 | 57 | 61.8 | 65.6 | 68.6 | 68.1 | 66.7 | 59.9 | 53.7 | 50.1 | 59.9 | 60.4 | 63.3 | 64.8 | 69.2 | 71.1 | 74.8 | 75.4 | 74.3 | 68.8 | 62 | 59.3 | 71.9 | 73 | 80.9 | 85.7 | 90.7 | 94.2 | 97 | 94.7 | 95.4 | 84.5 | 75.2 | 68 | 57.3 | 57.8 | 60.8 | 62.1 | 66.7 | 69.3 | 72.8 | 72.7 | 72.1 | 66.3 | 59.9 | 57.3 | 66.5 | 70.7 | 77.2 | 80.7 | 85.6 | 91.3 | 93.7 | 93.1 | 91.8 | 83.9 | 75.1 | 65.3 | 55.4 | 56 | 59 | 60 | 64.6 | 67.9 | 71.3 | 71.1 | 70.2 | 64.4 | 58.3 | 55.3 | 66 | 68.7 | 73.5 | 77.3 | 81.8 | 87.9 | 91.4 | 92 | 89.5 | 81.1 | 72.4 | 64.3 | 53.7 | 54.4 | 57.2 | 58.4 | 62.6 | 66.4 | 69.8 | 69.5 | 68.4 | 62.6 | 57 | 53.4 | 64.9 | 65.3 | 69.9 | 73.5 | 77.8 | 84.3 | 88.7 | 89.9 | 86.7 | 77.3 | 69.8 | 62.4 | 23.3 | 22.6 | 24 | 24.5 | 24.1 | 26.6 | 28.1 | 29.2 | 28.3 | 26 | 25.2 | 22.8 | 31 | 33.4 | 32.7 | 34.3 | 34 | 33.1 | 31 | 32.5 | 33.9 | 35.4 | 33.7 | 31.7 | 13.8 | 14 | 13.4 | 13.1 | 12.7 | 11.2 | 10.2 | 11.3 | 11.3 | 13.1 | 13.7 | 14.7 | 23.8 | 25.6 | 27.9 | 29.9 | 29.9 | 30.5 | 28.4 | 29.7 | 29.8 | 28.9 | 26 | 22.6 | 12.2 | 12.1 | 12.7 | 12.5 | 11.9 | 11 | 9.8 | 10.8 | 10.9 | 11.4 | 12 | 12 | 0.303 | 0.313 | 0.335 | 0.349 | 0.356 | 0.362 | 0.383 | 0.367 | 0.35 | 0.34 | 0.305 | 0.305 | 2.547 | 2.534 | 2.45 | 2.416 | 2.429 | 2.423 | 2.428 | 2.46 | 2.494 | 2.493 | 2.582 | 2.576 | 290 | 299 | 298 | 297 | 294 | 291 | 284 | 288 | 290 | 284 | 288 | 283 | 26 | 29 | 34 | 37 | 37 | 37 | 36 | 35 | 32 | 30 | 24 | 24 | 1027 | 1311 | 1763 | 2142 | 2344 | 2522 | 2427 | 2297 | 1956 | 1491 | 1143 | 931 | 70 | 128 | 87 | 96 | 124 | 128 | 113 | 58 | 60 | 90 | 56 | 65 | 2.03 | 2.61 | N/A | 0.85 | N/A | N/A | N/A | -409 | 783 | 443 | 1.13 | N/A | -3.06 | 1.3 | N/A | N/A | N/A | -202 | 401 | 202 | 51
4 | USA | CA | LOS ANGELES USC | 722874 | 93134 | 34.024 | -118.291 | 179 | 14.6 | -8 | NAP | 99-19 | 3A | 12 | 43.1 | 45.1 | 12 | 10.2 | 64.6 | 17.1 | 13.1 | 62.2 | 10.6 | 56.9 | 9 | 57.8 | 0.4 | 20 | 0.293 | 8 | 17.3 | 92 | 66.1 | 88.5 | 66.1 | 85.5 | 65.9 | 71.7 | 85.1 | 70.5 | 83 | 69.3 | 81 | 3 | 260 | 67.2 | 100.8 | 77.6 | 66 | 96.5 | 76.6 | 64.9 | 92.6 | 75.4 | 35.6 | 85.1 | 34.5 | 83 | 33.5 | 81.2 | 76.8 | 9.4 | 7.5 | 6.6 | 38.6 | 99.9 | 2 | 4.4 | 37.2 | 103 | 36.1 | 105.6 | 35 | 108.1 | 33.5 | 111.3 | 33 | 74.3 | 1.9 | 1.5 | 31.6 | 75.3 | 30.4 | 76.2 | 29.3 | 77.1 | 27.9 | 78.2 | 65.7 | 58.8 | 58.7 | 61.4 | 63.3 | 65.9 | 69.3 | 73.4 | 74 | 73.1 | 69.2 | 63.2 | 57.8 | 7.41 | 5.26 | 5.36 | 5.02 | 4.9 | 4.2 | 3.39 | 3.91 | 3.62 | 4.83 | 5.27 | 5.38 | 4.47 | 4 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 985 | 204 | 188 | 135 | 87 | 33 | 2 | 0 | 0 | 0 | 16 | 94 | 226 | 5739 | 273 | 244 | 354 | 400 | 493 | 578 | 725 | 744 | 693 | 595 | 396 | 244 | 1246 | 10 | 11 | 24 | 37 | 62 | 130 | 260 | 279 | 243 | 146 | 40 | 4 | 7772 | 143 | 139 | 228 | 325 | 375 | 546 | 1468 | 1633 | 1519 | 981 | 355 | 60 | 2435 | 22 | 31 | 61 | 110 | 128 | 125 | 403 | 479 | 562 | 394 | 116 | 4 | 1.9 | 1.4 | 1.9 | 2.1 | 2.4 | 2.3 | 2.1 | 2.1 | 2 | 1.8 | 1.5 | 1.3 | 1.4 | 15.9 | 3.6 | 4.2 | 2.2 | 0.9 | 0.4 | 0.1 | 0 | 0 | 0.2 | 0.7 | 1.1 | 2.4 | 29.5 | 16 | 14.6 | 7 | 2.4 | 4 | 0.8 | 0.3 | 0.1 | 2.3 | 5.4 | 2.6 | 9.7 | 6.5 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.3 | 3.9 | 3.7 | 2.1 | 0.7 | 0.8 | 0.2 | 0.1 | 0 | 0.5 | 1.1 | 0.8 | 2.3 | 83.1 | 84.8 | 86.8 | 90.5 | 91.3 | 90.2 | 92.8 | 92.7 | 97.4 | 95.3 | 89.4 | 79.8 | 55.4 | 56.5 | 59.9 | 61.5 | 61.6 | 69.2 | 71.8 | 70.2 | 68.1 | 62.2 | 59.7 | 54.3 | 78.1 | 78.4 | 80.2 | 82.3 | 82.8 | 83 | 87.4 | 88.5 | 91.1 | 89.4 | 83.3 | 75.1 | 54.6 | 55 | 57.3 | 58.2 | 62.7 | 67.2 | 70.3 | 69.3 | 68.7 | 61.8 | 57.8 | 53.6 | 73.9 | 73.1 | 75.1 | 76.8 | 77.4 | 79.5 | 84.3 | 85.1 | 86.4 | 84.3 | 77.5 | 70.9 | 53.3 | 54.7 | 56.7 | 57.8 | 62.7 | 66.5 | 69.5 | 68.8 | 67.4 | 61.4 | 56.1 | 52.8 | 69.2 | 68.2 | 70.6 | 72.2 | 73.3 | 76.6 | 81.4 | 82.1 | 82.3 | 79.1 | 73.1 | 66.8 | 52.8 | 54.1 | 56.2 | 57.7 | 61.5 | 65.1 | 68.6 | 68.3 | 66.9 | 62.3 | 55.8 | 52.6 | 60.5 | 62 | 63.7 | 65 | 68.4 | 70.2 | 74.2 | 73 | 73.2 | 69.7 | 63.6 | 60.5 | 69.1 | 70.2 | 77.3 | 78.9 | 81.5 | 84.8 | 87.5 | 87.5 | 91.2 | 82.2 | 74 | 66.8 | 58.7 | 59.4 | 61.3 | 62.2 | 65.8 | 68.4 | 71.8 | 71.2 | 71 | 67.3 | 61.9 | 59 | 66.1 | 68.5 | 73 | 74.6 | 77.4 | 81 | 84 | 84.2 | 85.4 | 79.4 | 71.7 | 65.4 | 57.3 | 57.8 | 59.7 | 60.4 | 63.9 | 66.9 | 70.5 | 70 | 69.3 | 65.7 | 60.4 | 57.4 | 64.4 | 66.1 | 69.4 | 71.4 | 74.1 | 78.2 | 81.9 | 82.1 | 82.1 | 76.4 | 69.5 | 63.8 | 56 | 56.4 | 58.3 | 59 | 62.3 | 65.7 | 69.2 | 68.9 | 68.1 | 64.2 | 59.4 | 55.9 | 63.5 | 64.3 | 66.2 | 68.8 | 71.3 | 75.8 | 79.7 | 80.2 | 79.5 | 73.2 | 67.9 | 62.2 | 18.8 | 17.4 | 17 | 16.5 | 14.8 | 14.7 | 16.5 | 17.3 | 17.6 | 17.8 | 18.7 | 18.1 | 26.7 | 25.8 | 25.3 | 24.8 | 22.2 | 19.8 | 19.6 | 20.7 | 23.6 | 27.3 | 26.8 | 25.2 | 11.8 | 11.2 | 10.5 | 10.2 | 9.1 | 8.2 | 7.7 | 7.8 | 8.4 | 10.3 | 11.6 | 12.4 | 18.4 | 19.2 | 19.1 | 19.3 | 18.2 | 18 | 18.2 | 18.8 | 19.9 | 19.2 | 18.8 | 17.4 | 9.4 | 9.8 | 8.9 | 8.8 | 8.1 | 7.8 | 7.5 | 7.6 | 7.6 | 7.9 | 9.1 | 9.8 | 0.343 | 0.356 | 0.382 | 0.384 | 0.385 | 0.405 | 0.402 | 0.383 | 0.369 | 0.38 | 0.325 | 0.326 | 2.463 | 2.437 | 2.34 | 2.347 | 2.376 | 2.324 | 2.401 | 2.433 | 2.465 | 2.397 | 2.558 | 2.551 | 274 | 282 | 283 | 286 | 286 | 279 | 279 | 283 | 283 | 270 | 280 | 274 | 28 | 32 | 38 | 39 | 39 | 41 | 37 | 36 | 33 | 33 | 25 | 24 | 1000 | 1281 | 1719 | 2104 | 2285 | 2402 | 2382 | 2262 | 1912 | 1450 | 1116 | 908 | 73 | 129 | 97 | 108 | 149 | 141 | 123 | 72 | 73 | 103 | 65 | 68 | 1.44 | N/A | N/A | 2.75 | N/A | N/A | N/A | -243 | 556 | 331 | 1.15 | N/A | -2.97 | 1.31 | N/A | N/A | N/A | -212 | 405 | 194 | 52
4 | USA | CA | HOLLYWOOD BURBANK | 722880 | 23152 | 34.201 | -118.358 | 775 | 14.29 | -8 | NAP | 94-19 | 3A | 12 | 38.9 | 41.3 | 5.3 | 7.4 | 63.2 | 11.3 | 10.1 | 62.8 | 25 | 59 | 20.8 | 58.5 | 1.7 | 350 | 0.387 | 8 | 23.2 | 97.9 | 67.8 | 94.3 | 66.8 | 91.2 | 66.1 | 72.4 | 89.8 | 70.9 | 87.6 | 69.3 | 85.5 | 8.4 | 180 | 66.4 | 100.2 | 78 | 65.1 | 95.7 | 77 | 63.8 | 91.1 | 75.3 | 36.4 | 89.7 | 35 | 87.6 | 33.8 | 85.9 | 82.9 | 18.1 | 14.8 | 12.6 | 34.2 | 105.4 | 2.3 | 3.8 | 32.5 | 108.1 | 31.1 | 110.4 | 29.8 | 112.5 | 28.1 | 115.2 | 28.9 | 75 | 2.3 | 3.2 | 27.2 | 77.3 | 25.8 | 79.2 | 24.6 | 81 | 22.9 | 83.3 | 65.4 | 56.6 | 56.7 | 60 | 62.5 | 65.7 | 70.4 | 75.8 | 77.1 | 74.8 | 68.2 | 61.2 | 55.6 | 9.39 | 5.79 | 5.95 | 5.91 | 6.31 | 5.7 | 5.26 | 4.78 | 4.98 | 6.11 | 6.02 | 5.93 | 5.18 | 31 | 9 | 8 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 10 | 1345 | 267 | 241 | 176 | 122 | 57 | 8 | 0 | 0 | 2 | 32 | 145 | 295 | 5662 | 213 | 195 | 313 | 374 | 488 | 612 | 801 | 840 | 743 | 564 | 336 | 183 | 1502 | 7 | 8 | 22 | 46 | 80 | 170 | 336 | 375 | 294 | 131 | 30 | 3 | 14776 | 140 | 170 | 345 | 587 | 779 | 1419 | 2981 | 3605 | 2879 | 1372 | 423 | 76 | 6519 | 20 | 40 | 98 | 207 | 307 | 557 | 1328 | 1786 | 1427 | 602 | 138 | 9 | 5.3 | 4.5 | 5 | 5.3 | 6.2 | 6.2 | 6.2 | 6.3 | 5.7 | 5.1 | 4.5 | 3.9 | 4.4 | 15.9 | 3.6 | 4.2 | 2.2 | 0.9 | 0.4 | 0.1 | 0 | 0 | 0.2 | 0.7 | 1.1 | 2.4 | 29.5 | 16 | 14.6 | 7 | 2.4 | 4 | 0.8 | 0.3 | 0.1 | 2.3 | 5.4 | 2.6 | 9.7 | 6.5 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.3 | 3.9 | 3.7 | 2.1 | 0.7 | 0.8 | 0.2 | 0.1 | 0 | 0.5 | 1.1 | 0.8 | 2.3 | 82.7 | 84.9 | 88.4 | 91.7 | 94.6 | 98.4 | 99.3 | 101.1 | 101.9 | 96.9 | 89.8 | 81 | 54.7 | 57 | 58.7 | 59.5 | 63.2 | 67 | 70.8 | 68.7 | 69.3 | 63.1 | 58.8 | 54.7 | 78.3 | 79.7 | 82.2 | 86 | 88.3 | 91 | 93.5 | 97.1 | 97.1 | 91.4 | 83.9 | 75.4 | 53.4 | 54.6 | 57.3 | 58.6 | 62.9 | 66.9 | 68.7 | 68.6 | 67.6 | 60.8 | 57.2 | 52.8 | 73.5 | 73.8 | 77.4 | 81 | 82.3 | 86.1 | 90.5 | 93.1 | 92.8 | 87.2 | 78.9 | 71.6 | 52.1 | 53.7 | 55.9 | 57.6 | 62.1 | 65.4 | 68.3 | 68 | 66.7 | 60.3 | 55.4 | 51.5 | 69.5 | 69 | 72.8 | 75.7 | 77.3 | 81.9 | 87.7 | 90 | 88.5 | 81.9 | 73.6 | 66.6 | 51.4 | 52.4 | 55 | 56.5 | 61.5 | 65.2 | 68 | 67.7 | 65.7 | 59.9 | 54.3 | 50.7 | 60.2 | 60.8 | 62.7 | 65.3 | 69.3 | 71.2 | 75.4 | 74.4 | 73.4 | 69.7 | 62.4 | 59.4 | 67.4 | 75.4 | 78.7 | 83.2 | 85.7 | 88.3 | 91.7 | 92.2 | 93.6 | 84.4 | 74.7 | 67.2 | 57.5 | 58.2 | 60.4 | 62.3 | 66.4 | 68.8 | 72.3 | 72.2 | 71.1 | 66.8 | 60.6 | 57.4 | 65.8 | 69.4 | 74.2 | 78 | 81.3 | 85.8 | 88.2 | 90 | 89.1 | 80 | 72.2 | 65.7 | 55.9 | 56.3 | 58.9 | 60.1 | 64.4 | 67.2 | 70.5 | 70.6 | 69.3 | 64.7 | 59.2 | 55.7 | 64.2 | 66.4 | 71.6 | 73.8 | 77.9 | 82.8 | 85.7 | 88 | 85.9 | 77.7 | 70.4 | 63.3 | 54.3 | 54.8 | 57.3 | 58.4 | 62.4 | 65.7 | 68.9 | 69 | 67.9 | 62.9 | 57.6 | 54 | 63.3 | 64.4 | 68.2 | 71 | 74 | 80.3 | 83.6 | 85.5 | 83.3 | 74.4 | 68.1 | 61.7 | 20.8 | 19.9 | 20.1 | 20 | 18.3 | 19.7 | 21.9 | 23.2 | 22.5 | 22 | 22.5 | 20.8 | 29.1 | 29.8 | 29.3 | 29.6 | 27.3 | 27.5 | 25.7 | 27.8 | 28.6 | 31.2 | 30.9 | 29.1 | 13.3 | 13.5 | 12.5 | 11.9 | 11.4 | 10.7 | 9.6 | 10.9 | 11.1 | 12.5 | 13.6 | 14 | 20 | 22.1 | 23.4 | 23.6 | 23.2 | 24.2 | 23.2 | 24.6 | 24.3 | 23.7 | 23.2 | 19.7 | 10.9 | 11.5 | 11.5 | 10.8 | 10.5 | 9.9 | 9.2 | 10.3 | 10.1 | 11.2 | 12.1 | 11.2 | 0.332 | 0.344 | 0.369 | 0.379 | 0.381 | 0.401 | 0.4 | 0.378 | 0.367 | 0.374 | 0.319 | 0.319 | 2.465 | 2.445 | 2.357 | 2.334 | 2.361 | 2.311 | 2.378 | 2.416 | 2.443 | 2.382 | 2.546 | 2.534 | 277 | 286 | 287 | 288 | 287 | 280 | 279 | 285 | 284 | 271 | 281 | 276 | 28 | 31 | 37 | 40 | 39 | 41 | 38 | 36 | 34 | 33 | 25 | 25 | 994 | 1275 | 1718 | 2107 | 2315 | 2464 | 2423 | 2294 | 1938 | 1466 | 1119 | 905 | 75 | 135 | 99 | 107 | 142 | 136 | 115 | 67 | 63 | 98 | 60 | 68 | N/A | N/A | -2.88 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.15 | N/A | -2.97 | 1.31 | N/A | N/A | N/A | -212 | 405 | 194 | 52
4 | USA | CA | SANTA MONICA | 722885 | 93197 | 34.016 | -118.451 | 174 | 14.6 | -8 | NAP | 00-19 | 3C | 12 | 43.3 | 45.3 | 8.8 | 8.7 | 63.1 | 14.5 | 11.6 | 61.2 | 16.9 | 57.8 | 14.9 | 57.2 | 3.2 | 40 | 0.349 | 8 | 11.1 | 85.7 | 62 | 82.1 | 62.5 | 79.3 | 63 | 70.3 | 77.4 | 69 | 76.1 | 67.8 | 74.9 | 6.5 | 210 | 67.7 | 102.4 | 74.1 | 66.2 | 97.1 | 73.2 | 64.8 | 92.3 | 71.7 | 34.3 | 77.6 | 33.2 | 76.4 | 32.2 | 74.9 | 75.6 | 14.5 | 12.5 | 11.2 | 39.6 | 94 | 2 | 4.7 | 38.1 | 97.4 | 37 | 100.2 | 35.9 | 102.8 | 34.4 | 106.2 | 32.6 | 71.5 | 2.3 | 2.1 | 30.9 | 73 | 29.6 | 74.2 | 28.3 | 75.4 | 26.6 | 76.9 | 62.9 | 57.8 | 57 | 59 | 60.4 | 62.8 | 65.6 | 69 | 69.5 | 69.2 | 66.1 | 61.6 | 56.9 | 6.42 | 5.48 | 5.06 | 4.56 | 4.51 | 3.92 | 2.72 | 3.39 | 3.41 | 4.61 | 5.1 | 5.32 | 4.53 | 7 | 3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1369 | 233 | 230 | 197 | 155 | 91 | 20 | 4 | 3 | 8 | 45 | 130 | 253 | 4731 | 245 | 198 | 280 | 311 | 395 | 469 | 590 | 603 | 575 | 499 | 349 | 217 | 620 | 11 | 7 | 12 | 16 | 22 | 39 | 129 | 141 | 133 | 79 | 28 | 3 | 2475 | 95 | 71 | 103 | 128 | 144 | 71 | 264 | 360 | 527 | 469 | 215 | 28 | 576 | 13 | 14 | 23 | 36 | 56 | 15 | 29 | 39 | 132 | 160 | 58 | 1 | 4.7 | 4.3 | 4.6 | 4.9 | 5.4 | 5.3 | 5.1 | 5 | 4.7 | 4.4 | 4.1 | 4.1 | 4.2 | 15.9 | 3.6 | 4.2 | 2.2 | 0.9 | 0.4 | 0.1 | 0 | 0 | 0.2 | 0.7 | 1.1 | 2.4 | 29.5 | 16 | 14.6 | 7 | 2.4 | 4 | 0.8 | 0.3 | 0.1 | 2.3 | 5.4 | 2.6 | 9.7 | 6.5 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.3 | 3.9 | 3.7 | 2.1 | 0.7 | 0.8 | 0.2 | 0.1 | 0 | 0.5 | 1.1 | 0.8 | 2.3 | 81.7 | 82.2 | 83 | 85 | 87.5 | 81.8 | 83.3 | 83.8 | 90.1 | 91.2 | 86.4 | 78 | 55.8 | 55.8 | 57.7 | 57.3 | 57.8 | 66.6 | 69.4 | 68.2 | 67.2 | 62.1 | 58 | 53.4 | 76.4 | 74.8 | 76.1 | 77.1 | 76.6 | 75 | 79.3 | 80.6 | 83.3 | 84.2 | 80.3 | 72.6 | 53.1 | 53.6 | 55.3 | 56 | 59.2 | 64.5 | 68.1 | 67.7 | 67.3 | 59.9 | 56.5 | 52.5 | 72.3 | 69.9 | 70.9 | 71.8 | 71.6 | 72.4 | 76.7 | 77.9 | 79.4 | 79.1 | 75 | 68.5 | 52.5 | 53.3 | 54.6 | 55.4 | 60.4 | 63.5 | 67.3 | 67.3 | 66.6 | 60.5 | 54.9 | 52.2 | 67.6 | 65.1 | 66.4 | 67.6 | 68.3 | 70.5 | 74.6 | 75.4 | 76.3 | 74.4 | 70.5 | 64.9 | 51.3 | 53 | 54.9 | 55.9 | 59.3 | 62.5 | 66.6 | 66.6 | 66.1 | 61.8 | 55.3 | 52.4 | 60.1 | 60.3 | 61.9 | 61.9 | 64.4 | 67.7 | 71.6 | 71.6 | 71.9 | 69.6 | 63.2 | 61.1 | 66.8 | 67.5 | 72.5 | 73.1 | 73.9 | 77.5 | 78.1 | 78.7 | 80.9 | 77.5 | 69.5 | 64.3 | 58.4 | 58.5 | 59.9 | 59.8 | 62.6 | 65.7 | 69.9 | 69.8 | 69.8 | 66.9 | 61.5 | 59.1 | 64.3 | 64.4 | 68.1 | 67.9 | 70.7 | 73.5 | 76 | 77.1 | 77.9 | 75.2 | 68.3 | 64 | 57.2 | 57.2 | 58.5 | 58.7 | 61.4 | 64.4 | 68.7 | 68.4 | 68.5 | 65.3 | 60.2 | 57.7 | 63.3 | 62.9 | 65.4 | 66 | 68.6 | 71 | 74.7 | 75.6 | 76.3 | 72.6 | 67.2 | 62.7 | 55.9 | 56 | 57.4 | 57.6 | 60.2 | 63.4 | 67.4 | 67.2 | 67.1 | 63.9 | 59.1 | 56.3 | 62.1 | 62.1 | 63.2 | 64.6 | 66.7 | 69.2 | 73.5 | 74.1 | 74.5 | 69.9 | 66.2 | 61.4 | 16.6 | 15.4 | 13.8 | 13.2 | 11.1 | 10 | 10.3 | 11.1 | 12.5 | 14.3 | 16.4 | 15.9 | 24.2 | 23.7 | 21.8 | 21 | 16.6 | 13 | 12.8 | 13.7 | 17.4 | 23.3 | 23.9 | 21.7 | 11.4 | 11.5 | 10.3 | 9.5 | 7.5 | 6 | 5.5 | 6 | 7.5 | 11 | 12 | 11.9 | 15.8 | 15.6 | 14.5 | 14.7 | 12.7 | 12.2 | 11.9 | 12.2 | 14.3 | 15.7 | 16.4 | 14.7 | 9.3 | 8.9 | 7.8 | 7.3 | 6.2 | 5.8 | 5.2 | 5.8 | 6.5 | 8.6 | 9.7 | 9.6 | 0.332 | 0.345 | 0.368 | 0.378 | 0.385 | 0.4 | 0.404 | 0.383 | 0.371 | 0.372 | 0.321 | 0.323 | 2.504 | 2.48 | 2.395 | 2.367 | 2.378 | 2.342 | 2.393 | 2.433 | 2.461 | 2.43 | 2.57 | 2.562 | 279 | 287 | 287 | 288 | 286 | 280 | 278 | 283 | 283 | 273 | 281 | 276 | 27 | 30 | 36 | 39 | 39 | 40 | 38 | 36 | 33 | 32 | 25 | 24 | 995 | 1276 | 1709 | 2096 | 2271 | 2372 | 2369 | 2252 | 1900 | 1441 | 1111 | 903 | 73 | 129 | 99 | 110 | 155 | 145 | 126 | 75 | 76 | 107 | 67 | 69 | 1.49 | N/A | -2.9 | 2.05 | 1.71 | N/A | N/A | -277 | 529 | 290 | 1.15 | N/A | -2.97 | 1.31 | N/A | N/A | N/A | -212 | 405 | 194 | 52
4 | USA | CA | VAN NUYS | 722886 | 23130 | 34.21 | -118.489 | 770 | 14.29 | -8 | NAP | 98-19 | 3A | 12 | 38.6 | 41.1 | 0.1 | 5.7 | 60.9 | 5.5 | 7.5 | 63.1 | 25.9 | 58.8 | 24 | 59.1 | 1.7 | 0 | 0.391 | 8 | 26.1 | 100 | 67.5 | 97 | 66.9 | 93.5 | 65.8 | 72.1 | 91.9 | 70.5 | 89.6 | 69.1 | 87.5 | 8.1 | 130 | 65.6 | 97.3 | 79.3 | 63.9 | 91.6 | 76.4 | 63 | 88.6 | 74.9 | 36.1 | 92.3 | 34.7 | 89.6 | 33.6 | 87.6 | 84.2 | 20.7 | 18 | 15.3 | 34.1 | 106.4 | 2.5 | 3.8 | 32.3 | 109.1 | 30.8 | 111.4 | 29.4 | 113.5 | 27.5 | 116.2 | 29.5 | 75.2 | 2.5 | 3.5 | 27.7 | 77.7 | 26.2 | 79.7 | 24.8 | 81.6 | 23 | 84.2 | 66.1 | 57.2 | 56.7 | 60.3 | 62.7 | 66.7 | 71.5 | 77.4 | 78.2 | 75.6 | 68.9 | 61.8 | 55.9 | 9.92 | 6.59 | 6.35 | 6.45 | 6.48 | 6.01 | 5.75 | 5.05 | 5.09 | 6.33 | 6.31 | 6.41 | 5.89 | 39 | 12 | 9 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 13 | 1307 | 257 | 244 | 175 | 119 | 47 | 8 | 0 | 0 | 2 | 31 | 135 | 289 | 5923 | 234 | 196 | 321 | 381 | 517 | 645 | 849 | 873 | 768 | 587 | 356 | 196 | 1716 | 14 | 11 | 28 | 50 | 99 | 203 | 384 | 408 | 320 | 152 | 40 | 7 | 18392 | 135 | 178 | 418 | 672 | 1107 | 1988 | 3913 | 4320 | 3377 | 1656 | 539 | 89 | 8920 | 17 | 32 | 116 | 243 | 481 | 909 | 2021 | 2353 | 1808 | 748 | 183 | 9 | 5.2 | 6.2 | 5.3 | 5.3 | 5.8 | 5.5 | 5.4 | 5.1 | 4.6 | 4.2 | 4.5 | 4.9 | 5.9 | 15.9 | 3.6 | 4.2 | 2.2 | 0.9 | 0.4 | 0.1 | 0 | 0 | 0.2 | 0.7 | 1.1 | 2.4 | 29.5 | 16 | 14.6 | 7 | 2.4 | 4 | 0.8 | 0.3 | 0.1 | 2.3 | 5.4 | 2.6 | 9.7 | 6.5 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.3 | 3.9 | 3.7 | 2.1 | 0.7 | 0.8 | 0.2 | 0.1 | 0 | 0.5 | 1.1 | 0.8 | 2.3 | 82.2 | 84 | 88.9 | 92.7 | 97.4 | 101.8 | 102.2 | 103.6 | 104.1 | 97.7 | 90.3 | 81.1 | 54.6 | 56 | 59.2 | 60.2 | 65.6 | 66 | 69.8 | 68.1 | 69.4 | 62.8 | 58.3 | 54.5 | 78.1 | 79.9 | 83 | 87 | 90.8 | 93.9 | 97.2 | 99.4 | 99.2 | 92.6 | 85.6 | 76.3 | 53.6 | 55.3 | 57.9 | 59.3 | 62.8 | 67 | 68.4 | 67.7 | 67 | 60.8 | 57.4 | 52.5 | 74 | 74.8 | 78.7 | 81.6 | 85.3 | 89.5 | 93.5 | 95.8 | 95.1 | 88.5 | 80.3 | 72.2 | 52.2 | 53.7 | 56.5 | 57.6 | 62.1 | 65.8 | 68.1 | 67 | 66.3 | 59.9 | 55.2 | 51.4 | 70.4 | 70 | 74.1 | 76.9 | 80 | 84.7 | 90.6 | 92 | 90.5 | 83.6 | 75.3 | 68.1 | 50.8 | 51.8 | 55.3 | 56.3 | 61.4 | 65 | 67.4 | 66.5 | 65 | 58.9 | 53.5 | 50.2 | 59.7 | 60.3 | 64 | 65.7 | 72 | 71.7 | 74.6 | 73.5 | 73.1 | 68.8 | 61.7 | 59.2 | 70.8 | 72.1 | 77 | 83.6 | 86.3 | 89.9 | 94.7 | 94.9 | 96.2 | 83.9 | 75.6 | 68.1 | 57.3 | 57.6 | 60.8 | 62.1 | 66.5 | 69.2 | 72 | 71.3 | 70.8 | 66.1 | 59.8 | 57.3 | 67.4 | 70.6 | 76.4 | 78.7 | 83.1 | 88.1 | 91 | 91.7 | 91.3 | 82 | 74.8 | 65.8 | 55.5 | 55.9 | 59 | 59.9 | 64.4 | 67.6 | 70.3 | 69.6 | 68.9 | 64.1 | 58.3 | 55.5 | 65.5 | 68.1 | 73.9 | 75.8 | 80.4 | 85 | 88.5 | 89.3 | 87.7 | 79 | 71.6 | 63.6 | 53.9 | 54.3 | 57.1 | 58.2 | 62.3 | 66 | 68.8 | 68.3 | 67.4 | 62.3 | 56.9 | 53.6 | 64 | 65.1 | 69.5 | 72.7 | 76.3 | 82.1 | 86.2 | 87.2 | 85 | 75.6 | 68.8 | 63 | 20.1 | 20 | 21 | 21.2 | 21.2 | 22.7 | 24.9 | 26.1 | 25.1 | 23.3 | 22.8 | 20.2 | 26.4 | 29.4 | 29.2 | 30.5 | 30.9 | 30.5 | 28.4 | 30.6 | 31.7 | 32.1 | 31.2 | 27.7 | 11.8 | 12.8 | 11.9 | 11.9 | 11.3 | 9.8 | 9.1 | 9.7 | 9.6 | 10.7 | 11.6 | 12.5 | 20.5 | 23.3 | 24.9 | 25.1 | 26.3 | 26.9 | 25.7 | 26.6 | 26.9 | 24.8 | 24.2 | 20.4 | 10.7 | 11.4 | 11.6 | 11.4 | 11.2 | 10 | 9.3 | 9.4 | 9.3 | 10.2 | 10.6 | 10.8 | 0.325 | 0.338 | 0.36 | 0.378 | 0.385 | 0.399 | 0.407 | 0.381 | 0.372 | 0.372 | 0.318 | 0.319 | 2.491 | 2.471 | 2.391 | 2.339 | 2.35 | 2.318 | 2.357 | 2.406 | 2.426 | 2.392 | 2.549 | 2.536 | 280 | 289 | 290 | 288 | 285 | 280 | 277 | 284 | 282 | 272 | 282 | 277 | 27 | 31 | 36 | 40 | 40 | 41 | 39 | 37 | 34 | 33 | 25 | 25 | 990 | 1269 | 1710 | 2099 | 2306 | 2451 | 2421 | 2293 | 1934 | 1461 | 1115 | 901 | 75 | 137 | 101 | 110 | 146 | 139 | 115 | 67 | 63 | 100 | 61 | 69 | 1.94 | N/A | -6.44 | 1.26 | N/A | N/A | N/A | -299 | 688 | 367 | 1.15 | N/A | -2.97 | 1.3 | N/A | N/A | N/A | -225 | 414 | 182 | 52
4 | USA | CA | LOMPOC | 722895 | 23243 | 34.667 | -120.467 | 88 | 14.65 | -8 | NAP | 94-19 | 3C | 12 | 32.3 | 35.5 | 22.5 | 17 | 46.9 | 25.8 | 19.9 | 44.1 | 20.8 | 57.8 | 18.6 | 58.3 | 4.4 | 80 | 0.524 | 8 | 15.7 | 82.1 | 62 | 78.7 | 61.4 | 74.8 | 60.8 | 66 | 76.7 | 64.3 | 74.1 | 62.9 | 72 | 10.3 | 270 | 61.5 | 81.8 | 70.1 | 60.5 | 79.1 | 69.2 | 58.8 | 74.1 | 67.2 | 30.6 | 76.9 | 29.4 | 74.2 | 28.4 | 71.9 | 90.7 | 20.2 | 18.5 | 17 | 27.6 | 93.4 | 2.1 | 9.5 | 26.1 | 100.2 | 24.9 | 105.8 | 23.7 | 111.1 | 22.2 | 118 | 25.3 | 70.8 | 1.9 | 6 | 23.9 | 75.2 | 22.8 | 78.7 | 21.7 | 82 | 20.3 | 86.4 | 57.6 | 52.7 | 52.7 | 54.7 | 55.8 | 57.9 | 60.2 | 62.3 | 63 | 62.9 | 60.5 | 56.8 | 51.9 | 5.63 | 4.71 | 4.6 | 4.23 | 4.02 | 3.42 | 2.82 | 2.68 | 2.65 | 3.77 | 4.49 | 5.11 | 4.7 | 100 | 27 | 22 | 9 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 33 | 2761 | 381 | 345 | 320 | 278 | 224 | 148 | 93 | 74 | 85 | 155 | 253 | 405 | 2891 | 111 | 98 | 155 | 177 | 244 | 305 | 381 | 404 | 387 | 326 | 209 | 94 | 74 | 0 | 0 | 1 | 2 | 3 | 3 | 8 | 13 | 22 | 16 | 6 | 0 | 968 | 25 | 26 | 42 | 64 | 70 | 33 | 38 | 62 | 206 | 278 | 118 | 6 | 259 | 1 | 3 | 8 | 22 | 21 | 5 | 5 | 7 | 59 | 93 | 35 | 0 | 7 | 6 | 6.6 | 7.1 | 7.9 | 8.6 | 8.4 | 7.7 | 7.2 | 6.5 | 6.2 | 5.9 | 6.1 | 17.3 | 3.9 | 4.2 | 2.6 | 1.1 | 0.4 | 0.1 | 0 | 0 | 0 | 0.8 | 1.3 | 2.8 | 32.2 | 16.7 | 15.8 | 12.6 | 3.9 | 2.3 | 0.7 | 0.2 | 0.1 | 0.4 | 3.9 | 4.1 | 9.1 | 5.8 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7 | 4 | 3.6 | 3.1 | 1.2 | 0.6 | 0.2 | 0 | 0 | 0.1 | 1 | 1.1 | 2.4 | 77.4 | 78.3 | 79.3 | 82.2 | 81.5 | 78.6 | 78.8 | 80.6 | 88 | 89.8 | 84.5 | 73.4 | 56 | 57.5 | 57.7 | 60 | 61.9 | 63.8 | 65.4 | 65.9 | 66.5 | 62.2 | 60.4 | 55 | 72.3 | 71.5 | 72.3 | 72.6 | 73.1 | 72.8 | 73.4 | 75 | 80.1 | 81.3 | 76.8 | 69.6 | 54.9 | 55.3 | 56.9 | 58.1 | 60.6 | 61.7 | 63.3 | 63.9 | 63.9 | 61.2 | 58.2 | 54.9 | 66.3 | 64.7 | 67.7 | 68.4 | 69.7 | 70.2 | 71.8 | 72.4 | 74.8 | 75.2 | 71.8 | 64.3 | 54.4 | 53.5 | 56.4 | 57.5 | 59.2 | 60.3 | 62.5 | 62.6 | 63.1 | 60 | 56.8 | 54.2 | 63.2 | 62.6 | 63.9 | 64.8 | 65.9 | 67.6 | 69.8 | 70.3 | 72 | 71.6 | 66.5 | 62.7 | 53.8 | 53.2 | 55.1 | 55.8 | 57.5 | 59.1 | 61.3 | 61.7 | 62 | 59.5 | 56.4 | 54 | 60.9 | 60.3 | 61.6 | 62.4 | 64.5 | 65.3 | 66.8 | 67 | 69.3 | 67 | 63.8 | 61 | 67.8 | 71.2 | 70.9 | 73.8 | 75.7 | 76.6 | 75.9 | 77.9 | 80.6 | 80 | 73.4 | 66 | 58.4 | 57.6 | 59.4 | 60 | 61.8 | 62.3 | 64.3 | 64.7 | 66 | 63.9 | 61.2 | 58.8 | 65.5 | 65.6 | 68.4 | 69.5 | 71.7 | 71.9 | 73.2 | 73.9 | 76.4 | 74.8 | 70.9 | 63.9 | 56.7 | 55.9 | 57.8 | 58.3 | 59.5 | 60.8 | 62.4 | 63.1 | 64 | 62 | 59.3 | 56.9 | 63.2 | 63.1 | 65.6 | 66.7 | 68.2 | 69 | 70.5 | 71.5 | 73.5 | 72.2 | 67.7 | 62.3 | 54.8 | 54.2 | 56.2 | 56.7 | 57.8 | 59.3 | 61.2 | 61.9 | 62.2 | 60.3 | 57.8 | 54.9 | 61.2 | 60.6 | 63.4 | 64.2 | 65.1 | 66.3 | 68.6 | 69.8 | 70.8 | 69.3 | 65.3 | 60.4 | 23.1 | 21.1 | 21 | 20.3 | 17.7 | 16.2 | 15.1 | 15.7 | 19.3 | 23.3 | 24.3 | 22.4 | 30.9 | 28.1 | 29.3 | 27.4 | 25.4 | 20.9 | 18.3 | 19.1 | 25.7 | 32.8 | 32.2 | 26.5 | 17.6 | 16.3 | 16.7 | 15.5 | 14.5 | 12.2 | 10.6 | 10.7 | 14.1 | 17.5 | 17.5 | 16.4 | 22.5 | 22.3 | 23.2 | 23.3 | 22 | 19.1 | 17.2 | 17.9 | 22.3 | 26.3 | 24.9 | 18.8 | 14.4 | 14.1 | 14.5 | 14.3 | 13 | 11.4 | 9.9 | 10.2 | 12.7 | 15.3 | 15.1 | 12.8 | 0.305 | 0.319 | 0.327 | 0.347 | 0.358 | 0.353 | 0.367 | 0.35 | 0.35 | 0.342 | 0.307 | 0.309 | 2.596 | 2.565 | 2.544 | 2.469 | 2.46 | 2.471 | 2.487 | 2.505 | 2.509 | 2.534 | 2.604 | 2.595 | 289 | 296 | 301 | 298 | 294 | 293 | 289 | 293 | 289 | 283 | 286 | 280 | 24 | 28 | 31 | 35 | 36 | 35 | 34 | 33 | 31 | 28 | 24 | 23 | 960 | 1232 | 1675 | 2087 | 2305 | 2366 | 2243 | 2078 | 1801 | 1397 | 1072 | 857 | 74 | 123 | 106 | 125 | 149 | 109 | 81 | 92 | 95 | 105 | 60 | 74 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.19 | N/A | -2.48 | 1.48 | N/A | N/A | N/A | -299 | 437 | 142 | 27
4 | USA | CA | SAN LUIS OBISPO | 722897 | 93206 | 35.237 | -120.641 | 200 | 14.59 | -8 | NAP | 94-19 | 3C | 12 | 34.2 | 36.5 | 19.9 | 15 | 53.5 | 24.4 | 18.7 | 52.9 | 21.9 | 57.2 | 19 | 58 | 1.9 | 100 | 0.501 | 9 | 23.6 | 89.9 | 64 | 85.3 | 63.3 | 81.8 | 62.9 | 67.5 | 83.2 | 66 | 80.8 | 64.6 | 78.5 | 10.9 | 310 | 61.9 | 83.5 | 71.5 | 60.6 | 79.6 | 70.2 | 59.1 | 75.3 | 68.4 | 31.8 | 83.2 | 30.6 | 80.8 | 29.7 | 78.5 | 78.6 | 24.2 | 20.9 | 18.9 | 29.8 | 99.9 | 2.9 | 4.6 | 27.7 | 103.3 | 26 | 106 | 24.4 | 108.5 | 22.3 | 111.9 | 27.7 | 70.7 | 3.1 | 2.7 | 25.4 | 72.6 | 23.6 | 74.3 | 21.9 | 75.8 | 19.7 | 77.8 | 60 | 53.9 | 54.1 | 56.3 | 57.4 | 60.3 | 63.2 | 66.2 | 66.8 | 66.6 | 63.9 | 58.2 | 53.1 | 6.98 | 5.02 | 5.61 | 5.37 | 5.29 | 4.71 | 3.97 | 3.37 | 3.27 | 4.81 | 5.85 | 5.86 | 4.78 | 79 | 20 | 19 | 8 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23 | 2155 | 345 | 308 | 276 | 238 | 163 | 79 | 23 | 14 | 31 | 91 | 218 | 369 | 3737 | 140 | 133 | 202 | 225 | 319 | 395 | 501 | 521 | 498 | 433 | 251 | 119 | 341 | 1 | 3 | 6 | 9 | 17 | 24 | 60 | 70 | 79 | 58 | 14 | 0 | 3742 | 51 | 65 | 99 | 158 | 249 | 314 | 527 | 577 | 760 | 706 | 208 | 28 | 1194 | 8 | 13 | 19 | 53 | 86 | 97 | 124 | 151 | 290 | 292 | 59 | 2 | 6.9 | 5.3 | 6.1 | 7.1 | 8.3 | 8.9 | 8.3 | 7.4 | 7.3 | 6.9 | 6.4 | 5.3 | 5.1 | 25.9 | 5.3 | 5.3 | 4 | 1.6 | 0.4 | 0.1 | 0 | 0 | 0.4 | 1 | 2.8 | 3.9 | 49.9 | 24.6 | 15.2 | 16.5 | 6.9 | 3.4 | 0.8 | 0.5 | 1.4 | 3.9 | 5.2 | 7.8 | 10.9 | 11.7 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8 | 5.2 | 4.8 | 3.4 | 1.6 | 0.8 | 0.2 | 0.1 | 0.2 | 0.7 | 1.1 | 2.2 | 2.8 | 80.3 | 82.2 | 82 | 87.6 | 89.3 | 90 | 89.5 | 90.4 | 95.9 | 94.8 | 87 | 78.3 | 55.2 | 60.5 | 62 | 62.4 | 64.6 | 65.3 | 66.3 | 65.8 | 66.2 | 63.8 | 61.7 | 54.7 | 73.5 | 74.6 | 76.1 | 78.6 | 80.8 | 82.2 | 83.2 | 83.8 | 88.1 | 87.8 | 80.1 | 71.9 | 55.7 | 57.8 | 58.5 | 59.5 | 62.2 | 63.6 | 65.1 | 65.8 | 64.5 | 61.7 | 58.6 | 54.1 | 69 | 69.1 | 71.2 | 72.7 | 74.7 | 77.2 | 79.8 | 80.1 | 82.2 | 81.7 | 74.3 | 67.1 | 54.7 | 55.8 | 57.5 | 58.3 | 60.2 | 62.1 | 64.4 | 64.5 | 63.7 | 59.8 | 56.8 | 53.4 | 64 | 63.9 | 66.5 | 68.1 | 70.3 | 73.3 | 76.3 | 76.7 | 77.7 | 76 | 69.8 | 63.3 | 53.8 | 53.9 | 56.2 | 56.9 | 58.8 | 61 | 63.2 | 63.5 | 62.8 | 59 | 55.8 | 52.6 | 61.4 | 62.5 | 64.2 | 64.5 | 66.4 | 67.5 | 69 | 69 | 70.2 | 68 | 63.9 | 61.3 | 66.4 | 73 | 77.3 | 80.6 | 83 | 85.4 | 83.3 | 83.5 | 83.2 | 85 | 77.6 | 65.8 | 58.9 | 59.9 | 61 | 61.6 | 63.4 | 64.8 | 66.4 | 66.5 | 66.7 | 64.6 | 61.3 | 59.1 | 65.9 | 69.2 | 71.6 | 75.2 | 77.5 | 79.5 | 80.6 | 81.3 | 82.1 | 79 | 72.1 | 63.5 | 57.1 | 57.8 | 58.9 | 59.5 | 61.1 | 62.9 | 64.9 | 65 | 65 | 62.6 | 59.6 | 56.9 | 63.8 | 65.7 | 67.9 | 70.4 | 72.6 | 76 | 78.6 | 79 | 78.8 | 75.3 | 69.9 | 62.1 | 55.4 | 55.9 | 57.1 | 57.5 | 59.2 | 61.3 | 63.4 | 63.7 | 63.4 | 60.9 | 58 | 54.9 | 62 | 62.6 | 65 | 66.5 | 69.4 | 72.8 | 75.9 | 76.6 | 76.6 | 72.5 | 66.7 | 60.9 | 22 | 20.4 | 21 | 21.3 | 21 | 22 | 21.9 | 22.3 | 23.6 | 24.7 | 23.9 | 22.4 | 31 | 29.3 | 28.8 | 29.8 | 29.5 | 28.5 | 27.4 | 27.7 | 31 | 34.3 | 31.8 | 30 | 16.5 | 15.7 | 15.2 | 15 | 14.1 | 13.2 | 12 | 11.9 | 13 | 14.7 | 14.7 | 16.4 | 21.4 | 22.9 | 23.7 | 25.5 | 25.6 | 25.5 | 24.9 | 25.6 | 26.2 | 27.4 | 25.2 | 19.8 | 13.1 | 13.4 | 13.9 | 13.9 | 13.1 | 12.4 | 11.3 | 11.3 | 11.7 | 12.7 | 13 | 12.4 | 0.308 | 0.324 | 0.329 | 0.334 | 0.343 | 0.353 | 0.351 | 0.343 | 0.341 | 0.344 | 0.308 | 0.313 | 2.563 | 2.523 | 2.515 | 2.499 | 2.491 | 2.453 | 2.514 | 2.503 | 2.514 | 2.505 | 2.577 | 2.561 | 286 | 293 | 300 | 302 | 298 | 293 | 293 | 295 | 291 | 281 | 284 | 277 | 25 | 29 | 31 | 34 | 35 | 36 | 33 | 33 | 31 | 29 | 24 | 23 | 924 | 1197 | 1650 | 2069 | 2358 | 2502 | 2357 | 2171 | 1865 | 1409 | 1047 | 821 | 75 | 128 | 119 | 141 | 134 | 98 | 79 | 74 | 74 | 88 | 56 | 79 | N/A | N/A | N/A | 1.37 | N/A | N/A | N/A | -436 | 463 | N/A | 1.03 | N/A | -2.21 | 1.26 | N/A | N/A | N/A | -284 | 373 | 101 | 28
4 | USA | CA | CHINO | 722899 | 03179 | 33.975 | -117.636 | 650 | 14.35 | -8 | NAP | 98-19 | 3B | 12 | 34.3 | 36.6 | 6.3 | 7.8 | 65.3 | 12.2 | 10.5 | 65.9 | 24.5 | 62.7 | 20.6 | 63.3 | 1.7 | 10 | 0.438 | 8 | 31.7 | 101.1 | 69.6 | 98.2 | 69 | 95.1 | 68 | 73.6 | 94.2 | 72.1 | 92.1 | 70.7 | 90.1 | 11.4 | 270 | 67.3 | 103 | 80.7 | 65.2 | 95.5 | 79.2 | 63.7 | 90.4 | 77.1 | 37.4 | 94.7 | 36 | 92.3 | 34.8 | 90 | 85.1 | 18.8 | 17.2 | 16 | 29.5 | 108.1 | 2.5 | 4.3 | 27.7 | 111.2 | 26.3 | 113.7 | 24.9 | 116.1 | 23.1 | 119.3 | 27.3 | 76.1 | 2.3 | 2.9 | 25.7 | 78.2 | 24.3 | 79.8 | 23 | 81.4 | 21.3 | 83.5 | 65.1 | 55 | 55.1 | 58.5 | 61.5 | 66.3 | 71.6 | 77.4 | 77.8 | 75 | 67.8 | 60.1 | 53.9 | 10.08 | 5.73 | 5.7 | 5.73 | 5.88 | 5.08 | 5 | 4.54 | 4.38 | 5.71 | 5.67 | 5.8 | 5.2 | 60 | 17 | 13 | 4 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 21 | 1541 | 313 | 280 | 214 | 136 | 44 | 5 | 0 | 0 | 2 | 35 | 168 | 344 | 5557 | 173 | 156 | 268 | 347 | 505 | 649 | 849 | 861 | 750 | 551 | 305 | 143 | 1563 | 4 | 3 | 12 | 31 | 84 | 204 | 384 | 396 | 302 | 121 | 21 | 1 | 19567 | 169 | 206 | 396 | 714 | 1184 | 2324 | 4273 | 4504 | 3446 | 1699 | 550 | 102 | 10162 | 26 | 52 | 123 | 280 | 516 | 1145 | 2400 | 2623 | 1964 | 824 | 197 | 12 | 5.3 | 4.3 | 4.5 | 5.2 | 6.2 | 6.8 | 6.8 | 6.5 | 6 | 5.2 | 4.7 | 4 | 3.9 | 11.5 | 2.3 | 2.5 | 1.4 | 1 | 0.2 | 0 | 0.1 | 0 | 0.2 | 0.5 | 1.2 | 1.9 | 24.4 | 8.4 | 8.4 | 3.4 | 2.9 | 0.9 | 0.1 | 0.9 | 0.2 | 0.5 | 5.5 | 2.2 | 8.5 | 4.4 | 0.4 | 0.2 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0.4 | 0.2 | 5.4 | 2.2 | 2.1 | 0.8 | 0.6 | 0.2 | 0 | 0.2 | 0 | 0.1 | 1.2 | 0.5 | 1.9 | 83.6 | 85.7 | 89.5 | 94.4 | 97.3 | 102.1 | 104.1 | 105.2 | 105.7 | 99 | 91.4 | 81.6 | 55 | 56.7 | 60.8 | 60.4 | 64.9 | 68.3 | 71.8 | 70.2 | 70.1 | 64.6 | 59.2 | 55.8 | 78.9 | 80.8 | 83.4 | 87.5 | 91.1 | 95.3 | 99.1 | 100.1 | 100 | 94 | 85.8 | 76.9 | 54.6 | 56 | 58.8 | 59.9 | 63.9 | 68.2 | 71 | 70.1 | 69.6 | 62.5 | 58.1 | 53.8 | 74.6 | 74.8 | 78.4 | 82 | 85.9 | 90.8 | 95.5 | 97.1 | 96.3 | 89.7 | 80.7 | 72.4 | 53.4 | 54.4 | 57.7 | 59 | 63.4 | 67.3 | 70.3 | 69.4 | 68.4 | 61.5 | 56.6 | 52 | 70.1 | 69.2 | 72.9 | 76.9 | 80.8 | 86.9 | 92.2 | 93.2 | 91.4 | 83.9 | 75.1 | 67.4 | 51.9 | 53.2 | 56.6 | 58.1 | 62.7 | 66.2 | 69.6 | 68.9 | 67 | 60.8 | 55.3 | 51.7 | 60.9 | 61.1 | 65 | 66.1 | 70.7 | 72.3 | 76.6 | 74.9 | 74.7 | 69.7 | 62.9 | 60.2 | 71.8 | 72.9 | 81.4 | 85.7 | 89.8 | 93 | 94.2 | 97.3 | 97.2 | 87.5 | 76.9 | 69.2 | 58.2 | 58.7 | 61.8 | 63 | 67.4 | 70.1 | 73.9 | 72.8 | 72.6 | 67.2 | 60.8 | 57.9 | 68.7 | 71.7 | 77.2 | 80.4 | 86.3 | 90.1 | 93.1 | 94.2 | 94.1 | 84 | 76.9 | 66.4 | 56.4 | 56.9 | 59.7 | 60.8 | 65.2 | 68.4 | 72.2 | 71.3 | 70.6 | 65.1 | 59.3 | 56.1 | 66.9 | 69.6 | 73.8 | 77.5 | 82.1 | 87.7 | 90.9 | 92.1 | 90.7 | 81.7 | 73.8 | 64.8 | 54.6 | 55.1 | 57.9 | 59.1 | 63 | 66.9 | 70.6 | 69.9 | 68.7 | 63.3 | 57.8 | 54.2 | 64.8 | 65.5 | 69.5 | 73.8 | 78.1 | 84.8 | 88.6 | 90 | 87 | 77.6 | 70.5 | 62.8 | 26.6 | 25.1 | 25.8 | 26.6 | 25.9 | 28 | 30.2 | 31.7 | 31.3 | 29.3 | 29.1 | 26.6 | 35.8 | 37.2 | 36.2 | 37.6 | 37.1 | 35.9 | 33.9 | 36.2 | 38.4 | 40.2 | 38.5 | 36.2 | 16.5 | 16.7 | 16 | 15 | 14.3 | 12.6 | 11.2 | 11.9 | 12.5 | 14.1 | 15.7 | 17.1 | 27.3 | 29.3 | 30.1 | 31.8 | 32.1 | 32.7 | 30.9 | 32.3 | 33.3 | 32.1 | 30.9 | 26.6 | 14.2 | 14.6 | 14.6 | 14.2 | 13.6 | 12.4 | 11.5 | 11.6 | 12.2 | 12.9 | 14.2 | 14 | 0.309 | 0.317 | 0.341 | 0.354 | 0.355 | 0.366 | 0.379 | 0.363 | 0.348 | 0.343 | 0.304 | 0.303 | 2.543 | 2.533 | 2.443 | 2.412 | 2.442 | 2.42 | 2.448 | 2.48 | 2.509 | 2.498 | 2.596 | 2.594 | 288 | 297 | 297 | 296 | 295 | 290 | 285 | 289 | 290 | 284 | 288 | 285 | 26 | 29 | 34 | 37 | 36 | 37 | 36 | 34 | 32 | 30 | 24 | 23 | 1021 | 1304 | 1753 | 2132 | 2327 | 2494 | 2418 | 2291 | 1947 | 1481 | 1137 | 926 | 71 | 128 | 89 | 99 | 129 | 131 | 115 | 59 | 62 | 93 | 57 | 65 | 2.66 | 1.24 | -5.89 | 2.05 | N/A | N/A | N/A | -414 | 994 | 536 | 1.13 | N/A | -3.06 | 1.3 | N/A | N/A | N/A | -202 | 401 | 202 | 51
4 | USA | CA | SAN DIEGO INTL | 722900 | 23188 | 32.734 | -117.183 | 15 | 14.69 | -8 | NAP | 94-19 | 3B | 12 | 45.3 | 47.2 | 16.8 | 12.9 | 61.2 | 21.9 | 16.4 | 61.5 | 20.2 | 59.7 | 17.9 | 59.6 | 1.8 | 340 | 0.353 | 8 | 8.6 | 84.8 | 64.4 | 81.6 | 65.6 | 79 | 65.8 | 71.4 | 78.4 | 70.3 | 77 | 69.3 | 75.6 | 8.5 | 300 | 68.9 | 106.1 | 75.1 | 67.7 | 102 | 74.4 | 66.7 | 98.4 | 73.6 | 35.2 | 78.6 | 34.3 | 77.2 | 33.3 | 75.8 | 76.1 | 16.7 | 14.6 | 12.7 | 41.7 | 92.5 | 2 | 4.5 | 40.3 | 95.7 | 39.1 | 98.4 | 37.9 | 100.9 | 36.4 | 104.2 | 34.3 | 73.3 | 2.2 | 1.8 | 32.7 | 74.6 | 31.4 | 75.6 | 30.1 | 76.6 | 28.5 | 77.9 | 64.1 | 58 | 58.3 | 60.2 | 61.9 | 64 | 66.4 | 70.1 | 71.8 | 71.1 | 67.4 | 62.2 | 57.5 | 6.22 | 4.08 | 3.91 | 3.72 | 3.94 | 3.43 | 2.92 | 3.21 | 3.27 | 3.97 | 4.06 | 4.29 | 3.62 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1101 | 221 | 192 | 156 | 108 | 57 | 15 | 1 | 0 | 0 | 16 | 103 | 232 | 5157 | 248 | 232 | 318 | 358 | 435 | 493 | 622 | 676 | 634 | 540 | 367 | 234 | 784 | 3 | 4 | 9 | 17 | 27 | 58 | 158 | 211 | 184 | 91 | 21 | 1 | 2415 | 37 | 40 | 72 | 109 | 105 | 67 | 271 | 548 | 614 | 386 | 154 | 12 | 469 | 2 | 6 | 15 | 27 | 36 | 10 | 21 | 70 | 126 | 114 | 42 | 0 | 5.9 | 4.7 | 5.7 | 6.1 | 6.9 | 6.9 | 6.8 | 6.5 | 6.4 | 6.2 | 5.2 | 4.5 | 4.5 | 8.7 | 1.7 | 1.6 | 1.6 | 0.7 | 0.2 | 0 | 0 | 0 | 0.2 | 0.3 | 1.2 | 1.3 | 19.9 | 6.1 | 6.9 | 6.3 | 2.9 | 1.3 | 0.7 | 0.1 | 0.3 | 1.4 | 2 | 5.7 | 5.6 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 3.9 | 1.7 | 1.7 | 1.6 | 0.8 | 0.3 | 0.1 | 0 | 0 | 0.4 | 0.4 | 1.3 | 1.2 | 78.5 | 79.8 | 81.6 | 83.9 | 84.9 | 80.4 | 82.4 | 85.7 | 88.9 | 88.9 | 85.7 | 75.6 | 54.4 | 55.3 | 58 | 57.2 | 58.6 | 66.8 | 69.7 | 69.6 | 69 | 62.2 | 59.2 | 52.9 | 73.6 | 73.2 | 74.6 | 76.4 | 75.2 | 75.3 | 79.3 | 81.8 | 83.3 | 83 | 78.1 | 70.9 | 53.2 | 54.3 | 55.7 | 57.4 | 61.9 | 65.8 | 68.8 | 69.7 | 68.7 | 61.3 | 56.5 | 53.7 | 69.5 | 68.6 | 69.8 | 71.5 | 70.9 | 72.5 | 76.9 | 79 | 80 | 77.8 | 73.2 | 67.3 | 53.6 | 54.3 | 56.3 | 58 | 61.7 | 64.4 | 68.1 | 69.1 | 69.1 | 62.5 | 56.3 | 54.2 | 65.5 | 65 | 66.4 | 68 | 68.4 | 70.9 | 74.9 | 76.9 | 77.3 | 74 | 69.5 | 64.7 | 53.8 | 54.7 | 56.4 | 58.3 | 60.6 | 63.3 | 67.2 | 68.3 | 68.3 | 63.2 | 57.7 | 54.9 | 60.9 | 61.2 | 62.2 | 63.4 | 66.1 | 68.4 | 71.9 | 72.8 | 73.3 | 70.3 | 64.9 | 62.2 | 64.6 | 66.4 | 70.1 | 70.3 | 73.1 | 76 | 79.3 | 81.2 | 81.6 | 77.6 | 69.8 | 65.6 | 59.3 | 59.5 | 60.2 | 61.7 | 64.2 | 66.8 | 69.9 | 71.2 | 71.7 | 67.9 | 63.1 | 60.2 | 63.6 | 64.6 | 67.1 | 68.9 | 70.7 | 73.6 | 76.6 | 78.2 | 78.7 | 74.6 | 68.1 | 64.2 | 58.2 | 58.3 | 59.1 | 60.3 | 62.8 | 65.5 | 68.9 | 70.1 | 70.5 | 66.3 | 61.8 | 58.9 | 62.6 | 63.4 | 65.3 | 67.2 | 68.8 | 71.6 | 75.1 | 76.7 | 77.1 | 72.6 | 67 | 63 | 57.1 | 57.2 | 58.1 | 59.3 | 61.7 | 64.2 | 67.9 | 69.2 | 69.3 | 64.9 | 60.4 | 57.5 | 61.9 | 62.3 | 63.9 | 65.8 | 67.4 | 70 | 73.9 | 75.4 | 75.6 | 71 | 65.9 | 61.8 | 14.5 | 12.8 | 11.3 | 10.4 | 8 | 7.6 | 8 | 8.6 | 9.5 | 11.5 | 13.9 | 14.5 | 22.1 | 20.7 | 19.3 | 18.7 | 12.8 | 10.7 | 10.3 | 11.4 | 14.2 | 20.4 | 22.2 | 20.1 | 11.1 | 10.4 | 9.5 | 9 | 6 | 4.6 | 4.2 | 4.7 | 6.2 | 11.6 | 12.4 | 11.9 | 13.5 | 13.1 | 12.4 | 13.3 | 10.7 | 11.2 | 9.8 | 10.9 | 12.3 | 14.1 | 14.5 | 13.1 | 8.7 | 7.9 | 7 | 6.9 | 5.2 | 4.8 | 4.2 | 4.6 | 5.6 | 8.6 | 9.4 | 8.7 | 0.317 | 0.328 | 0.341 | 0.352 | 0.372 | 0.371 | 0.4 | 0.399 | 0.365 | 0.372 | 0.325 | 0.328 | 2.55 | 2.532 | 2.479 | 2.453 | 2.418 | 2.424 | 2.426 | 2.408 | 2.479 | 2.432 | 2.555 | 2.545 | 288 | 295 | 298 | 297 | 290 | 289 | 280 | 279 | 286 | 275 | 282 | 277 | 26 | 29 | 33 | 36 | 37 | 37 | 37 | 37 | 33 | 32 | 26 | 25 | 1048 | 1324 | 1731 | 2086 | 2179 | 2260 | 2220 | 2145 | 1857 | 1451 | 1137 | 949 | 64 | 110 | 97 | 115 | 166 | 146 | 150 | 95 | 104 | 106 | 77 | 67 | 0.95 | N/A | -2.65 | 1.69 | N/A | N/A | N/A | -185 | 338 | 162 | 1.15 | N/A | -2.86 | 1.37 | N/A | N/A | N/A | -189 | 414 | 214 | 39
4 | USA | CA | MONTGOMERY-GIBBS | 722903 | 03131 | 32.816 | -117.139 | 417 | 14.48 | -8 | NAP | 98-19 | 3B | 12 | 40.8 | 43.1 | 11.5 | 10 | 63.8 | 16.6 | 12.9 | 63.1 | 18.8 | 58.7 | 16.7 | 58.5 | 1.6 | 110 | 0.365 | 8 | 14.6 | 90.8 | 65.6 | 87.2 | 64.8 | 83.9 | 65 | 71.4 | 83 | 70.2 | 80.8 | 69 | 78.8 | 8.7 | 300 | 67.8 | 103.6 | 76.5 | 66.3 | 98.2 | 75.2 | 65.2 | 94.8 | 74.1 | 35.5 | 83 | 34.3 | 80.9 | 33.4 | 79.2 | 76.5 | 15.8 | 12.9 | 11.9 | 36.5 | 99.5 | 1.9 | 4.4 | 35.2 | 102.7 | 34.1 | 105.3 | 33 | 107.8 | 31.7 | 111 | 31.1 | 73.7 | 2 | 1.8 | 29.7 | 75 | 28.5 | 76.1 | 27.4 | 77.1 | 25.9 | 78.4 | 63.9 | 56.9 | 56.7 | 58.9 | 60.9 | 63.5 | 66.9 | 71.6 | 73.1 | 72 | 67.5 | 61.7 | 56.3 | 7.61 | 5.28 | 4.99 | 4.72 | 4.93 | 4.09 | 3.78 | 4.07 | 4.02 | 5.07 | 5.28 | 5.33 | 4.67 | 10 | 4 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1359 | 256 | 238 | 199 | 141 | 75 | 18 | 1 | 0 | 1 | 30 | 128 | 272 | 5076 | 219 | 189 | 276 | 328 | 419 | 508 | 670 | 716 | 659 | 542 | 351 | 199 | 950 | 6 | 5 | 10 | 19 | 29 | 76 | 206 | 251 | 210 | 107 | 28 | 3 | 5841 | 107 | 101 | 146 | 238 | 233 | 288 | 907 | 1330 | 1301 | 816 | 318 | 56 | 1798 | 12 | 19 | 37 | 78 | 87 | 75 | 217 | 374 | 477 | 315 | 101 | 6 | 5.1 | 4.3 | 5 | 5.3 | 6 | 6 | 5.7 | 5.4 | 5.3 | 5.3 | 4.7 | 4.2 | 4.2 | 10.6 | 2 | 2 | 2 | 0.9 | 0.2 | 0.1 | 0 | 0 | 0.2 | 0.4 | 1.3 | 1.4 | 28.1 | 8.9 | 11.8 | 7.7 | 3.9 | 1.3 | 0.7 | 0.5 | 1.4 | 1.3 | 2.6 | 5.7 | 4.7 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9 | 2.1 | 2.4 | 2 | 1 | 0.3 | 0.2 | 0.1 | 0.2 | 0.3 | 0.6 | 1.4 | 1.2 | 81.8 | 82.9 | 85.1 | 88.2 | 89.7 | 88.1 | 90.3 | 92.5 | 96.6 | 94.4 | 88.5 | 80.4 | 55.6 | 55.9 | 59.1 | 57.4 | 58.9 | 67.2 | 69.1 | 69.3 | 68.3 | 62.8 | 58.4 | 54 | 77 | 76.9 | 77.8 | 80.6 | 80.5 | 80.8 | 85 | 87.9 | 90 | 88 | 82.4 | 74.2 | 53.7 | 54.2 | 56.3 | 57.1 | 60.3 | 66.4 | 69.2 | 69 | 68.3 | 60.1 | 57 | 52.9 | 72.6 | 71.9 | 72.5 | 74.7 | 73.7 | 76.6 | 81.9 | 83.8 | 85.3 | 82.5 | 76.8 | 70.4 | 52.9 | 53.8 | 55.6 | 56.9 | 61.1 | 64.8 | 68.3 | 69 | 67.7 | 60.5 | 55.6 | 52.4 | 67.8 | 66.3 | 68.1 | 70 | 70.3 | 73.5 | 79 | 81 | 81.4 | 77.8 | 72.3 | 65.9 | 51.9 | 53 | 55.9 | 57.4 | 60.1 | 63.6 | 67.5 | 68 | 66.7 | 61.1 | 55.3 | 52.7 | 60.1 | 60.5 | 62.2 | 63.1 | 65.7 | 69 | 72.5 | 73.1 | 73.4 | 70 | 63 | 61 | 70 | 68.8 | 75.4 | 76.8 | 78 | 82.6 | 84.1 | 86.2 | 88.7 | 79.1 | 71.8 | 68 | 58.4 | 58.3 | 60.2 | 60.7 | 63.5 | 67 | 70.7 | 71.2 | 71.5 | 67.2 | 61.4 | 59 | 66.2 | 67.4 | 71 | 72.6 | 74.2 | 78.8 | 81.3 | 82.8 | 83.6 | 77.3 | 71.3 | 65 | 56.9 | 56.8 | 58.8 | 59.4 | 62 | 65.4 | 69.3 | 69.9 | 70 | 65.3 | 60.1 | 57.3 | 64 | 65.3 | 67.7 | 69.4 | 71.3 | 75.2 | 79.4 | 80.4 | 80 | 74.8 | 68.9 | 62.9 | 55.4 | 55.4 | 57.2 | 58.1 | 60.5 | 64.2 | 68.1 | 68.8 | 68.5 | 63.9 | 58.9 | 55.8 | 62.7 | 63.2 | 64.5 | 66.5 | 68 | 72.9 | 77.2 | 78.5 | 77.6 | 71.9 | 67.1 | 61.6 | 19.7 | 18.1 | 16.6 | 15.7 | 12.7 | 12.7 | 13.6 | 14.6 | 15.6 | 17.3 | 19.3 | 19.2 | 27.8 | 28.1 | 26.2 | 26.5 | 21.2 | 18.2 | 17.6 | 19.2 | 22.4 | 27.9 | 27.9 | 27 | 12.6 | 12.7 | 11.6 | 11.4 | 9 | 7 | 6.6 | 7.1 | 8 | 11.9 | 12.6 | 13.5 | 18.6 | 19.7 | 19.1 | 19.1 | 16.9 | 17 | 16.2 | 17.1 | 18.6 | 19.3 | 19.5 | 17.4 | 10.2 | 10.3 | 9.4 | 8.9 | 7.5 | 6.9 | 6.4 | 6.6 | 7.2 | 8.7 | 10.1 | 9.8 | 0.311 | 0.322 | 0.334 | 0.345 | 0.364 | 0.364 | 0.392 | 0.393 | 0.359 | 0.365 | 0.319 | 0.322 | 2.556 | 2.541 | 2.489 | 2.464 | 2.43 | 2.436 | 2.435 | 2.414 | 2.488 | 2.44 | 2.562 | 2.552 | 290 | 297 | 300 | 299 | 292 | 291 | 282 | 281 | 288 | 277 | 284 | 279 | 26 | 29 | 33 | 35 | 37 | 36 | 36 | 36 | 33 | 32 | 26 | 25 | 1049 | 1324 | 1740 | 2099 | 2210 | 2307 | 2251 | 2166 | 1872 | 1461 | 1141 | 950 | 65 | 113 | 96 | 111 | 161 | 141 | 145 | 91 | 98 | 104 | 74 | 67 | 1.98 | N/A | N/A | 3.2 | N/A | N/A | N/A | -364 | 729 | 347 | 1.19 | N/A | -2.9 | 1.35 | N/A | N/A | N/A | -193 | 423 | 223 | 41
4 | USA | CA | BROWN FIELD | 722904 | 03178 | 32.572 | -116.979 | 515 | 14.42 | -8 | NAP | 97-19 | 3C | 12 | 39.1 | 41.8 | 7.9 | 8.4 | 61.8 | 13.2 | 10.9 | 62.2 | 20.5 | 61.1 | 18.3 | 60.5 | 6 | 120 | 0.378 | 8 | 15.8 | 89.9 | 64.3 | 85.8 | 64.6 | 82.4 | 64.8 | 71.5 | 82.3 | 70.1 | 79.9 | 68.9 | 77.8 | 8.4 | 290 | 68 | 105 | 75.3 | 66.5 | 99.5 | 74.2 | 65.6 | 96.3 | 73.5 | 35.5 | 82.5 | 34.4 | 79.9 | 33.3 | 78.1 | 77.7 | 16.2 | 12.9 | 11.9 | 34.6 | 98.3 | 2.4 | 3.5 | 32.9 | 100.8 | 31.5 | 102.8 | 30.1 | 104.8 | 28.4 | 107.4 | 29.7 | 73.5 | 2.5 | 1.9 | 27.9 | 74.9 | 26.4 | 76 | 25 | 77 | 23.2 | 78.4 | 62.7 | 56.2 | 55.5 | 57.7 | 59.8 | 62.8 | 66 | 70 | 71 | 70.5 | 66.3 | 60.9 | 55.6 | 7.34 | 5.58 | 5.18 | 4.67 | 4.7 | 3.98 | 3.45 | 3.63 | 3.61 | 4.8 | 5.09 | 5.63 | 4.9 | 23 | 8 | 6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 1557 | 279 | 269 | 235 | 169 | 91 | 23 | 1 | 1 | 4 | 41 | 152 | 292 | 4669 | 199 | 162 | 239 | 294 | 397 | 479 | 619 | 652 | 614 | 505 | 327 | 182 | 730 | 6 | 5 | 8 | 13 | 23 | 52 | 155 | 188 | 169 | 81 | 28 | 2 | 4630 | 99 | 88 | 136 | 206 | 220 | 209 | 661 | 914 | 1028 | 696 | 329 | 44 | 1354 | 15 | 19 | 41 | 69 | 84 | 53 | 133 | 216 | 338 | 271 | 111 | 4 | 5.2 | 5.4 | 5.9 | 5.3 | 5.8 | 5.6 | 5.1 | 4.7 | 4.5 | 4.5 | 4.8 | 5.1 | 5.5 | 12 | 1.9 | 2.5 | 1.7 | 1 | 0.3 | 0 | 0.1 | 0.1 | 0.2 | 0.6 | 1.2 | 2 | 22.4 | 5 | 10.1 | 3.7 | 2 | 1.6 | 0.2 | 0.9 | 0.2 | 1.2 | 5.6 | 3.5 | 6.3 | 6.4 | 0.2 | 0.1 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.1 | 4.3 | 1.6 | 2.3 | 0.9 | 0.6 | 0.4 | 0 | 0.2 | 0.1 | 0.3 | 1.3 | 0.6 | 1.6 | 82 | 82.8 | 85.2 | 87.9 | 90 | 86.9 | 88.2 | 90.7 | 95.1 | 93.8 | 89.1 | 79.1 | 55.4 | 56.1 | 57.8 | 57.2 | 59.4 | 67 | 70.4 | 69.3 | 67.8 | 61.8 | 57.6 | 53.5 | 76.5 | 75.9 | 77.1 | 80.1 | 80.1 | 79 | 83.5 | 85.3 | 88.1 | 87.5 | 83 | 73.5 | 53.8 | 54.6 | 56.2 | 57.8 | 61.7 | 66.6 | 69.6 | 69.5 | 68.7 | 60.2 | 56.7 | 52.3 | 72.2 | 70.4 | 71.7 | 73.5 | 73.4 | 75.2 | 80.4 | 81.8 | 83.5 | 81.6 | 76.9 | 70 | 52.7 | 53.4 | 56.2 | 57.6 | 61.4 | 64.8 | 68.4 | 69.1 | 68.2 | 60.3 | 55 | 52 | 67.3 | 65.4 | 67 | 69.4 | 70.4 | 72.9 | 77.4 | 79.1 | 80 | 76.4 | 71.9 | 65.6 | 51.9 | 53.1 | 56.1 | 58 | 60.5 | 63.5 | 67.3 | 68.1 | 67.3 | 60.6 | 54.6 | 52.4 | 60.2 | 60.4 | 62.2 | 63.1 | 66.5 | 69.3 | 72.9 | 72.9 | 73.5 | 69.4 | 63.3 | 61.2 | 68.4 | 67.7 | 74.2 | 75.5 | 77.9 | 82.2 | 82.8 | 85.1 | 86.6 | 77.4 | 72.7 | 67.3 | 58.4 | 58.2 | 60.1 | 61.4 | 64.2 | 67 | 70.7 | 71 | 71.7 | 66.8 | 61.3 | 58.8 | 65.9 | 66.8 | 69.7 | 72.6 | 74.2 | 77.8 | 80.6 | 82.1 | 82.7 | 75.9 | 70.6 | 64.3 | 56.9 | 56.8 | 58.7 | 59.8 | 62.4 | 65.6 | 69.2 | 69.5 | 70.1 | 65 | 59.8 | 57.2 | 64.1 | 65.2 | 67.2 | 69.3 | 71.4 | 74.4 | 78.5 | 79.4 | 78.8 | 73.8 | 68.3 | 62.5 | 55.4 | 55.3 | 57.3 | 58.4 | 60.9 | 64.2 | 68 | 68.5 | 68.6 | 63.5 | 58.6 | 55.5 | 62.4 | 63.4 | 64.6 | 66.7 | 68.8 | 72.1 | 76.2 | 77.4 | 76.4 | 71.3 | 66.6 | 61.2 | 20.5 | 19 | 18.6 | 18 | 15.2 | 14.4 | 15 | 15.8 | 17.1 | 18.9 | 20.6 | 20.2 | 27.7 | 28.1 | 28.1 | 27.3 | 22 | 17.8 | 18.5 | 19.7 | 22.9 | 28.7 | 28.8 | 26.8 | 14 | 14.1 | 14 | 13.3 | 10.2 | 7.8 | 7.3 | 7.6 | 9.3 | 14 | 14.1 | 14.4 | 19.4 | 20.8 | 20.8 | 20.5 | 18.8 | 17.5 | 17.1 | 17.9 | 19 | 20 | 20.9 | 18.2 | 11.9 | 12 | 11.5 | 10.6 | 8.9 | 8 | 6.9 | 7.1 | 7.8 | 10.3 | 12 | 11.3 | 0.31 | 0.321 | 0.332 | 0.344 | 0.363 | 0.365 | 0.394 | 0.396 | 0.359 | 0.365 | 0.32 | 0.322 | 2.556 | 2.539 | 2.491 | 2.462 | 2.428 | 2.424 | 2.429 | 2.402 | 2.483 | 2.437 | 2.554 | 2.549 | 291 | 298 | 301 | 300 | 293 | 290 | 282 | 280 | 288 | 277 | 285 | 279 | 26 | 29 | 33 | 35 | 37 | 37 | 36 | 37 | 33 | 32 | 26 | 25 | 1063 | 1335 | 1753 | 2117 | 2235 | 2339 | 2249 | 2161 | 1883 | 1479 | 1153 | 963 | 66 | 111 | 97 | 109 | 162 | 134 | 147 | 99 | 101 | 105 | 72 | 66 | 1.53 | N/A | N/A | 2.59 | 1.37 | 1.26 | N/A | -342 | 565 | 252 | 1.19 | N/A | -2.9 | 1.39 | N/A | N/A | N/A | -191 | 419 | 227 | 33
4 | USA | CA | NORTH ISLAND NAS | 722906 | 93112 | 32.7 | -117.2 | 26 | 14.68 | -8 | NAP | 94-19 | 3B | 12 | 44.9 | 46.3 | 21.1 | 15.9 | 65 | 26.5 | 20.5 | 63.8 | 24.4 | 59.1 | 20.8 | 58.9 | 2.2 | 90 | 0.366 | 8 | 8.8 | 85.1 | 63.8 | 81.5 | 65.1 | 79.1 | 65.8 | 71.4 | 77.9 | 70.3 | 76.7 | 69.3 | 75.5 | 9 | 320 | 69.5 | 108.5 | 74.9 | 67.9 | 102.8 | 74.2 | 66.5 | 97.6 | 73.3 | 35.2 | 78.5 | 34.3 | 76.7 | 33.3 | 75.9 | 80.6 | 18.7 | 16.5 | 14.6 | 40.3 | 93.6 | 2 | 5.4 | 38.9 | 97.5 | 37.8 | 100.7 | 36.7 | 103.8 | 35.2 | 107.7 | 35 | 73.7 | 2.3 | 2.2 | 33.4 | 75.3 | 32 | 76.6 | 30.7 | 77.9 | 29 | 79.5 | 64.2 | 58.1 | 58.5 | 60.2 | 61.8 | 64.2 | 66.6 | 70.1 | 71.7 | 71.2 | 67.5 | 62.4 | 57.7 | 6.26 | 4.47 | 4.07 | 4.02 | 4.06 | 3.58 | 2.98 | 3.1 | 3.1 | 3.97 | 3.95 | 4.65 | 3.79 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1093 | 218 | 188 | 159 | 111 | 56 | 15 | 1 | 0 | 1 | 14 | 103 | 227 | 5187 | 253 | 237 | 317 | 355 | 440 | 497 | 623 | 674 | 635 | 543 | 372 | 241 | 801 | 5 | 5 | 11 | 17 | 30 | 61 | 158 | 209 | 186 | 92 | 25 | 2 | 2473 | 71 | 51 | 80 | 126 | 119 | 59 | 270 | 515 | 605 | 380 | 173 | 24 | 513 | 9 | 7 | 17 | 42 | 51 | 9 | 15 | 62 | 127 | 119 | 53 | 2 | 6.3 | 5.4 | 6.5 | 6.6 | 7.3 | 7.1 | 6.9 | 6.7 | 6.8 | 6.7 | 5.7 | 5.2 | 5.3 | 8.7 | 1.7 | 1.6 | 1.6 | 0.7 | 0.2 | 0 | 0 | 0 | 0.2 | 0.3 | 1.2 | 1.3 | 19.9 | 6.1 | 6.9 | 6.3 | 2.9 | 1.3 | 0.7 | 0.1 | 0.3 | 1.4 | 2 | 5.7 | 5.6 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 3.9 | 1.7 | 1.7 | 1.6 | 0.8 | 0.3 | 0.1 | 0 | 0 | 0.4 | 0.4 | 1.3 | 1.2 | 80.9 | 80.2 | 82.2 | 85.5 | 87 | 79.3 | 82.2 | 85.1 | 89 | 89.8 | 86.6 | 77.5 | 57.4 | 56.7 | 57.6 | 59.2 | 59 | 67.4 | 69.9 | 69.6 | 70.1 | 61.7 | 58.7 | 53.8 | 75.1 | 73.7 | 74.6 | 76.5 | 74.9 | 75.1 | 79.2 | 81.2 | 83.1 | 82.8 | 78.8 | 71.7 | 55.4 | 55.1 | 56.7 | 57.9 | 62.6 | 65 | 68.8 | 69.6 | 68.9 | 60.6 | 57.9 | 54.1 | 70 | 68.5 | 70.1 | 71.5 | 71.4 | 73.1 | 77 | 78.9 | 79.7 | 77.5 | 73 | 67.8 | 54.9 | 55.6 | 57.2 | 58.8 | 61.8 | 63.9 | 67.9 | 68.9 | 69.1 | 62.8 | 57.6 | 55.4 | 65.7 | 65 | 66.5 | 68 | 69 | 71.4 | 75.1 | 76.6 | 77.1 | 73.8 | 69.7 | 64.9 | 55 | 55.4 | 57 | 58.2 | 60.7 | 63.3 | 67 | 67.9 | 68.1 | 63.5 | 58.5 | 55.5 | 62.9 | 61.7 | 62.2 | 63.3 | 66.6 | 69.1 | 72.2 | 72.2 | 73.3 | 70.6 | 64.8 | 62.4 | 66.7 | 66.8 | 69.4 | 70.7 | 73.2 | 75.2 | 78.5 | 79.2 | 81.8 | 76.5 | 70.1 | 65.9 | 60.3 | 59.6 | 60.5 | 61.7 | 64.4 | 66.9 | 70.1 | 70.9 | 71.8 | 68 | 63.2 | 60.4 | 64.3 | 65.6 | 67.4 | 69.3 | 70.2 | 73 | 76.3 | 77.6 | 78.6 | 74.2 | 68.4 | 64.5 | 58.9 | 58.5 | 59.4 | 60.4 | 63.1 | 65.4 | 69 | 69.9 | 70.7 | 66.3 | 62 | 59.2 | 63.7 | 64.2 | 65.8 | 67.5 | 68.6 | 71.1 | 75 | 76.5 | 77 | 72.3 | 67.6 | 63.5 | 57.5 | 57.4 | 58.4 | 59.4 | 61.9 | 64.1 | 68 | 69 | 69.4 | 64.9 | 60.8 | 57.8 | 62.5 | 62.9 | 64.6 | 66.1 | 67.3 | 69.7 | 73.7 | 75.3 | 75.5 | 70.7 | 66.7 | 62.5 | 15.4 | 13.7 | 11.9 | 11.2 | 8.8 | 7.9 | 8.3 | 8.8 | 10 | 12.4 | 14.8 | 15.5 | 23.9 | 21.4 | 19.4 | 19.2 | 13.4 | 10.5 | 10.7 | 11.4 | 14.4 | 21.6 | 22.7 | 21.4 | 10.5 | 9.8 | 8.9 | 8.6 | 6.2 | 4.9 | 4.5 | 4.7 | 5.8 | 9.6 | 10.6 | 11.1 | 14.1 | 13.7 | 12.9 | 13.8 | 11.3 | 10.7 | 10 | 10.6 | 12.6 | 14.1 | 15.1 | 13.3 | 9.1 | 8 | 7.2 | 7.3 | 6.3 | 5.3 | 4.7 | 4.8 | 5.3 | 7.4 | 9 | 9.1 | 0.316 | 0.327 | 0.34 | 0.351 | 0.371 | 0.37 | 0.399 | 0.397 | 0.364 | 0.37 | 0.324 | 0.327 | 2.554 | 2.536 | 2.483 | 2.456 | 2.421 | 2.426 | 2.429 | 2.413 | 2.482 | 2.443 | 2.559 | 2.551 | 288 | 295 | 298 | 297 | 290 | 289 | 280 | 280 | 286 | 276 | 283 | 277 | 26 | 29 | 33 | 36 | 37 | 37 | 36 | 36 | 33 | 32 | 26 | 25 | 1048 | 1324 | 1728 | 2081 | 2166 | 2240 | 2206 | 2136 | 1850 | 1447 | 1135 | 949 | 63 | 109 | 98 | 117 | 168 | 147 | 153 | 97 | 106 | 107 | 78 | 67 | 1.06 | N/A | N/A | 1.93 | N/A | N/A | N/A | N/A | N/A | N/A | 1.15 | N/A | -2.86 | 1.37 | N/A | N/A | N/A | -189 | 414 | 214 | 38
|  |  | SAN DIEGO - GILLESPIE | 722907
4 | USA | CA | IMPERIAL BEACH NOLF | 722909 | 93115 | 32.567 | -117.117 | 24 | 14.68 | -8 | NAP | 07-19 | 3C | 12 | 42.3 | 44.1 | 14.7 | 11.6 | 62.7 | 20.5 | 15.4 | 59.4 | 24.4 | 58.5 | 20.9 | 59.2 | 6 | 90 | 0.393 | 8 | 10.5 | 85.9 | 64.5 | 81.4 | 65.7 | 78.7 | 65.6 | 71.8 | 79.8 | 70.4 | 77.7 | 69.3 | 76 | 8.7 | 300 | 68.9 | 106.1 | 75.7 | 67.6 | 101.6 | 75.2 | 66.4 | 97.5 | 74.1 | 35.5 | 80.1 | 34.4 | 77.8 | 33.4 | 76.2 | 79.9 | 18.7 | 16.5 | 14.8 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 62.5 | 57.1 | 56.5 | 57.8 | 59.8 | 62.2 | 65.5 | 68.8 | 69.8 | 68.9 | 65.3 | 61 | 56.1 | 6.41 | 4.12 | 4.5 | 4.05 | 3.57 | 3.46 | 3.28 | 3.14 | 4.49 | 5.48 | 4.61 | 4.21 | 3.92 | 5 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1496 | 248 | 241 | 227 | 162 | 101 | 30 | 5 | 6 | 16 | 50 | 134 | 276 | 4550 | 221 | 184 | 243 | 294 | 378 | 464 | 584 | 615 | 568 | 476 | 331 | 192 | 566 | 2 | 4 | 5 | 6 | 14 | 44 | 124 | 156 | 134 | 61 | 15 | 1 | 2370 | 45 | 62 | 67 | 72 | 103 | 68 | 191 | 541 | 619 | 394 | 190 | 18 | 570 | 3 | 15 | 19 | 18 | 35 | 8 | 16 | 104 | 197 | 95 | 59 | 1 | 6.6 | 6.5 | 7 | 6.7 | 7.2 | 7.4 | 7 | 6.7 | 6.4 | 6.1 | 5.8 | 6.2 | 6.8 | 7.5 | 1.4 | 0.9 | 1.5 | 0.6 | 0.2 | 0.1 | 0 | 0 | 0.1 | 0.2 | 1.4 | 1.1 | 16.7 | 5.8 | 3.1 | 5.4 | 3.2 | 1.1 | 0.5 | 0.1 | 0.1 | 1.5 | 0.8 | 6.4 | 4.4 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1 | 1.3 | 0.9 | 1.3 | 0.8 | 0.2 | 0.2 | 0 | 0 | 0.3 | 0.2 | 1.4 | 1.1 | 79.3 | 81.9 | 81.5 | 82.4 | 85.4 | 80.3 | 81.4 | 87.2 | 95.3 | 88.3 | 87.7 | 76.6 | 53.9 | 55.7 | 57.9 | 57.7 | 60.1 | 68 | 69.9 | 71.3 | 72 | 63.3 | 57.5 | 51.4 | 73.8 | 74 | 73.4 | 74.5 | 75.3 | 75.3 | 78.1 | 81.5 | 84.6 | 82.2 | 78.7 | 71.1 | 52.9 | 54.4 | 56.8 | 57.8 | 60.2 | 65 | 69.1 | 70.2 | 68.7 | 63 | 56.9 | 53.7 | 69.7 | 68.9 | 68.3 | 70.2 | 70.2 | 72.9 | 76 | 78.6 | 79.5 | 78.1 | 74.2 | 67.2 | 53.3 | 55.6 | 57.6 | 58.7 | 60.7 | 64.1 | 67.7 | 68.9 | 70 | 64.6 | 56.5 | 54.6 | 65.9 | 65.5 | 65.7 | 67.5 | 68 | 71.1 | 74.3 | 76.6 | 76.8 | 74.9 | 70.2 | 64.8 | 54.5 | 55.9 | 57.2 | 58.7 | 59.8 | 63.1 | 66.6 | 68.1 | 68.9 | 64.4 | 57.6 | 54.9 | 60.5 | 62 | 62.7 | 63.6 | 65.4 | 68.3 | 72 | 73.3 | 74.1 | 71.8 | 64.4 | 61.7 | 64.9 | 66.9 | 69.3 | 71.3 | 73.2 | 78 | 80.1 | 83.1 | 86.7 | 79.3 | 70.7 | 65.6 | 59.5 | 59.9 | 60.9 | 61.4 | 63.1 | 66.4 | 70 | 71.1 | 72.3 | 69.2 | 62.5 | 60 | 64.4 | 66 | 68.4 | 68.6 | 69.9 | 73.9 | 76.5 | 79.1 | 80.6 | 76.6 | 68.9 | 64.5 | 58.4 | 58.5 | 59.5 | 60.3 | 61.6 | 65.2 | 68.8 | 69.7 | 70.9 | 67.3 | 61.4 | 58.7 | 63.4 | 64.9 | 65.4 | 67.4 | 68.3 | 71.5 | 74.7 | 77.2 | 78.3 | 75.4 | 68.4 | 63.4 | 57.2 | 57.2 | 58.3 | 59.3 | 60.3 | 64 | 67.6 | 68.8 | 69.6 | 65.5 | 60.1 | 57.1 | 62.4 | 63.6 | 63.9 | 66.4 | 66.6 | 70.1 | 73.1 | 75.7 | 75.9 | 72.7 | 67.3 | 62.3 | 17.8 | 16.9 | 15 | 14.8 | 11.5 | 9.4 | 9.4 | 10.5 | 13.5 | 16.7 | 18.8 | 17.8 | 25.8 | 25.6 | 21.1 | 22.9 | 16.3 | 11.8 | 11.6 | 13.1 | 17.2 | 23.5 | 27.2 | 23 | 13.6 | 14.2 | 12.3 | 13.2 | 8.8 | 6.5 | 5.9 | 6.3 | 8.1 | 13.4 | 15.3 | 14.4 | 16 | 19.6 | 16.3 | 17.8 | 14.1 | 11.7 | 11.7 | 12.8 | 14.9 | 18.8 | 19.2 | 16.1 | 11 | 12.6 | 10.5 | 10.7 | 8 | 6.6 | 6 | 6.5 | 7.4 | 11.7 | 13.1 | 11.5 | 0.315 | 0.327 | 0.339 | 0.352 | 0.372 | 0.373 | 0.4 | 0.399 | 0.366 | 0.368 | 0.324 | 0.326 | 2.556 | 2.537 | 2.486 | 2.453 | 2.417 | 2.417 | 2.424 | 2.406 | 2.477 | 2.448 | 2.557 | 2.552 | 289 | 296 | 298 | 297 | 290 | 288 | 280 | 279 | 286 | 276 | 283 | 278 | 26 | 29 | 33 | 36 | 37 | 37 | 37 | 37 | 33 | 31 | 26 | 25 | 1055 | 1329 | 1734 | 2090 | 2176 | 2253 | 2201 | 2130 | 1853 | 1455 | 1141 | 956 | 64 | 108 | 98 | 116 | 169 | 143 | 155 | 102 | 108 | 108 | 78 | 67 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.17 | N/A | -2.83 | 1.4 | N/A | N/A | N/A | -189 | 414 | 220 | 35
|  |  | SAN-NICHOLAS-ISLAND | 722910
4 | USA | CA | CATALINA | 722920 | 23191 | 33.405 | -118.416 | 1602 | 13.86 | -8 | NAP | 00-19 | 3C | 2 | 42.8 | 44.4 | 4.1 | 7.2 | 65.6 | 8.5 | 9 | 64.7 | 28.1 | 47.8 | 25.6 | 47.5 | 10.7 | 280 | 0.403 | 9 | 13.4 | 90.5 | 63 | 87.7 | 62.4 | 84.5 | 60.9 | 68.3 | 81.9 | 66.9 | 79.9 | 65.4 | 78.1 | 6.5 | 270 | 63.8 | 94 | 72.8 | 62.3 | 89.1 | 70.9 | 61 | 85 | 69.1 | 33.5 | 81.9 | 32.2 | 79.6 | 31 | 77.7 | 73.9 | 23.1 | 18.9 | 16.3 | 40.1 | 97.2 | 1.7 | 3.7 | 38.9 | 99.9 | 37.9 | 102.1 | 37 | 104.2 | 35.8 | 106.9 | 33.7 | 70.9 | 1.6 | 1.7 | 32.5 | 72.1 | 31.6 | 73.1 | 30.7 | 74 | 29.5 | 75.2 | 61.5 | 56.3 | 54.8 | 56.4 | 56.9 | 59.4 | 63.4 | 68.5 | 70.1 | 70.1 | 65.4 | 60.6 | 55.3 | 9.4 | 7.37 | 7.58 | 7.3 | 7.23 | 7.27 | 7.22 | 7.21 | 7.59 | 8.57 | 8.57 | 7.82 | 6.34 | 69 | 16 | 23 | 11 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 13 | 2183 | 286 | 303 | 290 | 268 | 215 | 117 | 41 | 27 | 38 | 103 | 183 | 312 | 4262 | 212 | 156 | 209 | 212 | 293 | 402 | 574 | 624 | 604 | 479 | 320 | 177 | 898 | 17 | 16 | 23 | 26 | 42 | 68 | 151 | 186 | 192 | 117 | 50 | 10 | 6799 | 18 | 31 | 85 | 162 | 307 | 580 | 1145 | 1584 | 1740 | 891 | 247 | 9 | 2087 | 0 | 0 | 9 | 36 | 87 | 206 | 331 | 492 | 626 | 257 | 43 | 0 | 7 | 7.8 | 8.4 | 8.3 | 8.3 | 7.1 | 5.6 | 5.3 | 5.5 | 6.1 | 6.8 | 7.2 | 7.9 | 11.6 | 2.2 | 2.4 | 1.6 | 0.7 | 0.3 | 0.1 | 0.1 | 0 | 0.2 | 0.6 | 1.1 | 2 | 27.4 | 7.9 | 7.5 | 3.7 | 1.8 | 1.1 | 0.3 | 0.6 | 0.1 | 1 | 3.5 | 2 | 7 | 5.1 | 0.2 | 0 | 0.5 | 0.2 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0.2 | 0 | 6.1 | 2.5 | 2.1 | 1.1 | 0.6 | 0.3 | 0.1 | 0.2 | 0 | 0.2 | 1 | 0.6 | 2.1 | 76.7 | 77.9 | 81.3 | 84.6 | 88.1 | 92.8 | 92.9 | 92.8 | 95.2 | 91.1 | 84.9 | 75.1 | 51.5 | 53.1 | 56.3 | 56.3 | 60.4 | 62 | 66.9 | 62.8 | 64.5 | 60.6 | 56.5 | 51 | 73.3 | 73.9 | 75.7 | 78.8 | 81.7 | 85.7 | 86.9 | 88.3 | 90.2 | 86.2 | 80.3 | 71.8 | 50.7 | 51.2 | 53.6 | 55 | 57.9 | 61.4 | 64.7 | 63 | 63.1 | 58.8 | 54.7 | 49.9 | 70.6 | 70.9 | 72.3 | 73.6 | 76.6 | 80.7 | 83.3 | 85.2 | 86.8 | 82.3 | 76.6 | 68.4 | 49.4 | 50.2 | 52.4 | 52.8 | 56.4 | 60.6 | 62.8 | 62.1 | 62.3 | 57.2 | 53 | 48.4 | 67.9 | 67.6 | 68.4 | 69.2 | 72 | 75.7 | 80.5 | 82.2 | 83.1 | 79.2 | 73.1 | 65.5 | 48.5 | 48.8 | 50.7 | 51.9 | 55.1 | 59.2 | 62.3 | 60.9 | 60.5 | 55.6 | 51.6 | 47.7 | 58.1 | 58.5 | 59.7 | 61.5 | 63.9 | 67.4 | 70.2 | 70.1 | 69.8 | 65.7 | 60.5 | 58.3 | 64.6 | 63.9 | 71.2 | 75.4 | 80.4 | 84.9 | 85.7 | 83.5 | 85.6 | 77.6 | 68.1 | 61.7 | 55.7 | 56 | 57.3 | 58.2 | 61.2 | 64.4 | 68.2 | 68.1 | 67.5 | 63.5 | 58.8 | 56.4 | 60.9 | 62.6 | 67.6 | 70.4 | 74.8 | 79.5 | 81.4 | 81.2 | 80.7 | 74.7 | 66.7 | 60.4 | 54 | 53.9 | 55.5 | 56.2 | 59.4 | 62.7 | 66.6 | 66.3 | 65.7 | 61.7 | 57.1 | 54.6 | 60.3 | 62.1 | 65.1 | 66.9 | 70.6 | 75.2 | 78.6 | 79 | 79.9 | 72.3 | 64.9 | 59.3 | 52.3 | 52.3 | 54 | 54.5 | 57.5 | 61.3 | 65 | 64.7 | 63.9 | 60 | 55.7 | 53.1 | 59.3 | 60 | 62.7 | 63.1 | 66.3 | 72.2 | 76 | 76.6 | 76.6 | 69.5 | 64.2 | 57.8 | 9.6 | 9.8 | 11.4 | 12.3 | 12.1 | 13.5 | 14.6 | 14.3 | 13.4 | 11.7 | 10.6 | 9.1 | 12 | 13.7 | 15.2 | 17.9 | 17.5 | 18.4 | 17.2 | 15.2 | 16.1 | 14.8 | 13.3 | 12.4 | 7.4 | 8.7 | 9.5 | 10 | 10.4 | 11.1 | 11.7 | 11.9 | 10.5 | 9 | 7.5 | 7.5 | 10.4 | 11.9 | 13.9 | 15.7 | 15.8 | 17.1 | 16.5 | 15.2 | 15 | 13.8 | 12.2 | 10 | 8.7 | 9.2 | 9.8 | 9.9 | 9.8 | 10.5 | 11.3 | 11.7 | 11.1 | 10 | 8.7 | 8.4 | 0.291 | 0.304 | 0.32 | 0.323 | 0.337 | 0.339 | 0.352 | 0.341 | 0.326 | 0.324 | 0.292 | 0.292 | 2.638 | 2.618 | 2.548 | 2.538 | 2.523 | 2.512 | 2.54 | 2.555 | 2.597 | 2.587 | 2.659 | 2.658 | 298 | 304 | 305 | 306 | 300 | 298 | 293 | 297 | 298 | 292 | 295 | 292 | 23 | 27 | 31 | 33 | 34 | 34 | 33 | 32 | 29 | 27 | 23 | 22 | 1007 | 1289 | 1696 | 2071 | 2146 | 2121 | 2196 | 2115 | 1797 | 1380 | 1098 | 908 | 69 | 110 | 98 | 115 | 185 | 161 | 154 | 103 | 114 | 126 | 85 | 71 | 1.85 | N/A | N/A | N/A | 1.4 | 1.39 | N/A | N/A | N/A | N/A | 1.15 | N/A | -2.92 | 1.4 | N/A | N/A | N/A | -212 | 414 | 196 | 50
|  |  | SAN-CLEMENTE-IS-NAAS | 722925
4 | USA | CA | CAMP PENDLETON MCAS | 722926 | 03154 | 33.3 | -117.35 | 75 | 14.66 | -8 | NAP | 94-19 | 3C | 12 | 31.9 | 34.6 | 10.5 | 9.4 | 63 | 16.8 | 12.9 | 60.5 | 18.9 | 61.4 | 16.4 | 60.4 | 0.6 | 30 | 0.386 | 8 | 20 | 91.3 | 65 | 87.5 | 65 | 84 | 65.2 | 71.6 | 82.9 | 70.3 | 81.1 | 69.2 | 79.4 | 8.8 | 210 | 68 | 103.1 | 76 | 66.3 | 97.2 | 75.4 | 65.2 | 93.3 | 74.6 | 35.4 | 82.8 | 34.3 | 81.2 | 33.3 | 79.5 | 87.1 | 15 | 12.7 | 11.7 | 27.2 | 101 | 3 | 3 | 25 | 103.1 | 23.3 | 104.9 | 21.6 | 106.6 | 19.4 | 108.7 | 25.1 | 75.1 | 3.1 | 3.6 | 22.8 | 77.7 | 21 | 79.8 | 19.2 | 81.9 | 17 | 84.5 | 61.4 | 54.2 | 54.2 | 56.7 | 58.5 | 62.4 | 66 | 69.7 | 70.7 | 69.4 | 64 | 58 | 53.1 | 7.62 | 5.25 | 4.91 | 4.4 | 4.39 | 3.73 | 3.26 | 3.58 | 3.95 | 4.85 | 4.58 | 4.9 | 4.84 | 60 | 16 | 14 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 23 | 1904 | 336 | 303 | 260 | 200 | 98 | 24 | 4 | 6 | 11 | 75 | 218 | 369 | 4238 | 147 | 133 | 210 | 257 | 384 | 479 | 611 | 641 | 582 | 433 | 241 | 120 | 607 | 2 | 2 | 2 | 6 | 17 | 53 | 150 | 182 | 143 | 42 | 7 | 1 | 5829 | 154 | 108 | 176 | 280 | 261 | 294 | 850 | 1289 | 1235 | 766 | 354 | 62 | 1856 | 30 | 26 | 57 | 104 | 108 | 69 | 177 | 372 | 463 | 316 | 127 | 7 | 4 | 3.3 | 3.7 | 4 | 4.5 | 4.7 | 4.6 | 4.6 | 4.4 | 4.1 | 3.8 | 3.2 | 3.2 | 11.7 | 2.1 | 2.8 | 1.7 | 0.8 | 0.3 | 0.1 | 0.2 | 0 | 0.2 | 0.6 | 0.9 | 1.7 | 23.6 | 9.4 | 11.3 | 6.9 | 2.4 | 1.4 | 0.6 | 2.3 | 0.4 | 1.5 | 5.6 | 2.7 | 9.1 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2 | 2.4 | 2.4 | 1.7 | 0.7 | 0.4 | 0.2 | 0.5 | 0.1 | 0.3 | 1.1 | 0.8 | 1.8 | 84 | 84.1 | 87.2 | 90.3 | 91 | 87.8 | 88.7 | 92.6 | 98.2 | 95.3 | 90.4 | 80.5 | 56.6 | 57.9 | 59 | 60.5 | 60.2 | 67.7 | 70.4 | 67.7 | 68 | 63.4 | 59.4 | 55.5 | 78.5 | 77 | 78.7 | 81.8 | 80.8 | 80.4 | 84.2 | 87.6 | 90.1 | 88.6 | 83.8 | 74.9 | 55.4 | 55.6 | 57.5 | 59.1 | 63.3 | 67 | 69.5 | 69.3 | 68.9 | 60.8 | 57.6 | 53.9 | 73.3 | 71.3 | 72.7 | 74.8 | 74.5 | 76.9 | 81.3 | 83.8 | 85 | 82.1 | 77.2 | 70.5 | 54.2 | 54.9 | 57.4 | 58.3 | 63.1 | 65.5 | 68.8 | 68.8 | 67.6 | 61.3 | 56.3 | 54.1 | 67.6 | 66.3 | 68 | 69.9 | 71.2 | 74.3 | 78.8 | 80.9 | 81.1 | 76.9 | 72.2 | 66.2 | 53.9 | 54.9 | 57.4 | 58.7 | 61.8 | 64.5 | 67.8 | 68.4 | 67.6 | 62.1 | 56.5 | 53.4 | 61.9 | 62.1 | 64.5 | 64.5 | 67.8 | 69.5 | 73.1 | 73.1 | 73.6 | 70.2 | 63.8 | 62.1 | 71.8 | 74.2 | 73.4 | 76.8 | 77.7 | 82.1 | 82.9 | 87.3 | 86.6 | 79.5 | 74.5 | 69.3 | 59.6 | 59.5 | 61.4 | 62.2 | 65.4 | 67.8 | 71.1 | 71.1 | 71.4 | 67.4 | 62.1 | 59.6 | 68.2 | 67.8 | 72 | 73.9 | 75.7 | 79.2 | 81.2 | 82.8 | 83.8 | 77.6 | 72.9 | 66.1 | 58 | 57.9 | 59.5 | 60.3 | 63.5 | 66.3 | 69.7 | 69.9 | 69.8 | 65.6 | 60.4 | 58 | 65.8 | 65.6 | 68.3 | 70.4 | 72.6 | 76.2 | 79.3 | 80.8 | 80.8 | 75.5 | 70.6 | 64.4 | 56.5 | 56.5 | 58.2 | 59 | 62 | 64.9 | 68.4 | 68.9 | 68.4 | 64 | 59.1 | 56.2 | 64.1 | 64 | 65.9 | 67.9 | 69.8 | 73.4 | 77.4 | 79 | 78.7 | 72.8 | 68.5 | 62.8 | 26.8 | 23.8 | 22.3 | 22.2 | 17.8 | 16.8 | 18.1 | 20 | 22.3 | 25.7 | 28.7 | 27.4 | 38 | 35.8 | 34.5 | 36.3 | 27.6 | 23.3 | 23 | 26.3 | 30.7 | 39.4 | 39.7 | 36 | 19.4 | 19 | 18.5 | 18.1 | 14.7 | 12.1 | 11 | 12.3 | 14.3 | 19 | 19.8 | 20.4 | 25.1 | 24.1 | 24.6 | 25.4 | 21.9 | 21.3 | 21 | 22.1 | 24.6 | 25.7 | 28 | 24.2 | 15.6 | 15.1 | 15 | 14.4 | 12.6 | 11.4 | 10.2 | 11 | 12.7 | 14.8 | 17.2 | 16.3 | 0.309 | 0.319 | 0.338 | 0.352 | 0.37 | 0.368 | 0.396 | 0.389 | 0.361 | 0.355 | 0.316 | 0.318 | 2.567 | 2.552 | 2.482 | 2.449 | 2.427 | 2.44 | 2.434 | 2.433 | 2.498 | 2.485 | 2.581 | 2.574 | 290 | 298 | 298 | 297 | 291 | 290 | 281 | 282 | 287 | 280 | 285 | 280 | 25 | 29 | 33 | 36 | 37 | 36 | 36 | 36 | 32 | 30 | 25 | 24 | 1033 | 1308 | 1737 | 2095 | 2230 | 2364 | 2337 | 2233 | 1899 | 1454 | 1134 | 934 | 66 | 124 | 91 | 109 | 151 | 146 | 123 | 62 | 78 | 101 | 68 | 68 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.12 | N/A | -3.04 | 1.22 | N/A | N/A | N/A | -193 | 394 | 202 | 49
4 | USA | CA | MCCLELLAN-PALOMAR | 722927 | 03177 | 33.128 | -117.279 | 328 | 14.52 | -8 | NAP | 98-19 | 3C | 12 | 43 | 44.9 | 11.8 | 10.2 | 59.6 | 17.3 | 13.3 | 57.9 | 17.1 | 60.9 | 14.8 | 59.1 | 3.1 | 80 | 0.337 | 8 | 9.1 | 84.3 | 62.9 | 81.1 | 64 | 78.5 | 64.3 | 71 | 77.5 | 69.6 | 75.7 | 68.7 | 74.6 | 6.4 | 250 | 68.6 | 106.4 | 74.3 | 67.3 | 101.5 | 73.5 | 66.2 | 97.7 | 72.7 | 35 | 77.7 | 33.9 | 76 | 33 | 74.8 | 76.3 | 13.4 | 11.9 | 10.7 | 38.5 | 94.4 | 1.7 | 5.1 | 37.3 | 98 | 36.3 | 101 | 35.3 | 103.8 | 34.1 | 107.5 | 32.2 | 73 | 2 | 1.8 | 30.8 | 74.3 | 29.6 | 75.3 | 28.4 | 76.3 | 26.9 | 77.5 | 62.5 | 56.8 | 56.2 | 57.7 | 59.5 | 62.2 | 65 | 69.3 | 70.3 | 69.3 | 65.9 | 60.8 | 56.1 | 6.62 | 5.17 | 4.67 | 4.23 | 4.33 | 3.5 | 2.92 | 3.13 | 3.03 | 4.23 | 4.71 | 4.89 | 4.3 | 8 | 4 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1523 | 261 | 251 | 232 | 175 | 101 | 33 | 1 | 0 | 3 | 42 | 145 | 279 | 4556 | 214 | 176 | 240 | 285 | 378 | 449 | 598 | 628 | 580 | 492 | 325 | 191 | 594 | 6 | 5 | 6 | 10 | 14 | 32 | 134 | 163 | 133 | 69 | 20 | 2 | 1974 | 46 | 42 | 56 | 83 | 96 | 48 | 213 | 336 | 488 | 391 | 154 | 21 | 422 | 5 | 8 | 12 | 25 | 34 | 8 | 20 | 38 | 117 | 112 | 40 | 3 | 4.3 | 3.8 | 4.5 | 4.6 | 5.1 | 5.3 | 4.9 | 4.5 | 4.1 | 4 | 3.8 | 3.6 | 3.8 | 11.3 | 2.3 | 2.3 | 1.6 | 0.9 | 0.3 | 0.1 | 0.1 | 0 | 0.2 | 0.6 | 0.9 | 1.7 | 23 | 9.9 | 10 | 6.3 | 2.1 | 1.1 | 0.8 | 1.7 | 0.4 | 1.1 | 5 | 3 | 8 | 3.5 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4 | 2.4 | 2.2 | 1.5 | 0.6 | 0.3 | 0.2 | 0.4 | 0.1 | 0.2 | 1.1 | 0.8 | 1.7 | 79.1 | 80.1 | 80.6 | 82.7 | 84.2 | 79.5 | 82.2 | 84.2 | 89.5 | 88.3 | 84.4 | 76.7 | 55.7 | 55.6 | 56.6 | 56.8 | 57.8 | 67 | 69.7 | 68.6 | 70.4 | 62.2 | 57.7 | 53.4 | 73.7 | 72.7 | 73.3 | 74.9 | 73.7 | 73.8 | 78.8 | 80.5 | 82.8 | 82.8 | 78.4 | 70.8 | 53.6 | 53.2 | 55 | 56.4 | 60.3 | 65.4 | 68.7 | 68.6 | 67.7 | 59.5 | 56.2 | 52.4 | 70 | 67.9 | 68.1 | 70 | 69.7 | 71.6 | 76.2 | 77.6 | 79.3 | 78.5 | 73 | 66.7 | 52.7 | 53.3 | 54.9 | 56.5 | 60.6 | 64.2 | 68.1 | 68.4 | 68 | 59.9 | 54.7 | 52.5 | 65.7 | 63.8 | 64.3 | 66 | 66.4 | 69.8 | 74.1 | 75.2 | 75.8 | 73.5 | 68.9 | 63.7 | 52.2 | 53.2 | 55.5 | 57.1 | 59.2 | 63.1 | 67.3 | 67.7 | 67 | 61.7 | 55.4 | 52.9 | 60.1 | 60.5 | 61.7 | 62.2 | 64.6 | 67.9 | 72.2 | 72.2 | 72.8 | 69.8 | 63.1 | 61.2 | 66.5 | 65.3 | 69.7 | 70.6 | 71.9 | 75.8 | 78.2 | 78.9 | 82.9 | 75.8 | 68.3 | 66.3 | 58.4 | 58.4 | 59.6 | 60.3 | 62.6 | 66.2 | 70.1 | 70.4 | 71 | 67.1 | 61.3 | 59.3 | 63.8 | 63.6 | 66 | 67.1 | 68.7 | 72.7 | 75.9 | 76.7 | 78.4 | 74.3 | 67.9 | 63 | 57.1 | 57 | 58.3 | 59.1 | 61.5 | 64.9 | 69 | 69.3 | 69.5 | 65.3 | 60 | 57.7 | 62.3 | 62.5 | 64 | 65.3 | 67.1 | 70.4 | 74.6 | 75.2 | 75.9 | 71.7 | 66.3 | 61.9 | 55.7 | 55.7 | 57.2 | 58.1 | 60.3 | 63.8 | 67.9 | 68.4 | 68.3 | 63.9 | 59 | 56.2 | 61.3 | 61.5 | 62.3 | 63.9 | 65.2 | 68.7 | 73.1 | 74.1 | 74.4 | 69.7 | 65 | 60.7 | 15.9 | 14.2 | 12.3 | 11.5 | 9 | 8.2 | 8.5 | 9.1 | 10.6 | 13 | 15.3 | 15.6 | 23 | 21.8 | 20 | 20.2 | 14.7 | 11.3 | 11.2 | 12 | 15.7 | 22 | 22.5 | 21.2 | 12.3 | 12.2 | 11.1 | 10.7 | 7.8 | 5.2 | 4.6 | 5.4 | 7.5 | 12.6 | 13.2 | 13 | 15.4 | 15.2 | 13.7 | 13.8 | 11.1 | 11 | 10.4 | 10.8 | 12.6 | 14.8 | 15.7 | 14.5 | 9.9 | 9.7 | 8.3 | 7.7 | 6.1 | 5.2 | 4.5 | 5 | 6.1 | 9.5 | 10.5 | 10.3 | 0.307 | 0.317 | 0.334 | 0.346 | 0.365 | 0.362 | 0.391 | 0.386 | 0.357 | 0.355 | 0.315 | 0.317 | 2.569 | 2.557 | 2.493 | 2.463 | 2.435 | 2.449 | 2.444 | 2.435 | 2.5 | 2.479 | 2.581 | 2.574 | 291 | 298 | 300 | 298 | 292 | 291 | 282 | 283 | 288 | 280 | 286 | 281 | 25 | 29 | 33 | 35 | 36 | 36 | 36 | 36 | 32 | 30 | 25 | 24 | 1038 | 1314 | 1736 | 2094 | 2218 | 2333 | 2299 | 2203 | 1886 | 1454 | 1135 | 939 | 65 | 119 | 93 | 110 | 155 | 145 | 133 | 74 | 87 | 102 | 71 | 68 | 1.67 | N/A | N/A | 2.45 | 1.71 | 1.58 | N/A | -378 | 551 | 238 | 1.08 | N/A | -2.92 | 1.19 | N/A | N/A | N/A | -176 | 380 | 198 | 45
4 | USA | CA | OCEANSIDE | 722934 | 53121 | 33.219 | -117.349 | 28 | 14.68 | -8 | NAP | 99-19 | 3C | 12 | 34.6 | 36.8 | 17.7 | 13.4 | 55.9 | 22.5 | 16.9 | 54.6 | 16.9 | 58.2 | 15.1 | 59.4 | 1.9 | 30 | 0.369 | 8 | 13.8 | 85.7 | 64.5 | 82.2 | 65.8 | 79.5 | 66.3 | 71.3 | 79.6 | 70.2 | 78 | 69.1 | 76.4 | 8.5 | 250 | 68.3 | 104.2 | 76 | 67 | 99.5 | 75.1 | 66 | 96.1 | 74.2 | 35.1 | 79.5 | 34.1 | 78.4 | 33.2 | 76.6 | 76.6 | 14.4 | 12.5 | 11.3 | 30.1 | 95 | 2.5 | 5 | 28.4 | 98.6 | 26.9 | 101.5 | 25.5 | 104.3 | 23.8 | 107.9 | 27.7 | 73.5 | 2.9 | 1.5 | 25.6 | 74.6 | 23.9 | 75.5 | 22.3 | 76.4 | 20.2 | 77.5 | 61.2 | 53.8 | 54.1 | 56.5 | 58.7 | 62.4 | 65.6 | 69.6 | 69.9 | 68.4 | 63.7 | 58 | 53 | 7.14 | 4.49 | 4.4 | 3.97 | 3.73 | 3.23 | 2.5 | 2.99 | 2.96 | 4.29 | 4.09 | 4.34 | 4.14 | 43 | 14 | 11 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 16 | 1899 | 349 | 307 | 267 | 192 | 91 | 20 | 2 | 1 | 11 | 73 | 215 | 371 | 4125 | 130 | 125 | 202 | 262 | 385 | 468 | 607 | 618 | 551 | 426 | 241 | 110 | 506 | 0 | 1 | 2 | 4 | 11 | 39 | 143 | 155 | 112 | 34 | 5 | 0 | 2680 | 44 | 49 | 70 | 122 | 135 | 76 | 413 | 551 | 622 | 419 | 166 | 13 | 577 | 6 | 7 | 16 | 38 | 52 | 12 | 39 | 67 | 160 | 134 | 44 | 2 | 4.2 | 3.6 | 4.2 | 4.2 | 4.7 | 4.9 | 4.7 | 4.5 | 4.3 | 4.2 | 3.8 | 3.5 | 3.5 | 11.3 | 2.3 | 2.3 | 1.6 | 0.9 | 0.3 | 0.1 | 0.1 | 0 | 0.2 | 0.6 | 0.9 | 1.7 | 23 | 9.9 | 10 | 6.3 | 2.1 | 1.1 | 0.8 | 1.7 | 0.4 | 1.1 | 5 | 3 | 8 | 3.5 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4 | 2.4 | 2.2 | 1.5 | 0.6 | 0.3 | 0.2 | 0.4 | 0.1 | 0.2 | 1.1 | 0.8 | 1.7 | 79.2 | 80.6 | 81.5 | 86.2 | 86.6 | 81.1 | 84.1 | 85.5 | 91 | 89.5 | 85.1 | 75 | 56 | 57.5 | 59 | 60.3 | 58.6 | 67.5 | 70.3 | 69.6 | 70.1 | 63.7 | 59 | 53.8 | 73.3 | 73.3 | 74.2 | 77.1 | 76.1 | 75.5 | 80.5 | 81.6 | 84 | 83.6 | 78.9 | 70.6 | 54.3 | 55.1 | 57.3 | 58.6 | 62.6 | 66.3 | 70 | 69.9 | 69.2 | 61.3 | 57.5 | 53.9 | 69.6 | 68.3 | 68.9 | 71.3 | 71.8 | 73.3 | 78.2 | 79.2 | 80.5 | 78.3 | 73.1 | 66.7 | 54.3 | 55 | 57 | 59.2 | 62.3 | 64.7 | 69.1 | 69.1 | 68.9 | 62.2 | 56.4 | 54.8 | 64.6 | 64.1 | 65.5 | 67.8 | 69.5 | 72 | 76.1 | 77 | 77.1 | 74.2 | 69.6 | 63.8 | 53.9 | 55.1 | 57.3 | 58.7 | 60.9 | 63.8 | 67.9 | 68 | 67.3 | 63.5 | 58 | 54.6 | 60.9 | 61.6 | 62.5 | 65 | 66.2 | 68.6 | 72.7 | 72.6 | 73.2 | 70.3 | 64 | 62 | 67.8 | 70.2 | 71.9 | 77.6 | 75.5 | 77.8 | 79.7 | 81.4 | 84.4 | 77.5 | 70 | 66.4 | 59.2 | 59.2 | 60.4 | 62 | 64.1 | 66.9 | 70.9 | 70.8 | 71.3 | 67.9 | 62.5 | 59.7 | 65.1 | 65.4 | 67.7 | 70.6 | 71.8 | 74.8 | 78 | 79.1 | 80.7 | 75.9 | 68.6 | 63.9 | 57.7 | 57.9 | 59.2 | 60.3 | 62.6 | 65.7 | 69.7 | 69.6 | 69.8 | 66 | 61.2 | 58.2 | 63.7 | 64.4 | 65.9 | 67.9 | 69.4 | 72.7 | 76.8 | 77.5 | 77.7 | 73.2 | 68.3 | 62.7 | 56.3 | 56.6 | 58.1 | 59.1 | 61.5 | 64.5 | 68.7 | 68.7 | 68.4 | 64.5 | 59.7 | 56.7 | 62.5 | 63 | 64 | 66.2 | 67.6 | 70.4 | 75.3 | 76 | 75.4 | 70.9 | 67 | 61.7 | 23.7 | 21.4 | 18.7 | 18.4 | 14.6 | 12.7 | 12.9 | 13.8 | 16.8 | 20.7 | 24.2 | 23.6 | 31.8 | 30.9 | 27.6 | 29 | 21.1 | 15.9 | 15.5 | 17.2 | 22 | 32.2 | 33 | 29.4 | 17.8 | 17.5 | 15.7 | 15.6 | 11.1 | 8.3 | 7.4 | 8.4 | 10.8 | 17.4 | 18.3 | 17.9 | 22.7 | 22.6 | 19.6 | 21.1 | 17.1 | 15.7 | 14.7 | 15.7 | 18.9 | 22.5 | 24.2 | 20.5 | 14.6 | 14.3 | 12.3 | 12.5 | 9.4 | 8.3 | 7.1 | 7.9 | 9.7 | 13.7 | 15.6 | 14.5 | 0.31 | 0.32 | 0.338 | 0.352 | 0.371 | 0.368 | 0.396 | 0.391 | 0.362 | 0.357 | 0.317 | 0.319 | 2.568 | 2.553 | 2.485 | 2.452 | 2.426 | 2.44 | 2.434 | 2.43 | 2.498 | 2.482 | 2.58 | 2.573 | 290 | 297 | 298 | 297 | 290 | 289 | 281 | 281 | 286 | 279 | 285 | 279 | 25 | 29 | 33 | 36 | 37 | 36 | 36 | 36 | 32 | 30 | 25 | 24 | 1033 | 1309 | 1733 | 2090 | 2214 | 2336 | 2314 | 2216 | 1889 | 1450 | 1132 | 935 | 66 | 121 | 92 | 111 | 154 | 147 | 128 | 67 | 82 | 102 | 70 | 68 | 1.01 | N/A | N/A | 2.77 | N/A | N/A | N/A | -218 | 385 | 198 | 1.1 | N/A | -3.01 | 1.19 | N/A | N/A | N/A | -185 | 391 | 202 | 47
4 | USA | CA | LOS ANGELES INTL | 722950 | 23174 | 33.938 | -118.389 | 97 | 14.64 | -8 | NAP | 94-19 | 3C | 2 | 45 | 47 | 12.2 | 10.3 | 62 | 17.5 | 13.4 | 61.2 | 25.6 | 57.5 | 22.4 | 56.6 | 4.2 | 80 | 0.408 | 8 | 10.3 | 84.7 | 63.3 | 81.3 | 64.2 | 78.6 | 64.3 | 70.5 | 78.2 | 69.3 | 76.3 | 68.2 | 75 | 8.6 | 260 | 67.6 | 101.8 | 74.6 | 66.4 | 97.7 | 73.5 | 65.4 | 94 | 72.6 | 34.5 | 78.2 | 33.4 | 76.7 | 32.5 | 74.9 | 76.1 | 20.3 | 17.6 | 16 | 40.4 | 94.3 | 2 | 4.3 | 38.9 | 97.4 | 37.7 | 99.9 | 36.6 | 102.3 | 35.1 | 105.4 | 33.7 | 72.1 | 2.4 | 2 | 32 | 73.5 | 30.5 | 74.7 | 29.2 | 75.8 | 27.4 | 77.2 | 63.4 | 57.9 | 57.6 | 59.1 | 60.6 | 63.2 | 66.1 | 69.3 | 70.2 | 69.8 | 66.8 | 62.1 | 57.6 | 6.28 | 4.89 | 4.73 | 4.12 | 4.35 | 3.52 | 2.67 | 3.07 | 3.35 | 4.13 | 4.92 | 5.08 | 4.2 | 4 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1256 | 227 | 215 | 191 | 147 | 77 | 15 | 2 | 1 | 3 | 29 | 116 | 233 | 4894 | 248 | 213 | 283 | 318 | 409 | 483 | 599 | 628 | 593 | 521 | 363 | 236 | 672 | 8 | 7 | 9 | 15 | 21 | 48 | 136 | 164 | 146 | 86 | 29 | 3 | 2127 | 61 | 57 | 59 | 93 | 86 | 65 | 235 | 387 | 462 | 419 | 178 | 25 | 453 | 8 | 12 | 10 | 25 | 27 | 9 | 26 | 48 | 95 | 139 | 52 | 2 | 7.3 | 6.2 | 7.4 | 7.8 | 8.6 | 8.2 | 7.8 | 7.9 | 7.6 | 7.2 | 6.6 | 6.2 | 6.2 | 12.1 | 2.6 | 2.8 | 1.8 | 0.7 | 0.1 | 0.1 | 0 | 0 | 0.2 | 0.4 | 1.3 | 1.9 | 29.5 | 12.7 | 13.3 | 6.4 | 4.5 | 0.9 | 1 | 0.4 | 1.3 | 1.9 | 3.8 | 7.5 | 8.8 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6 | 2.8 | 3 | 1.7 | 0.9 | 0.2 | 0.2 | 0.1 | 0.2 | 0.4 | 0.6 | 1.5 | 1.9 | 80.7 | 81.4 | 80.9 | 83.4 | 83.9 | 80.6 | 83.3 | 84.7 | 87.9 | 91 | 86.5 | 77.6 | 55.2 | 57 | 57.1 | 58.3 | 60.2 | 66.4 | 70.1 | 70 | 67 | 61.5 | 59 | 53.6 | 74.5 | 73.3 | 73.7 | 75.6 | 74.3 | 75.2 | 78.9 | 80.6 | 82.3 | 83.5 | 78.8 | 72 | 53.7 | 54.3 | 55.1 | 56.7 | 62.7 | 65.1 | 68.7 | 69 | 67.7 | 60.3 | 56.1 | 53.3 | 70.2 | 68.5 | 69 | 70.6 | 71.1 | 72.8 | 76.4 | 78 | 78.9 | 78.2 | 73.9 | 68.1 | 52.8 | 54 | 55.6 | 57.2 | 62.2 | 64.3 | 67.6 | 68 | 67.3 | 61.1 | 55.8 | 52.8 | 66 | 64.4 | 65.5 | 67.1 | 68.5 | 71.1 | 74.4 | 75.8 | 76.1 | 73.9 | 69.9 | 64.8 | 52.7 | 53.9 | 56.1 | 57.2 | 60.7 | 63.3 | 66.6 | 67.1 | 66.7 | 61.8 | 56.2 | 53 | 61.3 | 61.3 | 62 | 63.3 | 67.9 | 68.1 | 71.5 | 71.7 | 72.2 | 69.5 | 64.3 | 61.6 | 66.5 | 68.9 | 68.9 | 72.2 | 74.3 | 77.5 | 79.8 | 80.9 | 81.5 | 77.2 | 70.8 | 64.8 | 59.4 | 59.4 | 60.1 | 61 | 64.8 | 66.2 | 69.8 | 70.3 | 70.2 | 67.2 | 62.3 | 59.7 | 63.8 | 64.3 | 66.2 | 68.6 | 70.8 | 73.8 | 77.1 | 78.1 | 77.7 | 74.5 | 68.1 | 63.1 | 58 | 58.2 | 59 | 59.6 | 63.3 | 65 | 68.5 | 69.1 | 68.9 | 65.5 | 61.1 | 58.5 | 62.2 | 62.7 | 64.4 | 66.2 | 68.9 | 71.8 | 75 | 76.1 | 75.9 | 72 | 66.7 | 62.1 | 56.8 | 57 | 57.9 | 58.4 | 61.9 | 64 | 67.4 | 68 | 67.6 | 64.1 | 60 | 57.2 | 61.1 | 61.4 | 62.6 | 64.6 | 67.1 | 70.2 | 73.3 | 74.5 | 74.4 | 70.1 | 65.5 | 61.1 | 15.1 | 13.7 | 12.5 | 12.3 | 10.5 | 9.7 | 9.9 | 10.3 | 11 | 12.9 | 14.9 | 14.8 | 22.9 | 21.9 | 19.8 | 18.9 | 14.2 | 11.8 | 11.8 | 12.8 | 15.4 | 21.8 | 22.6 | 20.9 | 11.4 | 10.9 | 10 | 8.8 | 6.8 | 5.3 | 5.1 | 5.4 | 6.6 | 10 | 11.7 | 11.8 | 14.4 | 14.3 | 13.1 | 14.1 | 12.1 | 11.6 | 11.4 | 12.2 | 12.8 | 14.7 | 15.4 | 13.6 | 8.6 | 8.4 | 7.6 | 7.4 | 6.3 | 5.4 | 5 | 5.4 | 5.8 | 7.5 | 9 | 8.8 | 0.335 | 0.349 | 0.372 | 0.377 | 0.382 | 0.398 | 0.4 | 0.38 | 0.367 | 0.371 | 0.322 | 0.323 | 2.501 | 2.476 | 2.385 | 2.378 | 2.393 | 2.352 | 2.412 | 2.447 | 2.478 | 2.439 | 2.577 | 2.573 | 278 | 285 | 286 | 289 | 287 | 281 | 279 | 284 | 284 | 273 | 281 | 276 | 27 | 31 | 36 | 38 | 38 | 40 | 37 | 35 | 33 | 31 | 25 | 24 | 998 | 1280 | 1712 | 2096 | 2260 | 2349 | 2353 | 2240 | 1891 | 1435 | 1111 | 905 | 73 | 127 | 98 | 110 | 158 | 146 | 129 | 77 | 80 | 108 | 69 | 69 | 0.72 | N/A | -2.88 | N/A | N/A | N/A | N/A | N/A | 250 | N/A | 1.15 | N/A | -2.97 | 1.31 | N/A | N/A | N/A | -212 | 405 | 194 | 52
4 | USA | CA | TORRANCE-MUNI-AP | 722955 | 03122 | 33.8 | -118.33 | 102 | 14.64 | -8 | NAP | N/A | 3C | 12 | 44.4 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 8 | 11.8 | 87.9 | 62.8 | N/A | N/A | N/A | N/A | 69.8 | 79.9 | N/A | N/A | N/A | N/A | N/A | N/A | 66.2 | N/A | 74.5 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 5.8 | 5.8 | 5.4 | 4.9 | 4 | 3.1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 83.3 | 84.92 | 86.18 | 92.66 | 92.84 | 87.98 | N/A | N/A | N/A | N/A | N/A | N/A | 67.1 | 70.16 | 67.82 | 67.1 | 60.98 | 59.36 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 10.44 | 11.34 | 11.88 | 12.78 | 14.22 | 16.38 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.399 | 0.399 | 0.381 | 0.367 | 0.374 | 0.323 | N/A | N/A | N/A | N/A | N/A | N/A | 2.348 | 2.415 | 2.448 | 2.48 | 2.43 | 2.574 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
4 | USA | CA | LOS ANGELES HAWTHORNE | 722956 | 03167 | 33.923 | -118.334 | 63 | 14.66 | -8 | NAP | 98-19 | 3C | 12 | 44.5 | 45.9 | 11.5 | 9.9 | 65.6 | 17.1 | 13.1 | 64.1 | 17.9 | 58.7 | 15.4 | 59.6 | 1 | 70 | 0.348 | 8 | 11.7 | 88.4 | 63.5 | 84.6 | 63.6 | 81.6 | 63.9 | 70.7 | 80.1 | 69.4 | 78.3 | 68.4 | 77 | 6.9 | 250 | 67.3 | 100.7 | 75.5 | 66 | 96.1 | 74.7 | 64.7 | 91.7 | 73 | 34.6 | 80.1 | 33.5 | 78.7 | 32.6 | 77 | 75.2 | 16.3 | 14 | 12.5 | 39.4 | 97.2 | 2.8 | 5 | 37.4 | 100.8 | 35.7 | 103.7 | 34.1 | 106.5 | 32.1 | 110.1 | 33.4 | 72.3 | 2.1 | 1.7 | 31.8 | 73.5 | 30.6 | 74.5 | 29.3 | 75.4 | 27.8 | 76.6 | 64.7 | 58.8 | 58.6 | 60.7 | 62.2 | 64.5 | 67.2 | 70.9 | 71.5 | 71.2 | 68.4 | 63.5 | 58.1 | 6.62 | 5.11 | 5 | 4.7 | 4.77 | 3.81 | 3 | 3.65 | 3.51 | 4.53 | 5.3 | 5.18 | 4.36 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1039 | 202 | 189 | 152 | 111 | 51 | 8 | 1 | 0 | 1 | 19 | 87 | 218 | 5352 | 275 | 241 | 331 | 365 | 449 | 517 | 648 | 666 | 635 | 570 | 404 | 251 | 913 | 10 | 10 | 18 | 26 | 36 | 75 | 184 | 201 | 185 | 124 | 41 | 3 | 4013 | 115 | 103 | 141 | 197 | 182 | 150 | 563 | 662 | 820 | 715 | 311 | 54 | 1058 | 18 | 25 | 38 | 66 | 66 | 29 | 89 | 111 | 240 | 272 | 100 | 4 | 4.7 | 3.1 | 4.2 | 5 | 5.8 | 6 | 5.8 | 5.8 | 5.5 | 5 | 4 | 3.2 | 3 | 12.1 | 2.6 | 2.8 | 1.8 | 0.7 | 0.1 | 0.1 | 0 | 0 | 0.2 | 0.4 | 1.3 | 1.9 | 29.5 | 12.7 | 13.3 | 6.4 | 4.5 | 0.9 | 1 | 0.4 | 1.3 | 1.9 | 3.8 | 7.5 | 8.8 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6 | 2.8 | 3 | 1.7 | 0.9 | 0.2 | 0.2 | 0.1 | 0.2 | 0.4 | 0.6 | 1.5 | 1.9 | 82.3 | 84 | 84.4 | 88.7 | 88.4 | 84 | 86.8 | 87.2 | 93 | 94.1 | 89.1 | 79.7 | 55.2 | 56.6 | 58 | 59.5 | 60.1 | 66.9 | 70.1 | 69.2 | 68.1 | 62.5 | 59.3 | 54.1 | 77 | 76.5 | 77.7 | 79.2 | 78.7 | 77.7 | 82.1 | 83.1 | 86.2 | 87.1 | 82.2 | 74.1 | 53 | 54.1 | 55.6 | 57.1 | 61 | 65.4 | 68.8 | 68.4 | 67.3 | 60.9 | 57.6 | 53.3 | 72.7 | 71.3 | 72.4 | 73.4 | 73.1 | 74.7 | 79.4 | 80.2 | 81.9 | 81.6 | 76.7 | 70.2 | 52.8 | 54.1 | 55.5 | 57.1 | 61.2 | 64.4 | 68.2 | 67.8 | 67.2 | 61.5 | 55.8 | 52.5 | 68 | 66.3 | 68.2 | 69.6 | 70.2 | 72.6 | 77 | 77.5 | 78.5 | 76.7 | 72.1 | 65.9 | 52.6 | 54.1 | 55.8 | 56.8 | 60 | 63.3 | 67.2 | 67.1 | 66.4 | 62.1 | 56.2 | 52.7 | 60.5 | 61 | 62.1 | 62.8 | 66.1 | 68.4 | 72.3 | 71.6 | 72.3 | 69.7 | 63.8 | 61.1 | 66.7 | 68.8 | 73.8 | 76 | 78.9 | 79.6 | 82.7 | 81.3 | 84.7 | 79.1 | 73.4 | 65.3 | 58.9 | 59.1 | 60.2 | 60.5 | 63.7 | 66.4 | 70.3 | 70.2 | 70.4 | 67.5 | 62.2 | 59.3 | 64.4 | 65.8 | 69.3 | 71.5 | 72.9 | 75.6 | 79.1 | 79.4 | 80.4 | 77.5 | 70.3 | 64.5 | 57.5 | 57.7 | 58.9 | 59.3 | 62.2 | 65.4 | 69.1 | 69 | 69 | 65.6 | 60.9 | 57.8 | 63.9 | 64.4 | 66.8 | 68.7 | 70.3 | 73.5 | 77.2 | 77.8 | 78.3 | 74.5 | 68.5 | 63.2 | 56.3 | 56.5 | 57.7 | 58.2 | 60.9 | 64.3 | 68 | 67.9 | 67.6 | 64.3 | 59.7 | 56.5 | 62.8 | 63.3 | 64.5 | 66.3 | 68.2 | 71.1 | 75.6 | 76.3 | 76.4 | 72.2 | 67.2 | 62.1 | 17.2 | 15.5 | 14.1 | 13.3 | 11.2 | 10.5 | 11.4 | 11.7 | 12.7 | 14.6 | 16.8 | 16.7 | 25.7 | 24.5 | 22.1 | 21.5 | 17.5 | 13.6 | 14 | 14.5 | 18.6 | 24.4 | 26 | 24.3 | 11 | 10.6 | 9.1 | 8.6 | 6.9 | 5.7 | 5.5 | 5.8 | 6.9 | 9.3 | 11.4 | 12 | 16.2 | 16.8 | 15.4 | 15.8 | 13.9 | 12.9 | 13.2 | 13.3 | 15.5 | 16.7 | 17.5 | 15.7 | 8.4 | 8.5 | 7 | 7 | 6.1 | 5.6 | 5.3 | 5.6 | 6.1 | 7 | 9 | 9 | 0.339 | 0.353 | 0.377 | 0.379 | 0.383 | 0.399 | 0.399 | 0.381 | 0.367 | 0.374 | 0.323 | 0.325 | 2.488 | 2.461 | 2.366 | 2.372 | 2.392 | 2.348 | 2.415 | 2.448 | 2.48 | 2.43 | 2.574 | 2.57 | 276 | 284 | 284 | 288 | 286 | 280 | 279 | 284 | 284 | 272 | 281 | 276 | 27 | 31 | 37 | 38 | 38 | 40 | 37 | 35 | 33 | 32 | 25 | 24 | 1000 | 1282 | 1714 | 2098 | 2261 | 2353 | 2354 | 2240 | 1892 | 1437 | 1112 | 907 | 72 | 127 | 97 | 109 | 156 | 146 | 128 | 76 | 80 | 108 | 69 | 69 | 1.37 | N/A | -2.14 | 2.2 | N/A | N/A | N/A | -293 | 612 | 319 | 1.12 | N/A | -2.95 | 1.3 | N/A | N/A | N/A | -209 | 396 | 189 | 52
4 | USA | CA | LONG BEACH | 722970 | 23129 | 33.812 | -118.146 | 31 | 14.68 | -8 | NAP | 94-19 | 3B | 12 | 41.7 | 43.9 | 12 | 10.2 | 69.3 | 18.2 | 13.8 | 66.1 | 20.2 | 56.8 | 17.7 | 59.5 | 1.7 | 300 | 0.356 | 8 | 16.9 | 91.8 | 66 | 88.2 | 66 | 85.1 | 65.4 | 72.1 | 83 | 70.7 | 81.1 | 69.4 | 79.3 | 8.2 | 290 | 68.8 | 105.8 | 76 | 67.2 | 100.3 | 75.3 | 65.9 | 95.5 | 74.3 | 35.7 | 82.9 | 34.6 | 80.9 | 33.5 | 79.6 | 79.5 | 16.6 | 13.7 | 12.1 | 37.2 | 100.6 | 2 | 3.9 | 35.7 | 103.4 | 34.5 | 105.7 | 33.4 | 107.9 | 31.9 | 110.7 | 32.7 | 74.2 | 2.3 | 2.4 | 31.1 | 75.9 | 29.7 | 77.3 | 28.5 | 78.6 | 26.8 | 80.3 | 65.1 | 57.6 | 57.6 | 60.4 | 62.6 | 65.4 | 68.8 | 73 | 74.3 | 73 | 68.2 | 62.2 | 56.9 | 7.63 | 5.08 | 4.84 | 4.58 | 4.88 | 4.03 | 3.6 | 3.62 | 4.01 | 4.98 | 5.05 | 5.15 | 4.31 | 8 | 4 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1139 | 235 | 214 | 157 | 102 | 39 | 5 | 0 | 0 | 0 | 19 | 113 | 255 | 5504 | 240 | 214 | 323 | 379 | 477 | 564 | 714 | 755 | 691 | 566 | 366 | 215 | 1159 | 6 | 6 | 14 | 31 | 52 | 119 | 249 | 290 | 242 | 119 | 29 | 2 | 6898 | 131 | 113 | 186 | 312 | 299 | 426 | 1158 | 1615 | 1442 | 839 | 320 | 57 | 2237 | 25 | 31 | 54 | 106 | 104 | 105 | 297 | 526 | 535 | 338 | 109 | 7 | 5.1 | 4 | 4.8 | 5.4 | 6.1 | 6 | 5.9 | 5.8 | 5.5 | 5.1 | 4.5 | 3.9 | 3.9 | 12.4 | 2.8 | 3.2 | 1.8 | 0.7 | 0.3 | 0.1 | 0 | 0 | 0.1 | 0.5 | 0.9 | 2.1 | 24.9 | 12.8 | 13 | 6 | 2 | 2.1 | 0.9 | 0.4 | 0.1 | 1.6 | 4.4 | 2.2 | 9.8 | 4.8 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3.2 | 3 | 1.7 | 0.6 | 0.5 | 0.2 | 0.1 | 0 | 0.3 | 0.9 | 0.7 | 2.1 | 83.4 | 85.3 | 86.7 | 90.2 | 90.3 | 89.5 | 90.7 | 94.2 | 97 | 96.4 | 90 | 80 | 56.6 | 57.4 | 59.1 | 59.7 | 60.1 | 67.2 | 69.1 | 69.8 | 69.6 | 62.6 | 60 | 54.2 | 77.7 | 76.9 | 79.1 | 82.3 | 81.5 | 82.3 | 86.3 | 89.1 | 90.5 | 88.9 | 82.6 | 74.4 | 54.7 | 55.7 | 56.7 | 58.6 | 62.7 | 66.3 | 68.5 | 69 | 68.8 | 61.8 | 56.8 | 54.2 | 72.6 | 71 | 73.3 | 76.5 | 76 | 78.4 | 83.2 | 85.6 | 86 | 82.7 | 76.6 | 69.8 | 54.1 | 54.7 | 56.5 | 58.2 | 62.4 | 65.4 | 68 | 68.6 | 67.8 | 61.6 | 56.5 | 53.1 | 67.4 | 66.3 | 68.9 | 71.4 | 72.1 | 75.4 | 80.2 | 82.4 | 81.9 | 77.6 | 71.9 | 65.8 | 53.7 | 54.7 | 56.7 | 57.8 | 61.3 | 64.4 | 67.6 | 68.4 | 67.2 | 62.4 | 57.1 | 53.3 | 61.7 | 61.9 | 64.3 | 65.5 | 68.5 | 69.5 | 72.6 | 74 | 74.8 | 70.5 | 65.1 | 61.8 | 68.1 | 72.2 | 75.7 | 77.7 | 78.2 | 82.2 | 83.9 | 86.9 | 85.9 | 79.3 | 74 | 67.2 | 59.8 | 59.8 | 61.7 | 62.4 | 65.6 | 67.9 | 70.9 | 71.9 | 72.1 | 68.2 | 62.8 | 59.8 | 65.2 | 67.7 | 70.6 | 73.5 | 75 | 79.3 | 81.1 | 83 | 82.8 | 78.4 | 70.3 | 65.3 | 58.4 | 58.4 | 59.9 | 60.6 | 63.8 | 66.4 | 69.6 | 70.6 | 70.3 | 66.2 | 61.3 | 58.3 | 64.3 | 65.2 | 67.7 | 70.1 | 72.4 | 76.2 | 79.2 | 80.8 | 81 | 76.1 | 69.2 | 63.4 | 57.1 | 57.1 | 58.7 | 59.3 | 62.3 | 65.2 | 68.6 | 69.3 | 68.9 | 64.5 | 59.9 | 56.9 | 63.5 | 63.3 | 65.6 | 67.7 | 70.2 | 73.8 | 77.6 | 78.9 | 78.9 | 72.9 | 67.4 | 61.8 | 19.1 | 17.1 | 16.5 | 16.7 | 14 | 13.9 | 15.5 | 16.9 | 17.1 | 17.5 | 19 | 18.7 | 28.7 | 26.5 | 26.3 | 26.8 | 21.9 | 19.8 | 20 | 21.9 | 23.8 | 28 | 28.2 | 26.7 | 12.6 | 11.7 | 10.6 | 10 | 8.1 | 7.3 | 7.1 | 7.6 | 7.8 | 10.2 | 11.6 | 12.9 | 17.8 | 18.1 | 18 | 20.1 | 18.1 | 18 | 17.6 | 19.2 | 20.3 | 20.1 | 19.4 | 16.8 | 9.8 | 9.5 | 8.8 | 8.9 | 7.5 | 7.1 | 6.6 | 7.2 | 7.3 | 8.5 | 9.8 | 10.1 | 0.339 | 0.352 | 0.377 | 0.375 | 0.376 | 0.392 | 0.392 | 0.376 | 0.362 | 0.37 | 0.321 | 0.321 | 2.494 | 2.469 | 2.369 | 2.389 | 2.417 | 2.372 | 2.44 | 2.47 | 2.501 | 2.45 | 2.588 | 2.587 | 276 | 285 | 285 | 290 | 289 | 282 | 282 | 285 | 286 | 274 | 282 | 278 | 27 | 31 | 37 | 38 | 37 | 39 | 36 | 35 | 32 | 31 | 25 | 24 | 1007 | 1289 | 1721 | 2100 | 2253 | 2345 | 2346 | 2235 | 1889 | 1436 | 1116 | 912 | 71 | 125 | 95 | 108 | 156 | 146 | 129 | 74 | 81 | 108 | 69 | 69 | 0.77 | N/A | -4.72 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.12 | N/A | -2.97 | 1.26 | N/A | N/A | N/A | -202 | 396 | 193 | 54
4 | USA | CA | LOS ALAMITOS AAF | 722975 | 53141 | 33.79 | -118.052 | 35 | 14.68 | -8 | NAP | 08-19 | 3B | 12 | 38.9 | 41.3 | 9.5 | 9 | 69.6 | 17.3 | 13.2 | 66.2 | 21.1 | 62.7 | 18.5 | 59.4 | 2.1 | 20 | 0.372 | 8 | 17.6 | 92.1 | 66.1 | 88.5 | 65.9 | 85.5 | 65.8 | 72.4 | 83.1 | 71.2 | 80.9 | 70.1 | 79.3 | 9.3 | 210 | 69.5 | 108.6 | 74.7 | 68.3 | 104 | 74.4 | 67.1 | 99.7 | 74 | 36 | 82.8 | 35 | 81.1 | 34 | 79.6 | 76.6 | 16.8 | 14.4 | 12.5 | 34.3 | 102.3 | 1.7 | 4.2 | 33.1 | 105.3 | 32.1 | 107.7 | 31.2 | 110.1 | 30 | 113.2 | 31.2 | 74.2 | 1.6 | 1.8 | 30.1 | 75.5 | 29.2 | 76.6 | 28.3 | 77.6 | 27.2 | 78.9 | 64.1 | 57 | 56.4 | 59.4 | 62 | 64.2 | 67.7 | 71.8 | 72.9 | 72.6 | 67.8 | 61.5 | 55.6 | 7.5 | 4.56 | 5.26 | 4.41 | 4.29 | 3.63 | 3.11 | 3.59 | 3.83 | 4.86 | 4.81 | 4.82 | 4.28 | 16 | 4 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 1292 | 253 | 245 | 184 | 111 | 56 | 5 | 0 | 0 | 1 | 21 | 124 | 292 | 5167 | 219 | 187 | 290 | 360 | 439 | 530 | 674 | 710 | 679 | 553 | 347 | 179 | 970 | 3 | 5 | 9 | 21 | 30 | 85 | 210 | 245 | 230 | 110 | 21 | 1 | 7083 | 120 | 121 | 187 | 344 | 266 | 333 | 1102 | 1492 | 1658 | 1028 | 378 | 54 | 2363 | 22 | 34 | 60 | 117 | 118 | 85 | 268 | 451 | 659 | 419 | 122 | 8 | 4.9 | 3.9 | 4.8 | 5.1 | 5.9 | 6.2 | 5.8 | 5.6 | 5.1 | 4.7 | 4.3 | 3.8 | 4.1 | 12.4 | 2.8 | 3.2 | 1.8 | 0.7 | 0.3 | 0.1 | 0 | 0 | 0.1 | 0.5 | 0.9 | 2.1 | 24.9 | 12.8 | 13 | 6 | 2 | 2.1 | 0.9 | 0.4 | 0.1 | 1.6 | 4.4 | 2.2 | 9.8 | 4.8 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3.2 | 3 | 1.7 | 0.6 | 0.5 | 0.2 | 0.1 | 0 | 0.3 | 0.9 | 0.7 | 2.1 | 83.6 | 85.5 | 87.4 | 90.8 | 92.9 | 88.7 | 90.6 | 92.4 | 98.5 | 97.4 | 90.1 | 80.4 | 55.8 | 57.6 | 59.6 | 59.7 | 60.6 | 68.1 | 68.5 | 68.1 | 68.2 | 63.6 | 60.5 | 52.7 | 77.2 | 77.2 | 78.7 | 82.4 | 82.1 | 80.9 | 86 | 88.5 | 91.1 | 90 | 83.3 | 73.6 | 55.2 | 56.1 | 57.4 | 58.4 | 60.6 | 66.9 | 68.9 | 68.9 | 69.4 | 62.9 | 57.8 | 54.7 | 73.3 | 71.4 | 73.7 | 77.3 | 74.7 | 77.4 | 82.6 | 85.1 | 87.2 | 84.3 | 77.9 | 68.9 | 54.3 | 57.3 | 58.1 | 57.7 | 62.5 | 65.8 | 69 | 68.8 | 68.5 | 62.5 | 56.6 | 53.4 | 68.3 | 67 | 69.2 | 71.9 | 71.3 | 74.7 | 79.9 | 81.7 | 83.1 | 79 | 73.1 | 65.3 | 54.9 | 56.8 | 57.9 | 58.4 | 61.1 | 64.8 | 68.4 | 68.5 | 68.7 | 62.7 | 57 | 54.6 | 62.2 | 65.2 | 65.2 | 65.2 | 66.5 | 70.2 | 72.8 | 73.5 | 74.7 | 72.6 | 65.4 | 64 | 68.3 | 70.6 | 73.8 | 77.7 | 76.1 | 82.9 | 82.8 | 84.9 | 89.3 | 80.8 | 73.9 | 66.5 | 60.4 | 62.1 | 62.4 | 62.9 | 65 | 68.3 | 71.2 | 72.1 | 72.5 | 69.7 | 63.5 | 61.2 | 65 | 67.5 | 71 | 73.3 | 74.5 | 78.7 | 81.6 | 82.2 | 84 | 78.5 | 71.2 | 64.9 | 59.2 | 60.2 | 60.9 | 61.4 | 63.5 | 66.8 | 70.1 | 71 | 71.1 | 68 | 62.1 | 59.5 | 63.6 | 65.8 | 68.9 | 70.9 | 71.1 | 75.7 | 79.8 | 80.2 | 80.9 | 76.2 | 69.5 | 62.6 | 57.8 | 58.6 | 59.5 | 60.1 | 62.1 | 65.6 | 68.9 | 69.6 | 69.8 | 66.1 | 60.6 | 58 | 63.3 | 64 | 66.3 | 68.2 | 69.3 | 73.4 | 77.8 | 78.1 | 78.9 | 73.6 | 67.7 | 61.3 | 22.6 | 19.7 | 19 | 19.3 | 15.2 | 14.4 | 15.8 | 17.6 | 19.6 | 21 | 23 | 20.5 | 31.7 | 29.1 | 29.3 | 31.5 | 23.5 | 20.7 | 21 | 23.9 | 27.3 | 32.4 | 32.7 | 29.1 | 15.1 | 14.7 | 13.6 | 11.8 | 9.2 | 8 | 7.5 | 7.9 | 8.9 | 12 | 14.2 | 15 | 20.9 | 20.7 | 20.4 | 22 | 18.5 | 18.9 | 18.6 | 19.6 | 22.9 | 22.4 | 23 | 17.9 | 12.9 | 12.9 | 11.5 | 10.3 | 8.1 | 7.6 | 7 | 7.3 | 8.5 | 9.8 | 12.6 | 12.2 | 0.335 | 0.346 | 0.372 | 0.371 | 0.371 | 0.387 | 0.389 | 0.373 | 0.359 | 0.365 | 0.318 | 0.318 | 2.507 | 2.485 | 2.386 | 2.398 | 2.43 | 2.386 | 2.449 | 2.479 | 2.509 | 2.466 | 2.595 | 2.596 | 278 | 287 | 286 | 291 | 290 | 284 | 283 | 286 | 287 | 276 | 284 | 279 | 27 | 30 | 36 | 37 | 37 | 38 | 36 | 34 | 32 | 31 | 24 | 23 | 1010 | 1291 | 1725 | 2102 | 2256 | 2356 | 2351 | 2240 | 1893 | 1439 | 1118 | 914 | 71 | 125 | 93 | 107 | 154 | 146 | 127 | 71 | 79 | 106 | 68 | 68 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.12 | N/A | -2.93 | 1.3 | N/A | N/A | N/A | -198 | 389 | 187 | 52
4 | USA | CA | FULLERTON | 722976 | 03166 | 33.872 | -117.979 | 96 | 14.64 | -8 | NAP | 98-19 | 3B | 12 | 40 | 42.8 | 8.8 | 8.7 | 68.1 | 15.2 | 11.9 | 69.9 | 18.9 | 66.7 | 16.3 | 64.7 | 1.2 | 90 | 0.327 | 8 | 19 | 95.3 | 66.8 | 91.7 | 66.8 | 88.7 | 66.2 | 72.4 | 87.4 | 71.1 | 85.3 | 69.9 | 83.1 | 6.5 | 210 | 67.5 | 101.4 | 78.5 | 66.1 | 96.4 | 77.3 | 64.6 | 91.7 | 75.5 | 36.1 | 87.6 | 34.9 | 85.1 | 33.9 | 83.5 | 81.5 | 12.8 | 10.9 | 10 | 35.2 | 103.8 | 2.4 | 4.3 | 33.5 | 106.9 | 32.1 | 109.4 | 30.8 | 111.9 | 29.1 | 115 | 31.5 | 74.2 | 2.1 | 1.8 | 29.9 | 75.5 | 28.7 | 76.6 | 27.5 | 77.6 | 25.9 | 78.9 | 66.1 | 58 | 58.3 | 61.2 | 63.6 | 66.8 | 70.5 | 75.1 | 76 | 74.4 | 69.2 | 62.8 | 56.9 | 8.19 | 5.15 | 5.22 | 5.16 | 5.23 | 4.41 | 3.85 | 3.92 | 4.1 | 5.25 | 5.14 | 5.15 | 4.46 | 9 | 3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 1042 | 225 | 197 | 139 | 85 | 27 | 2 | 0 | 0 | 0 | 14 | 100 | 253 | 5885 | 250 | 233 | 348 | 409 | 520 | 614 | 777 | 805 | 733 | 596 | 383 | 217 | 1443 | 7 | 8 | 22 | 44 | 82 | 166 | 312 | 340 | 283 | 145 | 33 | 1 | 11384 | 212 | 193 | 320 | 500 | 566 | 903 | 2131 | 2540 | 2191 | 1272 | 465 | 91 | 4324 | 45 | 58 | 103 | 195 | 216 | 257 | 750 | 1012 | 959 | 553 | 166 | 10 | 3.7 | 3.1 | 3.7 | 3.9 | 4.4 | 4.5 | 4.4 | 4.1 | 3.7 | 3.4 | 3.2 | 2.8 | 2.9 | 13.3 | 3 | 3.2 | 1.8 | 1 | 0.3 | 0.1 | 0 | 0 | 0.2 | 0.5 | 1.1 | 2 | 26.4 | 12.2 | 13.6 | 6.2 | 2.5 | 2.4 | 1.1 | 0.4 | 0.1 | 1.7 | 5.2 | 3.1 | 9.8 | 4.3 | 0.1 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2 | 3.2 | 3 | 1.7 | 0.6 | 0.5 | 0.3 | 0.1 | 0 | 0.4 | 1 | 0.8 | 2.1 | 85 | 87.2 | 90 | 94.1 | 95.3 | 93.4 | 94.9 | 97 | 100.9 | 98.1 | 91.6 | 81.4 | 55.7 | 56.9 | 59.8 | 59.6 | 60.3 | 70.1 | 70.4 | 70.2 | 69.8 | 62.9 | 59.3 | 55.3 | 80.4 | 80.2 | 81.8 | 85.3 | 85 | 86.2 | 90.4 | 92.9 | 94.5 | 91.3 | 84.8 | 76.4 | 55.3 | 56 | 57.7 | 58.8 | 61.8 | 67.7 | 69.2 | 69.8 | 69.5 | 62.4 | 57.5 | 54.1 | 75.1 | 74.2 | 76.6 | 79.3 | 79.9 | 82 | 87.3 | 89.6 | 90 | 86.2 | 79.2 | 72.1 | 53.7 | 55.1 | 56.7 | 58.4 | 63.1 | 66.5 | 69.1 | 69.3 | 68.1 | 61.3 | 56.2 | 53 | 70.3 | 69.6 | 72 | 74.3 | 75.1 | 79.1 | 84 | 85.6 | 85.3 | 81 | 73.9 | 67.4 | 53.4 | 54.2 | 57 | 58.4 | 61.8 | 65.5 | 68.5 | 68.6 | 67.2 | 62.3 | 56.2 | 52.7 | 61.4 | 62 | 64.3 | 64.7 | 68.2 | 70.9 | 73.8 | 74.2 | 74.2 | 71.2 | 63.9 | 61.7 | 71.8 | 73.9 | 78.2 | 80.4 | 82.6 | 87.6 | 88.2 | 90.5 | 91.7 | 83.4 | 75.4 | 68.6 | 59.3 | 59.7 | 61.7 | 62.4 | 65.7 | 68.9 | 71.7 | 72.2 | 72 | 68.2 | 62.2 | 59.6 | 67.2 | 69.9 | 73.8 | 77.1 | 78.6 | 83.3 | 85 | 87.5 | 87.9 | 81.1 | 73.5 | 66.2 | 57.7 | 58.1 | 60 | 60.9 | 64 | 67.4 | 70.5 | 70.9 | 70.4 | 66.2 | 60.6 | 57.9 | 66.1 | 67.7 | 70.9 | 74.3 | 76.1 | 80.4 | 83.2 | 85.2 | 84.6 | 77.9 | 71.2 | 64.5 | 56.3 | 56.6 | 58.6 | 59.3 | 62.4 | 66 | 69.2 | 69.5 | 69 | 64.5 | 59.4 | 56.3 | 64.8 | 65.6 | 68.1 | 70.6 | 72.9 | 77.5 | 81.3 | 82.5 | 81.8 | 74.8 | 68.9 | 63.1 | 22 | 20.1 | 19.1 | 18.7 | 16.3 | 16 | 17.7 | 19 | 19.8 | 20.7 | 22.1 | 21.4 | 32 | 30.2 | 29.3 | 30.1 | 26 | 22.4 | 22.5 | 25 | 27.4 | 32.4 | 32 | 30.5 | 13.4 | 12.8 | 12 | 11.6 | 9.9 | 8.2 | 7.7 | 8.6 | 9.2 | 11.6 | 12.5 | 14 | 21 | 22.2 | 20.9 | 22.3 | 19.5 | 20 | 19.8 | 21.5 | 22.8 | 22 | 22.4 | 19.6 | 10.9 | 10.9 | 10 | 9.9 | 8.4 | 7.8 | 7.4 | 8.2 | 8.7 | 9.6 | 10.6 | 11.1 | 0.332 | 0.342 | 0.368 | 0.371 | 0.37 | 0.386 | 0.389 | 0.373 | 0.359 | 0.363 | 0.317 | 0.316 | 2.51 | 2.492 | 2.393 | 2.391 | 2.428 | 2.384 | 2.444 | 2.475 | 2.505 | 2.465 | 2.593 | 2.594 | 279 | 288 | 288 | 291 | 290 | 284 | 283 | 286 | 287 | 276 | 284 | 279 | 27 | 30 | 36 | 38 | 37 | 38 | 36 | 34 | 32 | 31 | 24 | 23 | 1011 | 1293 | 1731 | 2110 | 2278 | 2399 | 2374 | 2257 | 1910 | 1452 | 1123 | 916 | 71 | 127 | 93 | 105 | 147 | 141 | 123 | 68 | 73 | 102 | 65 | 68 | 2.09 | N/A | -4.82 | 2.38 | N/A | N/A | N/A | -346 | 880 | 441 | 1.12 | N/A | -2.97 | 1.26 | N/A | N/A | N/A | -202 | 396 | 193 | 54
4 | USA | CA | COSTA MESA WAYNE | 722977 | 93184 | 33.68 | -117.866 | 54 | 14.67 | -8 | NAP | 99-19 | 3B | 12 | 42.8 | 44.9 | 6.9 | 7.8 | 67.1 | 14.7 | 11.6 | 67.4 | 21.3 | 62.6 | 18.5 | 63.8 | 1.3 | 30 | 0.345 | 8 | 13.2 | 89.8 | 65.3 | 86.3 | 65.3 | 83.2 | 64.9 | 71.3 | 82.3 | 70.1 | 80.3 | 69.1 | 78.6 | 7.9 | 230 | 67.7 | 102.1 | 76.4 | 66.3 | 97 | 75.3 | 65.3 | 93.7 | 74.3 | 35.1 | 82.2 | 34 | 80.3 | 33.2 | 78.8 | 77.7 | 16.1 | 13.1 | 12 | 38 | 99 | 2.5 | 5 | 36.3 | 102.7 | 34.8 | 105.6 | 33.4 | 108.4 | 31.6 | 112.1 | 33.1 | 73.5 | 2.2 | 1.5 | 31.5 | 74.6 | 30.2 | 75.5 | 29 | 76.3 | 27.4 | 77.4 | 64.8 | 58 | 57.9 | 60 | 62 | 64.9 | 68 | 72.2 | 73.1 | 72.4 | 68.5 | 62.9 | 57.4 | 7.12 | 5.12 | 4.83 | 4.31 | 4.35 | 3.78 | 3 | 3.38 | 3.37 | 4.61 | 4.8 | 4.93 | 4.34 | 5 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1106 | 227 | 205 | 166 | 110 | 42 | 4 | 0 | 0 | 0 | 16 | 97 | 239 | 5407 | 249 | 222 | 310 | 361 | 462 | 539 | 688 | 715 | 672 | 572 | 386 | 231 | 1033 | 9 | 6 | 11 | 21 | 39 | 93 | 223 | 250 | 222 | 123 | 33 | 3 | 5385 | 134 | 93 | 143 | 237 | 249 | 228 | 841 | 1114 | 1211 | 781 | 308 | 46 | 1525 | 26 | 22 | 37 | 79 | 100 | 45 | 164 | 256 | 409 | 287 | 94 | 6 | 4.8 | 3.8 | 4.4 | 4.9 | 5.6 | 6.1 | 6.1 | 5.9 | 5.3 | 4.7 | 4.1 | 3.5 | 3.6 | 10.6 | 2.4 | 2.7 | 2.2 | 0.8 | 0.1 | 0 | 0 | 0.1 | 0.4 | 0.2 | 1.2 | 1.5 | 26.1 | 7.9 | 12.4 | 10 | 4.1 | 0.5 | 0.5 | 0.2 | 1.7 | 1.9 | 1 | 5.3 | 4.2 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9 | 2.3 | 3 | 2.3 | 1.1 | 0.1 | 0.1 | 0 | 0.4 | 0.6 | 0.2 | 1.2 | 1.3 | 83.7 | 83.6 | 84.6 | 89 | 90.5 | 85.8 | 88.1 | 89.9 | 95.1 | 94.2 | 88.4 | 79.2 | 55.9 | 56.8 | 58.1 | 60.2 | 59.8 | 67.9 | 69.4 | 68.2 | 68.9 | 62.9 | 60 | 53.8 | 77.6 | 76.2 | 77.7 | 80.8 | 80.6 | 79.2 | 83.9 | 86.1 | 89 | 87.5 | 82.1 | 73.4 | 53.7 | 54.9 | 56 | 57.8 | 61.2 | 66.3 | 68.4 | 68.7 | 69 | 61.6 | 57.5 | 54.8 | 73.2 | 71.4 | 72.3 | 74.4 | 74.2 | 75.9 | 81.2 | 82.5 | 84.4 | 82.1 | 76.8 | 69.9 | 53.6 | 54.7 | 55.8 | 57.4 | 62.3 | 65.1 | 68.5 | 68.8 | 68.1 | 62.2 | 56.9 | 53.7 | 68.5 | 66.7 | 68 | 69.9 | 70.9 | 73.5 | 78.7 | 79.9 | 80.7 | 77.5 | 72.2 | 66.1 | 53.2 | 54.4 | 56.3 | 57.8 | 61 | 64 | 67.8 | 68.3 | 67.6 | 62.5 | 57.1 | 53.7 | 61.3 | 61.8 | 62.8 | 63.5 | 66.3 | 69.1 | 72.6 | 72.5 | 73.1 | 70.6 | 64.2 | 62.3 | 69.9 | 70.2 | 74.9 | 76.9 | 77.2 | 80.3 | 83.4 | 83.9 | 86.7 | 80.7 | 74.9 | 69.3 | 59.4 | 59.6 | 60.6 | 61.4 | 64.4 | 67.3 | 70.6 | 70.9 | 71.1 | 68.1 | 62.5 | 59.8 | 65.9 | 67 | 69.3 | 72 | 74.1 | 78 | 79.6 | 81.5 | 83.8 | 78.3 | 71.6 | 65.6 | 58.1 | 58.2 | 59.2 | 59.9 | 62.8 | 66 | 69.4 | 69.7 | 69.9 | 66.3 | 61.3 | 58.4 | 64.8 | 65.2 | 67.1 | 69.5 | 71.4 | 75 | 78.4 | 79.6 | 80.4 | 75.9 | 69.7 | 64 | 56.7 | 56.9 | 57.9 | 58.8 | 61.7 | 64.8 | 68.4 | 68.7 | 68.7 | 64.8 | 60 | 57.1 | 63.6 | 63.6 | 64.9 | 67.3 | 69.4 | 72.3 | 76.9 | 78 | 78.3 | 73.5 | 68 | 62.8 | 18.2 | 16.3 | 14.9 | 14.3 | 12.2 | 11.5 | 12.3 | 13.2 | 14.5 | 15.7 | 17.9 | 17.6 | 27 | 25.3 | 24.5 | 24.3 | 19.6 | 15.4 | 15.8 | 17.3 | 20.8 | 26 | 26.8 | 24.5 | 11.8 | 11.3 | 10.6 | 9.7 | 7.9 | 6.2 | 5.7 | 6.2 | 7.5 | 10.2 | 11.5 | 12.5 | 18.4 | 17.5 | 16.3 | 16.9 | 15.4 | 15 | 14.2 | 15.3 | 17.8 | 18.5 | 18.5 | 16 | 10 | 9.3 | 8.4 | 7.9 | 6.7 | 6.3 | 5.4 | 6 | 7 | 8.5 | 9.5 | 9.7 | 0.323 | 0.333 | 0.357 | 0.363 | 0.362 | 0.377 | 0.383 | 0.368 | 0.353 | 0.354 | 0.312 | 0.311 | 2.537 | 2.522 | 2.43 | 2.42 | 2.454 | 2.416 | 2.466 | 2.493 | 2.526 | 2.499 | 2.609 | 2.611 | 283 | 292 | 292 | 293 | 293 | 287 | 284 | 288 | 289 | 280 | 286 | 283 | 26 | 30 | 35 | 37 | 36 | 37 | 35 | 34 | 31 | 30 | 24 | 23 | 1016 | 1295 | 1729 | 2100 | 2246 | 2357 | 2355 | 2244 | 1896 | 1440 | 1123 | 919 | 69 | 126 | 91 | 107 | 154 | 147 | 124 | 64 | 77 | 105 | 68 | 69 | 1.42 | N/A | N/A | 3.38 | N/A | N/A | N/A | -284 | 558 | 306 | 1.13 | N/A | -3.06 | 1.3 | N/A | N/A | N/A | -202 | 401 | 202 | 50
4 | USA | CA | NEEDLES | 723805 | 23179 | 34.768 | -114.619 | 890 | 14.23 | -8 | NAP | 01-19 | 1B | 12 | 37.4 | 40.3 | -1.8 | 5.2 | 65.3 | 2.3 | 6.4 | 66.4 | 30.2 | 58.1 | 27 | 58.4 | 5.4 | 240 | 0.505 | 7 | 22.5 | 114.7 | 69.6 | 112.3 | 69.3 | 110.2 | 69 | 76.9 | 99.3 | 75.3 | 98.4 | 74.3 | 98.5 | 9.7 | 220 | 71 | 118 | 86.6 | 68.4 | 107.8 | 88.8 | 65.8 | 98.3 | 91.5 | 40.7 | 98.9 | 39.4 | 97.9 | 38.3 | 98.1 | 82.6 | 25.9 | 22.5 | 19.2 | 31.9 | 119 | 3.2 | 2.1 | 29.6 | 120.5 | 27.7 | 121.8 | 25.9 | 122.9 | 23.6 | 124.5 | 25 | 78.1 | 2.8 | 2.1 | 23 | 79.7 | 21.4 | 80.9 | 19.8 | 82.1 | 17.8 | 83.6 | 75.8 | 55.7 | 59 | 66.6 | 73.5 | 82.4 | 93.2 | 98.3 | 96.4 | 89.4 | 76.2 | 64 | 54 | 16.6 | 5.79 | 6.32 | 6.96 | 6.89 | 7.25 | 5.6 | 4.49 | 4.47 | 5.79 | 6.51 | 6.8 | 5.67 | 52 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 26 | 998 | 291 | 184 | 67 | 12 | 0 | 0 | 0 | 0 | 0 | 5 | 98 | 341 | 9471 | 195 | 256 | 514 | 704 | 1006 | 1296 | 1496 | 1438 | 1183 | 812 | 421 | 150 | 4943 | 2 | 15 | 116 | 266 | 541 | 846 | 1031 | 973 | 733 | 352 | 67 | 1 | 79763 | 21 | 188 | 1354 | 3344 | 8160 | 14925 | 18695 | 17090 | 11460 | 3942 | 575 | 9 | 54574 | 1 | 27 | 498 | 1612 | 5005 | 10793 | 14247 | 12687 | 7645 | 1912 | 147 | 0 | 8.1 | 8.1 | 7.9 | 8.3 | 9.2 | 9 | 8.7 | 8.1 | 7.6 | 7.2 | 7.8 | 7.6 | 7.6 | 4.6 | 0.6 | 0.6 | 0.5 | 0.2 | 0.1 | 0 | 0.3 | 0.6 | 0.5 | 0.3 | 0.4 | 0.4 | 9.6 | 3.6 | 3.6 | 3.2 | 2.8 | 0.7 | 0.5 | 2.2 | 3.4 | 4.7 | 1.7 | 1.7 | 2.6 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0.9 | 0.8 | 0.7 | 0.6 | 0.2 | 0.1 | 0.5 | 0.9 | 0.9 | 0.4 | 0.4 | 0.6 | 76.7 | 83.3 | 94.2 | 101 | 109.3 | 118.2 | 118.9 | 115.4 | 110.8 | 100.4 | 88.5 | 75.3 | 52.5 | 55 | 59.8 | 61 | 66.9 | 67 | 71.1 | 70.3 | 68.8 | 65.1 | 59 | 55.1 | 72.9 | 79.6 | 89.2 | 96.7 | 105.8 | 113.4 | 115.4 | 113.1 | 107.9 | 96.6 | 84.2 | 71.1 | 51.1 | 53.8 | 57.6 | 59.9 | 64 | 65.9 | 70.7 | 70.8 | 68.1 | 63.2 | 57 | 51.8 | 69.8 | 75.7 | 85.5 | 92.8 | 102.3 | 110.9 | 113 | 110.9 | 105.8 | 93.4 | 80.8 | 67.6 | 50 | 52.2 | 56.2 | 58.4 | 62.7 | 65.9 | 70.6 | 70.3 | 68 | 61.9 | 56.1 | 50.2 | 66.7 | 71.9 | 82 | 89 | 99 | 108.3 | 110.4 | 108.6 | 103.3 | 90.3 | 76.8 | 64.4 | 48.9 | 51 | 54.7 | 57.2 | 61.7 | 65.5 | 70.1 | 70.2 | 67.5 | 60.9 | 54.3 | 48.5 | 57.8 | 59.3 | 61.8 | 65 | 70.9 | 73.2 | 78.6 | 79.3 | 76 | 69.8 | 62.2 | 57.5 | 66.3 | 72.6 | 87.6 | 91.7 | 104 | 105.9 | 107 | 101.8 | 95.8 | 86.5 | 79.8 | 67.6 | 55.4 | 56.6 | 59.2 | 61.5 | 66.5 | 70.8 | 76.5 | 77.4 | 73.9 | 67.2 | 59.4 | 55.3 | 64.5 | 69.7 | 83.3 | 89.8 | 99.6 | 105.6 | 100.1 | 98.6 | 95.1 | 87.1 | 79.5 | 65.8 | 53.2 | 54.5 | 57.3 | 59.9 | 64.2 | 68.8 | 75.2 | 75.8 | 72.5 | 65.2 | 57.3 | 53 | 64.6 | 69.4 | 81.9 | 87.6 | 97.9 | 104.6 | 98.9 | 98.3 | 94.8 | 87.7 | 75.9 | 63.7 | 51.1 | 52.8 | 55.8 | 58.4 | 62.4 | 67.2 | 74.2 | 74.6 | 71 | 63.2 | 55.6 | 50.7 | 63 | 68.7 | 78.8 | 85.7 | 96 | 103.7 | 99.4 | 98 | 94.7 | 85.4 | 74.2 | 61.5 | 19.7 | 21.6 | 24.5 | 24.7 | 25.2 | 26 | 22.5 | 22.8 | 24.3 | 23.7 | 21.7 | 18.6 | 23 | 27.1 | 29.6 | 29.4 | 29.5 | 28.7 | 25.3 | 25.1 | 26.6 | 26.9 | 25.4 | 21.8 | 11.4 | 12.7 | 12.6 | 12.4 | 11.7 | 10.1 | 8.9 | 8.8 | 10.3 | 12 | 11.9 | 10.8 | 19.3 | 22.5 | 26.9 | 26.4 | 27.6 | 25.8 | 20.8 | 21.3 | 22 | 22.7 | 22.6 | 18.4 | 10.1 | 10.9 | 11.7 | 11.5 | 12.7 | 11.5 | 7.5 | 7.5 | 9.2 | 10.8 | 11 | 9.7 | 0.273 | 0.276 | 0.29 | 0.324 | 0.335 | 0.334 | 0.384 | 0.379 | 0.338 | 0.301 | 0.277 | 0.272 | 2.598 | 2.612 | 2.546 | 2.422 | 2.419 | 2.424 | 2.394 | 2.401 | 2.484 | 2.564 | 2.606 | 2.615 | 302 | 312 | 314 | 305 | 301 | 299 | 284 | 284 | 292 | 298 | 298 | 296 | 24 | 26 | 30 | 36 | 37 | 37 | 38 | 37 | 32 | 27 | 23 | 22 | 1039 | 1353 | 1821 | 2259 | 2552 | 2709 | 2407 | 2235 | 1978 | 1531 | 1153 | 926 | 68 | 101 | 80 | 80 | 82 | 89 | 106 | 94 | 71 | 73 | 48 | 63 | N/A | N/A | -4.75 | N/A | -1.8 | N/A | N/A | N/A | N/A | N/A | 0.7 | N/A | -3.06 | N/A | -0.74 | N/A | N/A | N/A | 257 | 144 | 12
4 | USA | CA | EDWARDS AFB | 723810 | 23114 | 34.9 | -117.867 | 2311 | 13.51 | -8 | NAP | 94-19 | 3B | 12 | 21.7 | 25.3 | -6.1 | 4.3 | 39.7 | -1.3 | 5.6 | 42.8 | 30.6 | 51 | 27.4 | 51.6 | 3.1 | 0 | 0.592 | 7 | 32 | 105 | 64.6 | 102.3 | 63.7 | 100 | 63 | 68.9 | 92.8 | 67.5 | 93.5 | 66 | 93.2 | 12.2 | 240 | 61.6 | 89.2 | 76.5 | 57.6 | 77.2 | 78.3 | 54.7 | 69.2 | 77.4 | 34.3 | 92.1 | 33 | 93.7 | 31.8 | 92.8 | 75.2 | 28.2 | 25.7 | 23.5 | 14.8 | 109.6 | 4.4 | 2 | 11.6 | 111.1 | 9.1 | 112.2 | 6.6 | 113.4 | 3.4 | 114.8 | 12.5 | 71.9 | 4.3 | 1.8 | 9.4 | 73.2 | 6.9 | 74.3 | 4.4 | 75.3 | 1.3 | 76.7 | 63.1 | 45.6 | 48.6 | 54.9 | 60.3 | 67.6 | 77.6 | 83.9 | 83 | 75.3 | 62.9 | 52.1 | 43.8 | 15.21 | 5.73 | 6.13 | 6.31 | 7.46 | 7.47 | 7.09 | 4.49 | 4.31 | 6.24 | 6.44 | 6.61 | 6.27 | 551 | 158 | 91 | 27 | 9 | 0 | 0 | 0 | 0 | 0 | 2 | 54 | 210 | 2787 | 602 | 460 | 317 | 177 | 61 | 6 | 0 | 0 | 7 | 114 | 387 | 656 | 5318 | 21 | 52 | 178 | 317 | 547 | 829 | 1051 | 1022 | 760 | 404 | 118 | 19 | 2076 | 0 | 0 | 3 | 35 | 142 | 385 | 586 | 557 | 317 | 50 | 1 | 0 | 30067 | 1 | 17 | 211 | 741 | 2086 | 5453 | 8260 | 7755 | 4298 | 1130 | 114 | 1 | 17657 | 0 | 2 | 36 | 252 | 983 | 3310 | 5267 | 4940 | 2429 | 428 | 10 | 0 | 10 | 7 | 9.1 | 10.4 | 12.7 | 13.5 | 13.1 | 11.7 | 10.7 | 9 | 8.2 | 7.1 | 7.1 | 5.7 | 1.1 | 1.4 | 0.6 | 0.3 | 0.1 | 0 | 0.2 | 0.1 | 0.2 | 0.3 | 0.3 | 0.8 | 13 | 5.9 | 6 | 2.3 | 1 | 0.9 | 0.5 | 0.9 | 0.4 | 1.3 | 2 | 1.1 | 3.6 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 1.5 | 1.5 | 0.6 | 0.3 | 0.2 | 0.1 | 0.2 | 0.2 | 0.4 | 0.5 | 0.3 | 0.9 | 70.3 | 76.4 | 84.2 | 90.9 | 98.8 | 107.1 | 108.9 | 107.8 | 101.5 | 93.2 | 81.4 | 70.8 | 50.7 | 51.6 | 54.5 | 57.7 | 61.6 | 64.8 | 65.6 | 65.8 | 64.2 | 58.9 | 54 | 51.3 | 66.1 | 72.3 | 79.6 | 86.5 | 93.8 | 102.7 | 105.4 | 104.2 | 98.8 | 89.1 | 77.4 | 64.9 | 47.9 | 50.3 | 53 | 55.7 | 59.2 | 62.4 | 64.9 | 64.6 | 63.3 | 58 | 52 | 48.1 | 63 | 68 | 75.5 | 82.4 | 90.1 | 99.6 | 102.5 | 101.8 | 96.3 | 85.1 | 73.1 | 61.1 | 46.9 | 49.1 | 51.7 | 54.3 | 58.3 | 61.5 | 64.1 | 63.7 | 62.3 | 56.1 | 51 | 46.6 | 59.1 | 63.3 | 71.6 | 78.1 | 85.9 | 96.2 | 99.9 | 99.4 | 93.2 | 81.1 | 68.1 | 57.1 | 46 | 47.3 | 50.8 | 53.1 | 57.2 | 60.7 | 63.5 | 62.9 | 61 | 54.9 | 49 | 45.1 | 55.7 | 55.4 | 57.1 | 60.2 | 63.8 | 67.8 | 71.4 | 70.4 | 69.3 | 64 | 57.3 | 55.5 | 62.5 | 66.5 | 73.4 | 84.1 | 93.5 | 100.2 | 91 | 93.6 | 90.7 | 80.7 | 68.4 | 61.6 | 52.6 | 52.9 | 55.1 | 57.9 | 61.2 | 65.2 | 69.3 | 68.6 | 67.5 | 60.9 | 54.5 | 52.5 | 59.6 | 64.4 | 72.8 | 80.3 | 88.4 | 95.6 | 92 | 94.1 | 87.7 | 79.4 | 71.2 | 60.1 | 50.3 | 50.9 | 53.5 | 56.1 | 59.6 | 63.5 | 67.7 | 66.9 | 65.7 | 58.7 | 52.6 | 50.1 | 57.1 | 63.4 | 71.3 | 77.6 | 85.9 | 93.8 | 94.2 | 95.1 | 87.2 | 79.2 | 68.3 | 57.1 | 48.2 | 49.2 | 51.9 | 54.4 | 58.1 | 62.1 | 66.1 | 65.2 | 63.8 | 56.7 | 50.8 | 47.6 | 55.6 | 60.7 | 68 | 74.7 | 82.6 | 91.3 | 94 | 94.7 | 86.2 | 75.9 | 65.2 | 54.7 | 26.9 | 26.3 | 28.6 | 28.6 | 29 | 32.2 | 32 | 33.2 | 32.7 | 32.6 | 31.1 | 26.6 | 33.8 | 35.3 | 36.8 | 36.3 | 35.1 | 36 | 34.7 | 35.3 | 35.6 | 39 | 37.9 | 32.4 | 19.2 | 17.6 | 16.2 | 14.7 | 12.6 | 11.5 | 11 | 12.1 | 13.4 | 17.4 | 20.2 | 18.9 | 23.3 | 27.7 | 31.2 | 31.9 | 32.9 | 33.8 | 29 | 30.6 | 29.2 | 31.4 | 31.7 | 23.5 | 14.4 | 14.6 | 14.4 | 13.1 | 12 | 11.4 | 11 | 11.8 | 11 | 14 | 17.1 | 14.8 | 0.273 | 0.283 | 0.298 | 0.32 | 0.335 | 0.33 | 0.353 | 0.34 | 0.325 | 0.302 | 0.277 | 0.276 | 2.548 | 2.538 | 2.485 | 2.424 | 2.405 | 2.432 | 2.414 | 2.429 | 2.464 | 2.515 | 2.56 | 2.556 | 301 | 309 | 311 | 306 | 301 | 300 | 293 | 296 | 297 | 297 | 296 | 293 | 25 | 28 | 32 | 36 | 37 | 36 | 37 | 36 | 33 | 29 | 24 | 23 | 986 | 1284 | 1750 | 2166 | 2445 | 2661 | 2502 | 2348 | 2003 | 1512 | 1125 | 898 | 74 | 128 | 88 | 89 | 106 | 105 | 107 | 65 | 49 | 80 | 46 | 65 | N/A | N/A | -5.47 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | N/A | -3.35 | 1.15 | N/A | N/A | N/A | -202 | 392 | 189 | 44
4 | USA | CA | BARSTOW-DAGGETT | 723815 | 23161 | 34.854 | -116.786 | 1917 | 13.71 | -8 | NAP | 94-19 | 2B | 12 | 29.6 | 32.5 | -1.9 | 5.3 | 49.9 | 1.3 | 6.3 | 48.8 | 34.7 | 54.7 | 32.1 | 55 | 5.5 | 270 | 0.588 | 7 | 29.2 | 108.9 | 67.9 | 106.6 | 66.9 | 104.4 | 65.9 | 72.5 | 98.5 | 70.9 | 97.2 | 69.4 | 96 | 10.8 | 280 | 65 | 99.5 | 81.7 | 62.2 | 89.9 | 84.7 | 58.5 | 78.5 | 88.5 | 37.2 | 98.8 | 35.9 | 96.5 | 34.5 | 96.3 | 91.6 | 32.1 | 27.7 | 24.7 | 23.3 | 113.4 | 3.7 | 2 | 20.6 | 114.8 | 18.5 | 116 | 16.4 | 117.1 | 13.7 | 118.5 | 18.9 | 76.3 | 3.3 | 5 | 16.5 | 79.9 | 14.6 | 82.8 | 12.7 | 85.7 | 10.3 | 89.3 | 68.5 | 49.7 | 52.9 | 59.9 | 65.6 | 74.4 | 84.2 | 90 | 88.8 | 81.3 | 68.8 | 56.8 | 48.2 | 15.95 | 5.84 | 6.47 | 6.98 | 7.66 | 7.86 | 6.75 | 4.25 | 4.06 | 6.23 | 7.07 | 7.24 | 5.74 | 250 | 77 | 40 | 6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 104 | 1925 | 476 | 339 | 188 | 85 | 16 | 1 | 0 | 0 | 1 | 42 | 256 | 521 | 6992 | 66 | 122 | 313 | 469 | 756 | 1025 | 1240 | 1203 | 939 | 584 | 227 | 48 | 3189 | 0 | 1 | 29 | 104 | 306 | 576 | 775 | 738 | 489 | 161 | 10 | 0 | 46479 | 4 | 51 | 484 | 1375 | 4016 | 8495 | 12201 | 11251 | 6508 | 1889 | 201 | 4 | 28829 | 0 | 4 | 117 | 554 | 2175 | 5485 | 8282 | 7492 | 3879 | 804 | 37 | 0 | 10.8 | 7.8 | 9.6 | 11.6 | 14.2 | 14.5 | 14 | 11.5 | 10.8 | 10.2 | 9.4 | 8.3 | 7.7 | 3.9 | 0.5 | 0.6 | 0.5 | 0.2 | 0.1 | 0.1 | 0.4 | 0.3 | 0.5 | 0.2 | 0.3 | 0.4 | 7.5 | 2.5 | 2.5 | 1.9 | 1.8 | 0.5 | 1.3 | 2 | 1.3 | 3.3 | 1 | 1.7 | 2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0.6 | 0.7 | 0.5 | 0.4 | 0.1 | 0.2 | 0.4 | 0.4 | 0.8 | 0.2 | 0.4 | 0.5 | 72.7 | 79.2 | 88.3 | 95.1 | 103.7 | 110.9 | 112.6 | 110.2 | 104.8 | 96.3 | 83.9 | 72.7 | 52.3 | 52.9 | 57 | 60.3 | 65.4 | 65.3 | 69.4 | 69.9 | 66.2 | 62.2 | 55.2 | 53 | 69.1 | 75 | 83.1 | 90.6 | 99.3 | 106.9 | 109.7 | 107.9 | 102 | 91.8 | 79.5 | 67.5 | 49.7 | 51.7 | 55 | 58.1 | 62.9 | 65.4 | 68.5 | 67.9 | 65.5 | 60.4 | 53.7 | 49.9 | 65.8 | 70.9 | 79.4 | 86.5 | 95.7 | 104.3 | 107.4 | 105.7 | 99.6 | 88.4 | 75.3 | 63.9 | 47.9 | 50.1 | 53.5 | 56.4 | 60.6 | 64.4 | 67.7 | 66.5 | 64.9 | 58.7 | 52.4 | 47.9 | 62.4 | 66.6 | 75.6 | 82.2 | 91.7 | 101.3 | 104.7 | 103.2 | 97 | 84.4 | 71.2 | 60.3 | 46.8 | 48.4 | 52.3 | 54.8 | 59.6 | 63.4 | 66.8 | 65.6 | 63.4 | 56.9 | 50.7 | 46 | 55.5 | 56.5 | 58.9 | 62.2 | 69.2 | 72.3 | 75.2 | 74.3 | 71.5 | 65.9 | 58.2 | 55.7 | 67.7 | 71.6 | 80.1 | 90.4 | 100.8 | 104.8 | 102.3 | 100 | 92.7 | 85 | 75.7 | 67.7 | 52.7 | 53.8 | 56.6 | 59.5 | 64.4 | 68.6 | 72.9 | 72.1 | 69.8 | 62.8 | 55.7 | 52.9 | 63 | 68.8 | 77.9 | 86.6 | 94.5 | 101.9 | 98.7 | 98.2 | 92 | 85.3 | 74.7 | 63.3 | 50.6 | 51.8 | 54.8 | 57.4 | 61.9 | 66.2 | 71.2 | 70.5 | 68.3 | 60.5 | 53.6 | 50.4 | 60.6 | 66.4 | 75.9 | 82.6 | 91.5 | 99.7 | 97.6 | 97 | 91 | 83.9 | 72.2 | 60.4 | 48.5 | 50 | 53.2 | 55.6 | 60.1 | 64.2 | 69.7 | 69 | 66.3 | 58.6 | 51.9 | 47.9 | 59.2 | 63.9 | 73 | 79.4 | 88.7 | 97.3 | 96.6 | 95.8 | 90.1 | 80.8 | 68.9 | 57.2 | 23.5 | 23.9 | 26 | 26.7 | 27.9 | 30.1 | 29.2 | 29.2 | 28.4 | 27.2 | 25.6 | 22.9 | 27.7 | 29.6 | 30.6 | 31.5 | 31.7 | 32.5 | 31.5 | 30.5 | 29.9 | 30.6 | 29.6 | 26.8 | 14.2 | 13.8 | 12.5 | 12.2 | 11.4 | 11 | 11.2 | 11 | 10.9 | 12.8 | 14.1 | 14.5 | 22.1 | 25.2 | 28.3 | 29.3 | 30.5 | 31.5 | 27.2 | 27 | 26.6 | 27.7 | 26.9 | 22.6 | 12.1 | 12.2 | 12 | 11.7 | 12.3 | 12.7 | 12.2 | 12 | 10.7 | 11.8 | 13 | 12.6 | 0.273 | 0.282 | 0.294 | 0.326 | 0.336 | 0.337 | 0.371 | 0.351 | 0.33 | 0.309 | 0.275 | 0.274 | 2.546 | 2.534 | 2.492 | 2.391 | 2.391 | 2.405 | 2.376 | 2.417 | 2.456 | 2.489 | 2.576 | 2.565 | 301 | 309 | 312 | 304 | 300 | 298 | 287 | 292 | 295 | 294 | 298 | 294 | 25 | 28 | 32 | 37 | 38 | 37 | 38 | 36 | 33 | 29 | 24 | 23 | 1028 | 1343 | 1814 | 2244 | 2523 | 2700 | 2462 | 2306 | 2008 | 1544 | 1152 | 929 | 74 | 114 | 73 | 69 | 91 | 96 | 111 | 84 | 62 | 71 | 46 | 58 | N/A | N/A | -3.01 | N/A | -0.97 | N/A | N/A | N/A | N/A | N/A | 1.12 | N/A | -3.29 | 1.03 | N/A | N/A | N/A | -178 | 391 | 211 | 40
4 | USA | CA | LANCASTER FOX | 723816 | 03159 | 34.741 | -118.212 | 2338 | 13.5 | -8 | NAP | 94-19 | 3B | 12 | 21.3 | 24.9 | -2.7 | 5.2 | 39.1 | 1.4 | 6.4 | 42.8 | 32.9 | 50.9 | 28.9 | 51.6 | 3 | 270 | 0.631 | 7 | 29 | 103.5 | 65.7 | 100.9 | 64.5 | 98.6 | 63.6 | 68.6 | 95.9 | 67.2 | 94.9 | 65.8 | 93.7 | 13.9 | 220 | 59 | 81.2 | 80.1 | 55.9 | 72.6 | 80.9 | 53.6 | 66.5 | 79.6 | 34 | 94.9 | 32.8 | 95 | 31.6 | 93.4 | 76.8 | 30.2 | 27.1 | 25 | 15.2 | 108.9 | 4 | 1.9 | 12.3 | 110.3 | 10 | 111.4 | 7.7 | 112.4 | 4.8 | 113.8 | 12.1 | 71.1 | 3.7 | 1.9 | 9.4 | 72.4 | 7.3 | 73.5 | 5.2 | 74.6 | 2.6 | 75.9 | 62.5 | 45.5 | 48.1 | 54 | 59.1 | 67.6 | 76.9 | 83.2 | 81.8 | 74.4 | 62.7 | 51.6 | 44.1 | 15.03 | 5.73 | 5.89 | 6.45 | 7.28 | 8.05 | 7.56 | 4.91 | 4.54 | 6.07 | 6.58 | 6.71 | 6.01 | 564 | 160 | 97 | 34 | 10 | 0 | 0 | 0 | 0 | 0 | 2 | 60 | 201 | 2883 | 604 | 475 | 343 | 204 | 69 | 9 | 0 | 0 | 7 | 122 | 402 | 648 | 5125 | 21 | 43 | 158 | 283 | 544 | 806 | 1030 | 987 | 731 | 396 | 109 | 17 | 1968 | 0 | 0 | 3 | 26 | 148 | 365 | 565 | 522 | 287 | 51 | 1 | 0 | 28071 | 1 | 14 | 177 | 567 | 1967 | 4829 | 7830 | 7312 | 4115 | 1155 | 104 | 0 | 15814 | 0 | 1 | 30 | 176 | 909 | 2744 | 4766 | 4462 | 2281 | 436 | 9 | 0 | 10.9 | 7.4 | 9.5 | 11.5 | 14.1 | 15 | 14.8 | 12.9 | 11.4 | 9.8 | 9.1 | 8.1 | 7.7 | 7.5 | 1.2 | 1.9 | 1.4 | 0.4 | 0.1 | 0 | 0.1 | 0.1 | 0.2 | 0.3 | 0.5 | 1.1 | 14.4 | 4.6 | 6.2 | 5.6 | 1.8 | 1.1 | 0.8 | 0.9 | 1 | 1.3 | 2.4 | 2.1 | 5.4 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 1.1 | 2.1 | 1.5 | 0.5 | 0.3 | 0.2 | 0.2 | 0.2 | 0.4 | 0.5 | 0.6 | 1.4 | 70.3 | 75.8 | 84.3 | 90.2 | 98.1 | 105.5 | 107.6 | 105.9 | 101.1 | 93 | 81.3 | 70.1 | 49.8 | 51.1 | 55 | 58.5 | 62.5 | 65 | 67.7 | 67.5 | 64.6 | 60.2 | 53.9 | 51.4 | 66.3 | 71.9 | 79 | 85 | 93.4 | 100.4 | 104.1 | 102.8 | 98.4 | 88.9 | 77.2 | 65.3 | 47.4 | 50 | 53.6 | 55.9 | 60.4 | 63.3 | 66.2 | 65.6 | 63.5 | 58.2 | 52.1 | 48.1 | 63.2 | 67.3 | 74.9 | 80.9 | 89.6 | 97.3 | 101.1 | 100.3 | 95.6 | 85 | 72.7 | 61.5 | 46.7 | 48.3 | 52 | 54.4 | 59.3 | 62.4 | 65 | 64.3 | 62.3 | 56.5 | 50.8 | 46 | 59.1 | 62.5 | 70.3 | 76.1 | 85.1 | 94 | 98.3 | 97.9 | 92.6 | 81 | 67.8 | 57.8 | 45.1 | 46.8 | 50.5 | 53 | 57.6 | 61.3 | 64.1 | 63.4 | 61 | 54.9 | 48.8 | 45.2 | 53.9 | 54.5 | 57.2 | 60.4 | 64.4 | 67.3 | 71 | 70.4 | 68.5 | 63.8 | 56.5 | 54.5 | 63.7 | 66.6 | 77.7 | 83.7 | 92.9 | 99.3 | 97.7 | 98.2 | 94 | 80.6 | 72.8 | 63.5 | 51.4 | 52 | 55.1 | 57.9 | 62.3 | 65.6 | 69.1 | 68.2 | 66.4 | 60.5 | 54.2 | 51.8 | 59.6 | 66.1 | 73.9 | 80.2 | 89.7 | 95.8 | 96.1 | 96.4 | 91.5 | 82.1 | 70.4 | 60.3 | 49.3 | 50.2 | 53.5 | 55.9 | 60.3 | 64.1 | 67.7 | 66.6 | 64.6 | 58.6 | 52.3 | 49.4 | 57.8 | 63.3 | 71 | 76.4 | 86.1 | 93.5 | 94.6 | 95.8 | 89.4 | 79.7 | 68.1 | 57.1 | 47.2 | 48.5 | 51.7 | 54.1 | 58.8 | 62.4 | 66.2 | 65 | 62.7 | 56.7 | 50.6 | 46.8 | 56.5 | 59.9 | 67.3 | 73.1 | 82.6 | 90.4 | 93.1 | 94.5 | 87.6 | 76.5 | 65.3 | 55.4 | 26.7 | 25.4 | 26.9 | 26.6 | 26.5 | 28.3 | 29 | 31.3 | 32.6 | 32.2 | 30 | 26.5 | 34.6 | 36.3 | 36.6 | 35.6 | 33.5 | 32.8 | 33.1 | 34.7 | 37.1 | 39.2 | 38.2 | 33.1 | 19.9 | 19 | 17.2 | 15.5 | 13.3 | 12.2 | 12.3 | 13.7 | 15.3 | 18.2 | 19.9 | 19.5 | 24.2 | 28.6 | 30.6 | 30.3 | 30.9 | 30.7 | 28.4 | 30.6 | 32.1 | 32.7 | 30.9 | 23.8 | 15 | 15.7 | 15 | 13.8 | 12.6 | 12 | 11.2 | 13.2 | 13.9 | 15.3 | 16.5 | 15.1 | 0.292 | 0.302 | 0.32 | 0.347 | 0.361 | 0.355 | 0.382 | 0.362 | 0.347 | 0.332 | 0.299 | 0.292 | 2.504 | 2.491 | 2.432 | 2.358 | 2.342 | 2.373 | 2.342 | 2.374 | 2.412 | 2.434 | 2.509 | 2.523 | 293 | 301 | 303 | 297 | 292 | 293 | 284 | 289 | 289 | 285 | 287 | 286 | 26 | 30 | 34 | 39 | 40 | 39 | 40 | 38 | 35 | 31 | 26 | 24 | 977 | 1263 | 1723 | 2128 | 2403 | 2626 | 2504 | 2353 | 1996 | 1501 | 1118 | 891 | 75 | 139 | 98 | 101 | 119 | 116 | 103 | 60 | 46 | 84 | 48 | 67 | N/A | N/A | -3.46 | N/A | N/A | 2.12 | N/A | N/A | N/A | N/A | 1.13 | N/A | -3.2 | 1.19 | N/A | N/A | N/A | -207 | 401 | 191 | 46
4 | USA | CA | PALMDALE | 723820 | 23182 | 34.629 | -118.084 | 2524 | 13.4 | -8 | NAP | 94-19 | 3B | 12 | 25.3 | 28 | -1.2 | 5.7 | 48 | 2.7 | 6.9 | 47.4 | 32.2 | 48.2 | 28.2 | 48.9 | 3.6 | 200 | 0.573 | 7 | 28.6 | 102.4 | 65.2 | 100.1 | 64.8 | 98 | 64 | 69.9 | 93.8 | 68.2 | 92.7 | 66.6 | 91.8 | 14.1 | 250 | 62.7 | 93.6 | 80.1 | 59.1 | 82.1 | 80.5 | 55.6 | 72.3 | 81.3 | 35.3 | 93.2 | 33.8 | 92.5 | 32.4 | 91.7 | 85.1 | 28.3 | 25.5 | 23.4 | 20.1 | 107.4 | 2.9 | 2 | 18 | 108.8 | 16.3 | 110 | 14.7 | 111.1 | 12.6 | 112.6 | 17 | 73.1 | 2.7 | 4.5 | 15 | 76.4 | 13.4 | 79 | 11.8 | 81.5 | 9.9 | 84.8 | 62.9 | 46.5 | 48.6 | 54.3 | 59.3 | 67.3 | 76.2 | 83.1 | 82.1 | 75.2 | 63.8 | 52.8 | 45.2 | 14.69 | 5.79 | 5.98 | 6.49 | 7.42 | 7.63 | 6.99 | 4.83 | 4.63 | 6.57 | 6.43 | 6.78 | 5.92 | 494 | 138 | 91 | 33 | 11 | 0 | 0 | 0 | 0 | 0 | 2 | 47 | 172 | 2730 | 575 | 459 | 333 | 200 | 67 | 7 | 0 | 0 | 8 | 100 | 366 | 615 | 5218 | 28 | 52 | 168 | 288 | 537 | 786 | 1025 | 995 | 756 | 429 | 132 | 22 | 1979 | 0 | 0 | 2 | 28 | 139 | 343 | 560 | 530 | 314 | 62 | 1 | 0 | 27842 | 3 | 16 | 154 | 574 | 1965 | 4723 | 7832 | 7263 | 4151 | 1056 | 103 | 2 | 15444 | 0 | 1 | 23 | 175 | 902 | 2639 | 4718 | 4352 | 2260 | 365 | 9 | 0 | 9.8 | 7.2 | 9 | 10.4 | 12.3 | 12.8 | 12.3 | 11 | 10 | 8.8 | 8.6 | 7.4 | 7.5 | 7 | 1.3 | 1.3 | 1.1 | 0.4 | 0.1 | 0 | 0 | 0.2 | 0.2 | 0.2 | 1 | 1 | 15.6 | 4.7 | 6.4 | 5.2 | 2.5 | 1.7 | 0.7 | 0.5 | 1.5 | 2.1 | 2 | 5.6 | 5.3 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 1.3 | 1.6 | 1.3 | 0.6 | 0.3 | 0.2 | 0.1 | 0.4 | 0.5 | 0.5 | 1.2 | 1.3 | 71.4 | 76.1 | 83.8 | 90 | 98.2 | 103.9 | 106.8 | 105.5 | 100.4 | 91.4 | 81.2 | 71.1 | 50.3 | 51.2 | 54.7 | 57.9 | 63.7 | 63.6 | 67.5 | 68.4 | 65 | 59.4 | 53.2 | 50.6 | 66.9 | 71.6 | 78.7 | 84.8 | 93.2 | 99.6 | 103.2 | 101.8 | 97.7 | 87.9 | 77.1 | 65.7 | 47.8 | 49.3 | 53.5 | 55.6 | 60.9 | 63.4 | 65.6 | 65.4 | 64.3 | 58 | 51.7 | 48.3 | 63.7 | 66.8 | 74.7 | 81.1 | 89.9 | 96.8 | 100.3 | 99.5 | 95.2 | 84.1 | 72.7 | 62.3 | 46.6 | 48.1 | 52.1 | 54.5 | 59.6 | 62.3 | 65 | 65 | 62.3 | 56.3 | 50.5 | 46.2 | 59.7 | 62.5 | 70.4 | 76.2 | 85.6 | 93.2 | 97.9 | 97.1 | 92.1 | 80.6 | 68 | 57.8 | 45.3 | 46.5 | 50.8 | 52.8 | 57.5 | 61.4 | 64.3 | 63.8 | 61.7 | 54.9 | 48.8 | 45 | 53.8 | 54.6 | 57.6 | 60.3 | 66.4 | 69.6 | 72.5 | 72.4 | 71.2 | 64 | 56.7 | 55 | 63.4 | 64.1 | 75.8 | 82.9 | 90.3 | 93.8 | 96 | 96.1 | 91.3 | 78.1 | 72.2 | 64.1 | 51.5 | 51.7 | 55.4 | 57.8 | 63.1 | 66 | 69.9 | 69.4 | 68.1 | 60.7 | 54.1 | 52.1 | 60.3 | 65.6 | 73 | 79.2 | 90 | 93.8 | 94 | 95.1 | 89 | 80.2 | 70.1 | 60.3 | 49.6 | 50 | 53.7 | 55.8 | 60.5 | 64.1 | 68.3 | 67.6 | 66.1 | 58.7 | 52.2 | 49.5 | 58.1 | 63.1 | 70.6 | 76.5 | 85.9 | 91.9 | 93 | 93.9 | 87.5 | 78.2 | 67.7 | 57.2 | 47.5 | 48.4 | 51.9 | 54 | 58.8 | 62.4 | 66.7 | 65.8 | 64 | 56.7 | 50.6 | 47 | 57.3 | 60 | 67.8 | 73 | 82.5 | 89.4 | 92 | 93 | 85.4 | 75.7 | 65.2 | 55.6 | 25.1 | 23.9 | 25.9 | 26.6 | 27.2 | 29.3 | 28.6 | 29.6 | 30.3 | 28.8 | 27.7 | 24.4 | 31.7 | 32.7 | 33.5 | 33.9 | 33.9 | 33.3 | 31.7 | 32 | 32.8 | 34.4 | 34.1 | 30.8 | 17 | 16 | 15 | 14.2 | 13.4 | 12.5 | 11.9 | 12.9 | 12.8 | 14.7 | 16.3 | 17 | 23.2 | 26.1 | 29.3 | 29.9 | 31.8 | 31.2 | 27.4 | 29.4 | 28.8 | 28.9 | 28.2 | 23.3 | 13.6 | 13.6 | 14.1 | 13.4 | 13.1 | 12.3 | 11.8 | 13.4 | 12 | 12.5 | 14.2 | 14 | 0.286 | 0.296 | 0.314 | 0.335 | 0.346 | 0.345 | 0.365 | 0.347 | 0.334 | 0.321 | 0.288 | 0.284 | 2.521 | 2.51 | 2.447 | 2.392 | 2.388 | 2.401 | 2.393 | 2.42 | 2.453 | 2.468 | 2.543 | 2.548 | 296 | 304 | 305 | 301 | 297 | 296 | 289 | 293 | 294 | 290 | 292 | 290 | 26 | 29 | 34 | 37 | 38 | 38 | 38 | 36 | 33 | 30 | 25 | 24 | 992 | 1278 | 1740 | 2141 | 2408 | 2623 | 2496 | 2348 | 1995 | 1508 | 1128 | 904 | 75 | 137 | 95 | 97 | 115 | 116 | 105 | 62 | 47 | 84 | 49 | 65 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 362 | N/A | 1.13 | N/A | -3.2 | 1.19 | N/A | N/A | N/A | -207 | 401 | 191 | 46
4 | USA | CA | SANDBERG | 723830 | 23187 | 34.744 | -118.724 | 4510 | 12.45 | -8 | NAP | 94-19 | 4A | 12 | 26.6 | 28.3 | -6.1 | 4.7 | 47 | -1.2 | 6.1 | 46.5 | 40.1 | 36.5 | 35.6 | 37.7 | 15.4 | 340 | 0.657 | 7 | 20.3 | 93.1 | 61 | 90.4 | 60.2 | 87.9 | 59.2 | 65.7 | 84.5 | 63.6 | 83.4 | 61.9 | 82.1 | 12.6 | 160 | 60.3 | 92.4 | 72 | 56.2 | 79.6 | 71.9 | 53.7 | 72.6 | 71 | 32.9 | 84.4 | 31.1 | 83.7 | 29.8 | 81.9 | 86.4 | 33.3 | 28.6 | 25.7 | 22.3 | 97.6 | 3.5 | 3 | 19.8 | 99.7 | 17.7 | 101.5 | 15.7 | 103.2 | 13.1 | 105.4 | 19.1 | 69.3 | 3.8 | 5.8 | 16.4 | 73.5 | 14.2 | 76.9 | 12.1 | 80.2 | 9.4 | 84.4 | 57.9 | 44.9 | 44.2 | 48.5 | 51.2 | 58.6 | 68.2 | 75.6 | 75.8 | 70.6 | 60.5 | 51.1 | 43.9 | 14.48 | 7.93 | 8.76 | 9.17 | 9.82 | 9.62 | 9.21 | 5.96 | 5.98 | 8.42 | 9.33 | 9.33 | 7.82 | 1027 | 197 | 207 | 144 | 105 | 30 | 3 | 0 | 0 | 1 | 22 | 98 | 220 | 3796 | 624 | 583 | 516 | 423 | 247 | 73 | 4 | 5 | 47 | 197 | 424 | 653 | 3893 | 38 | 45 | 96 | 141 | 296 | 550 | 795 | 800 | 620 | 348 | 131 | 33 | 1187 | 0 | 1 | 4 | 9 | 48 | 170 | 334 | 340 | 216 | 58 | 7 | 0 | 9865 | 0 | 3 | 13 | 50 | 345 | 1491 | 3037 | 3023 | 1599 | 292 | 12 | 0 | 3743 | 0 | 0 | 0 | 3 | 86 | 553 | 1244 | 1246 | 557 | 54 | 0 | 0 | 13.4 | 14.1 | 14.2 | 14 | 14.5 | 14.4 | 13.9 | 11.8 | 11.5 | 11.5 | 12.9 | 13.4 | 14.5 | 14.5 | 2.8 | 4 | 2.4 | 0.9 | 0.4 | 0.1 | 0.1 | 0.1 | 0.2 | 0.7 | 1.2 | 2.2 | 29.8 | 12.2 | 14.4 | 8.3 | 3 | 3.8 | 1.1 | 1.2 | 0.2 | 1 | 4.4 | 3.2 | 8 | 5.6 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 7.7 | 3.4 | 3.7 | 2 | 0.9 | 0.7 | 0.2 | 0.3 | 0 | 0.2 | 0.9 | 0.8 | 2.1 | 65.6 | 72 | 75.7 | 79.4 | 86.9 | 95.9 | 96.6 | 96.1 | 92.7 | 85.3 | 75.5 | 67.2 | 45.7 | 48.2 | 50.8 | 52.6 | 58.6 | 61.2 | 62.3 | 63 | 60.2 | 54.7 | 50.8 | 45.3 | 61.6 | 64.9 | 69.9 | 74.4 | 82.2 | 90.5 | 93 | 92.3 | 89.2 | 80.8 | 71.7 | 61.5 | 43.8 | 45.8 | 49.1 | 51.1 | 56.6 | 59.3 | 61.4 | 60.8 | 58.9 | 54.1 | 48.4 | 43.6 | 58.2 | 60.9 | 65.7 | 70.2 | 77.7 | 86.2 | 90 | 89.9 | 86.3 | 77.1 | 67.3 | 57.8 | 41.7 | 43.6 | 47.7 | 50.5 | 55.1 | 58.2 | 60.8 | 60 | 57.5 | 52.3 | 46.8 | 41.9 | 55.5 | 57 | 61.9 | 65.8 | 73.4 | 82.3 | 87 | 87.2 | 82.9 | 73.4 | 63.7 | 54.6 | 40.6 | 41.8 | 45.7 | 48.7 | 53.6 | 57.8 | 59.8 | 59 | 56.7 | 51 | 45.3 | 40.9 | 50.2 | 50.7 | 53.2 | 58.6 | 64.5 | 69.6 | 69.2 | 68.4 | 66.1 | 60.9 | 53.9 | 51.9 | 55.9 | 64.1 | 68.4 | 68 | 71.6 | 80.8 | 86.4 | 87.4 | 80.8 | 74.9 | 68.7 | 55.6 | 47.3 | 47.9 | 51 | 54.2 | 59 | 62.8 | 65.5 | 64.4 | 63 | 57.5 | 50.6 | 48.2 | 54.4 | 60 | 65.9 | 67.7 | 76.9 | 84.9 | 85.8 | 85.4 | 79.2 | 72.6 | 65.4 | 54.3 | 45.3 | 45.7 | 49.3 | 51.8 | 56.8 | 60.6 | 63.8 | 62.3 | 60.9 | 55 | 48.9 | 45.8 | 52.2 | 56.4 | 62.1 | 66.3 | 74.6 | 81.7 | 83.9 | 84.7 | 78.8 | 71.3 | 62.6 | 52.4 | 43.5 | 43.8 | 47.4 | 50 | 54.8 | 58.9 | 62 | 60.7 | 58.9 | 53 | 47.1 | 43.6 | 51 | 53.3 | 58.9 | 63.7 | 71.4 | 79.1 | 81.7 | 83 | 78.2 | 69.2 | 59.6 | 50.7 | 11.9 | 12.7 | 15.1 | 16.9 | 18.5 | 20.2 | 20.3 | 20.4 | 19.2 | 16.5 | 13.6 | 12.3 | 14.3 | 16.7 | 18.4 | 20.5 | 21.7 | 22.4 | 21.6 | 21.1 | 20.3 | 18.5 | 15.9 | 15.7 | 8.3 | 8.9 | 9.7 | 10.4 | 10.1 | 9.3 | 9 | 8.8 | 8.3 | 8.2 | 7.8 | 8.7 | 12.6 | 14.9 | 16.9 | 19 | 20.9 | 20.6 | 19.7 | 19.8 | 19.5 | 17.7 | 15.2 | 13.5 | 8.5 | 8.9 | 9.7 | 10.9 | 10.7 | 10.7 | 10.2 | 10 | 9.6 | 9.3 | 8.7 | 9.5 | 0.26 | 0.269 | 0.28 | 0.309 | 0.318 | 0.317 | 0.336 | 0.318 | 0.311 | 0.295 | 0.267 | 0.264 | 2.611 | 2.608 | 2.569 | 2.474 | 2.472 | 2.48 | 2.461 | 2.489 | 2.511 | 2.547 | 2.611 | 2.609 | 307 | 315 | 318 | 310 | 306 | 305 | 298 | 303 | 302 | 300 | 302 | 299 | 23 | 26 | 30 | 35 | 35 | 35 | 35 | 34 | 31 | 28 | 23 | 22 | 955 | 1238 | 1694 | 2102 | 2380 | 2599 | 2508 | 2355 | 1985 | 1485 | 1103 | 874 | 77 | 143 | 107 | 111 | 130 | 116 | 97 | 57 | 45 | 88 | 51 | 71 | 2.25 | N/A | -3.04 | 2.61 | N/A | N/A | -216 | -475 | 616 | 329 | 1.12 | N/A | -2.97 | 1.15 | N/A | N/A | N/A | -218 | 401 | 167 | 49
4 | USA | CA | MEADOWS FIELD | 723840 | 23155 | 35.434 | -119.054 | 489 | 14.44 | -8 | NAP | 94-19 | 3B | 12 | 33.3 | 36 | 17.7 | 13.6 | 59.7 | 22.5 | 17.2 | 55.6 | 24.6 | 60.4 | 19.7 | 58.2 | 2.6 | 130 | 0.427 | 7 | 25.7 | 103.2 | 69.8 | 100.9 | 69 | 98.6 | 68 | 73.4 | 96.8 | 71.6 | 95.4 | 70.1 | 93.7 | 11.3 | 300 | 64.9 | 93.7 | 87.5 | 62.3 | 85.4 | 85.2 | 60.3 | 79.5 | 83.8 | 37.1 | 97.1 | 35.6 | 96 | 34.2 | 93.6 | 85.1 | 18.2 | 15.5 | 12.9 | 29.2 | 108.2 | 3.3 | 1.8 | 26.8 | 109.5 | 24.8 | 110.5 | 23 | 111.5 | 20.5 | 112.9 | 27.4 | 75.4 | 3.2 | 3.9 | 25.1 | 78.2 | 23.3 | 80.4 | 21.5 | 82.6 | 19.2 | 85.4 | 66.2 | 49.8 | 53.5 | 58.7 | 63.2 | 70.8 | 78.7 | 84.9 | 83.4 | 78 | 67.3 | 56.4 | 49.2 | 13.88 | 5.53 | 5.27 | 6.15 | 7.35 | 7.34 | 7.18 | 5.32 | 5.03 | 6.44 | 6.3 | 6.05 | 5.68 | 199 | 72 | 22 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 84 | 1957 | 472 | 323 | 211 | 120 | 27 | 3 | 0 | 0 | 1 | 48 | 264 | 488 | 6122 | 65 | 119 | 275 | 397 | 644 | 860 | 1081 | 1037 | 841 | 537 | 206 | 60 | 2406 | 0 | 0 | 16 | 66 | 206 | 413 | 616 | 572 | 392 | 120 | 5 | 0 | 31099 | 3 | 22 | 245 | 817 | 2448 | 5420 | 8649 | 7596 | 4616 | 1201 | 81 | 1 | 17111 | 0 | 1 | 53 | 302 | 1122 | 3038 | 5262 | 4467 | 2427 | 427 | 12 | 0 | 5.8 | 4.6 | 5.2 | 5.7 | 6.8 | 7.1 | 7.2 | 6.9 | 6.3 | 5.8 | 5.1 | 4.3 | 4.5 | 6.1 | 1 | 1.2 | 1.1 | 0.6 | 0.2 | 0.1 | 0 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 13.3 | 3.9 | 5.4 | 4.3 | 2.6 | 2.4 | 0.5 | 0.3 | 1.2 | 1.1 | 1.8 | 3 | 1.8 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0.8 | 1.2 | 0.9 | 0.6 | 0.4 | 0.2 | 0 | 0.2 | 0.3 | 0.4 | 0.7 | 0.5 | 72 | 77.3 | 85.7 | 92.8 | 99.4 | 105.2 | 106.7 | 106 | 102 | 94.1 | 81.2 | 70.4 | 52.9 | 57.1 | 61.2 | 62.3 | 67.2 | 69.9 | 70.4 | 71.4 | 69 | 65.4 | 59.6 | 54.5 | 66.7 | 72 | 80.2 | 87.9 | 94.6 | 101.3 | 103.4 | 102.4 | 98.6 | 88.8 | 75.9 | 66 | 53.7 | 55.8 | 59.8 | 61 | 65.5 | 69.1 | 69.9 | 69.1 | 67.1 | 63.1 | 57.8 | 52.7 | 63.1 | 67.7 | 76 | 83.2 | 90.6 | 98 | 101.2 | 99.7 | 95.9 | 84.7 | 71.8 | 62.5 | 53 | 54.3 | 57.7 | 59.8 | 63.3 | 67.3 | 69.5 | 68.1 | 66.6 | 61.7 | 56.5 | 51.8 | 59.8 | 64.1 | 71.9 | 78.3 | 86.5 | 94.4 | 98.5 | 97 | 92.6 | 80.9 | 67.8 | 59.4 | 51.6 | 53.1 | 56.5 | 58.3 | 62.2 | 65.8 | 68.7 | 67.5 | 65.8 | 60.4 | 55.3 | 51.1 | 59.2 | 60.7 | 64.7 | 66 | 70.9 | 73.9 | 76.4 | 75.3 | 74.3 | 68.3 | 62.5 | 58.9 | 65.9 | 70.3 | 80.3 | 82.7 | 95.6 | 100.8 | 96.9 | 97.9 | 93.1 | 87.2 | 74.1 | 65.4 | 56.2 | 58.1 | 61.9 | 63.2 | 67.8 | 71.1 | 73.5 | 72.4 | 71.1 | 66 | 60.1 | 56.2 | 62 | 67.7 | 76.3 | 82.7 | 91 | 96.8 | 97.5 | 96.8 | 90.3 | 84.2 | 72.3 | 61.6 | 54.4 | 56.2 | 59.5 | 61 | 65.3 | 69.1 | 71.8 | 70.5 | 68.7 | 63.8 | 58.2 | 54.1 | 60.3 | 65 | 72.5 | 80.2 | 86.7 | 93.6 | 95.6 | 94.7 | 90 | 81.2 | 69.3 | 59.8 | 52.5 | 54.3 | 57.5 | 59.2 | 63.2 | 67.4 | 70.2 | 68.9 | 66.9 | 61.8 | 56.3 | 52 | 58.3 | 62.1 | 69.2 | 76 | 83.6 | 91.3 | 94.2 | 92.7 | 89.6 | 78.1 | 65.8 | 57.8 | 17.3 | 19.6 | 22.4 | 23.9 | 24.6 | 26.1 | 25.7 | 25.8 | 25.1 | 23.5 | 20.2 | 17.9 | 22.8 | 25.3 | 28.8 | 30.1 | 28.4 | 28 | 25.8 | 27 | 27.4 | 28.5 | 26.1 | 22 | 12.8 | 12.9 | 12.9 | 12.3 | 11.2 | 10.7 | 9.7 | 10.1 | 10.4 | 12.6 | 13.3 | 12.2 | 18 | 22.1 | 26.1 | 28.1 | 27.3 | 27.1 | 24.9 | 26.1 | 25.7 | 25.1 | 22.7 | 17.1 | 11.3 | 12.1 | 12.9 | 12.1 | 11.4 | 11.2 | 10.8 | 10.9 | 10.2 | 11.3 | 12.2 | 10.5 | 0.326 | 0.338 | 0.343 | 0.372 | 0.379 | 0.369 | 0.4 | 0.376 | 0.372 | 0.37 | 0.342 | 0.328 | 2.443 | 2.415 | 2.407 | 2.329 | 2.336 | 2.364 | 2.316 | 2.351 | 2.373 | 2.344 | 2.401 | 2.447 | 277 | 286 | 294 | 289 | 287 | 288 | 279 | 284 | 280 | 270 | 267 | 268 | 28 | 32 | 35 | 40 | 40 | 39 | 41 | 38 | 36 | 34 | 29 | 26 | 863 | 1188 | 1656 | 2091 | 2435 | 2690 | 2549 | 2371 | 2000 | 1470 | 1045 | 799 | 85 | 129 | 118 | 118 | 120 | 87 | 92 | 61 | 48 | 76 | 49 | 79 | 1.42 | N/A | -3.55 | N/A | -1.58 | -1.76 | -65 | -306 | 490 | 268 | 1.1 | N/A | -2.66 | 1.17 | N/A | N/A | N/A | -232 | 392 | 160 | 40
4 | USA | CA | FRESNO YOSEMITE | 723890 | 93193 | 36.78 | -119.719 | 333 | 14.52 | -8 | NAP | 94-19 | 3B | 12 | 32.5 | 34.8 | 22.9 | 17.4 | 58.8 | 26.4 | 20.6 | 56.2 | 18.5 | 52.7 | 16.5 | 52.2 | 2 | 90 | 0.446 | 7 | 29.1 | 103.8 | 69.6 | 101.3 | 68.6 | 98.8 | 67.7 | 73.1 | 96.9 | 71.4 | 94.6 | 69.9 | 92.9 | 8.1 | 300 | 65.1 | 94 | 84.7 | 62.8 | 86.6 | 83.5 | 60.8 | 80.6 | 81.5 | 36.8 | 96.6 | 35.3 | 94.7 | 34 | 92.8 | 83.3 | 18.3 | 16.4 | 14.4 | 29.3 | 108.2 | 2.6 | 1.9 | 27.5 | 109.6 | 26 | 110.7 | 24.5 | 111.8 | 22.7 | 113.2 | 28.1 | 75.6 | 2.6 | 3.6 | 26.2 | 78.2 | 24.7 | 80.3 | 23.2 | 82.4 | 21.3 | 85 | 65.2 | 48.6 | 52.2 | 57.7 | 62.4 | 70 | 77.8 | 83.8 | 82.4 | 77.1 | 66.5 | 55.5 | 47.9 | 13.8 | 5 | 4.92 | 5.93 | 7.01 | 7.11 | 6.8 | 5.11 | 4.68 | 6.06 | 6.04 | 5.87 | 5.11 | 246 | 88 | 30 | 7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 102 | 2138 | 510 | 358 | 235 | 131 | 30 | 2 | 0 | 0 | 2 | 53 | 288 | 529 | 5807 | 44 | 92 | 247 | 372 | 621 | 834 | 1048 | 1004 | 812 | 512 | 183 | 38 | 2223 | 0 | 0 | 9 | 52 | 186 | 387 | 583 | 539 | 364 | 100 | 3 | 0 | 29602 | 0 | 4 | 162 | 710 | 2381 | 5265 | 8270 | 7237 | 4414 | 1103 | 56 | 0 | 16698 | 0 | 0 | 26 | 244 | 1094 | 3005 | 5161 | 4397 | 2391 | 375 | 5 | 0 | 5.9 | 4 | 4.8 | 5.8 | 7.2 | 8.2 | 8.4 | 7.5 | 6.8 | 5.9 | 4.6 | 3.7 | 3.8 | 11 | 2.1 | 2 | 2 | 0.9 | 0.4 | 0.2 | 0 | 0 | 0.2 | 0.6 | 1.3 | 1.5 | 21.6 | 8.5 | 6.1 | 7.2 | 4.4 | 1.7 | 1.9 | 0.2 | 0.2 | 1.2 | 2.4 | 3.5 | 4.3 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9 | 1.7 | 1.7 | 1.6 | 1 | 0.5 | 0.4 | 0 | 0 | 0.4 | 0.7 | 1 | 1 | 68.3 | 73.9 | 83.5 | 91.7 | 99.3 | 105.3 | 107.4 | 106.3 | 102.5 | 94 | 79.7 | 67 | 53 | 57.3 | 60.5 | 62.8 | 66.8 | 69.9 | 70.7 | 70.8 | 68.1 | 65.5 | 59.6 | 55 | 64 | 69.2 | 78.4 | 86.6 | 94.6 | 101.6 | 104.2 | 102.7 | 98.9 | 88 | 74.9 | 63 | 53.8 | 56.9 | 59.9 | 61.7 | 65.4 | 68.4 | 69.9 | 69.2 | 67.3 | 63.3 | 58.3 | 53.3 | 60.6 | 65.5 | 74.6 | 82.1 | 90.5 | 98.1 | 101.6 | 100.1 | 96 | 84 | 70.6 | 60 | 52.7 | 54.7 | 58.2 | 60.2 | 63.6 | 66.8 | 69.1 | 67.9 | 66.5 | 61.7 | 57 | 52 | 57.7 | 62.2 | 70.8 | 77.4 | 86.3 | 94.5 | 98.8 | 97.4 | 92.7 | 80.4 | 66.8 | 57.1 | 51.8 | 53.5 | 57 | 58.9 | 62.2 | 65.8 | 68.4 | 67.4 | 65.6 | 60.4 | 55.5 | 51 | 58.9 | 60.5 | 64.3 | 66.6 | 70 | 74.1 | 75.4 | 76.4 | 72.3 | 67.9 | 62.4 | 58.9 | 63.2 | 67.7 | 77.5 | 82.9 | 92.6 | 98.3 | 100.3 | 98.7 | 94.1 | 86.1 | 74.4 | 63.6 | 55.9 | 58.3 | 62 | 63.6 | 67.6 | 71.7 | 73.3 | 72.5 | 70.2 | 65.8 | 60.2 | 55.9 | 60 | 66.2 | 74.8 | 81.3 | 90.4 | 95.4 | 98.3 | 94.7 | 91.5 | 83.2 | 71.1 | 59.6 | 54.1 | 56.4 | 59.8 | 61.6 | 65.5 | 69.4 | 71.5 | 70.5 | 68.3 | 63.7 | 58.5 | 53.9 | 58.3 | 63.6 | 71.4 | 78.8 | 86.6 | 92 | 95.4 | 93.6 | 90.5 | 80.5 | 68.1 | 57.7 | 52.2 | 54.5 | 57.9 | 59.7 | 63.4 | 67.6 | 70.1 | 68.9 | 66.9 | 61.9 | 56.6 | 51.9 | 56.7 | 60.8 | 68.4 | 75.3 | 83.1 | 90.1 | 93.6 | 92.2 | 89.2 | 77.4 | 64.8 | 55.8 | 15.8 | 18.1 | 21.2 | 23.3 | 25.6 | 28.4 | 29.1 | 29.4 | 27.7 | 24.5 | 19.8 | 16.1 | 21.3 | 23.2 | 27.4 | 30 | 30.6 | 30.9 | 30 | 30.8 | 30.7 | 29.4 | 25.9 | 20.3 | 12.5 | 12.2 | 11.6 | 10.6 | 9.9 | 9.2 | 9 | 8.8 | 9.2 | 10.5 | 12.1 | 11.8 | 15.8 | 20.2 | 24.7 | 27.3 | 28.9 | 29.4 | 28.3 | 29.2 | 28.5 | 26.5 | 22.4 | 13.7 | 10.1 | 11.3 | 11.6 | 10.4 | 10 | 9.6 | 9.7 | 9.5 | 9.2 | 9.8 | 11.3 | 9.1 | 0.359 | 0.372 | 0.395 | 0.378 | 0.368 | 0.364 | 0.383 | 0.368 | 0.371 | 0.39 | 0.38 | 0.371 | 2.324 | 2.304 | 2.239 | 2.331 | 2.387 | 2.399 | 2.374 | 2.389 | 2.391 | 2.283 | 2.253 | 2.266 | 259 | 271 | 275 | 286 | 290 | 290 | 283 | 286 | 279 | 260 | 247 | 243 | 31 | 35 | 41 | 40 | 38 | 37 | 38 | 37 | 35 | 36 | 33 | 30 | 773 | 1105 | 1572 | 2001 | 2379 | 2669 | 2570 | 2357 | 1958 | 1422 | 962 | 705 | 111 | 129 | 136 | 152 | 137 | 98 | 97 | 72 | 60 | 81 | 54 | 98 | 1.01 | N/A | -2.2 | N/A | N/A | -1.44 | -68 | -223 | 344 | 205 | 0.92 | N/A | -2.05 | 0.79 | N/A | N/A | N/A | -245 | 301 | 95 | 23
4 | USA | CA | MAMMOTH YOSEMITE | 723894 | 03181 | 37.633 | -118.85 | 7128 | 11.28 | -8 | NAP | 08-19 | 6A | 12 | -0.2 | 5.1 | -11.2 | 3.9 | 24.7 | -7.2 | 4.9 | 25.1 | 35.2 | 43.3 | 28.9 | 42 | 2.5 | 350 | 0.643 | 7 | 36.1 | 86.3 | 54.2 | 84.3 | 53.5 | 82.2 | 52.6 | 57.3 | 77.3 | 56 | 77.1 | 54.8 | 76.7 | 11.9 | 280 | 50.8 | 72 | 61.5 | 47.9 | 64.5 | 61.6 | 45.3 | 58.3 | 60.8 | 27.9 | 77.1 | 26.8 | 76.4 | 25.9 | 76.8 | 62.2 | 26.9 | 23 | 19.2 | -12.7 | 90.1 | 7.2 | 2.4 | -17.9 | 91.8 | -22.1 | 93.2 | -26.1 | 94.5 | -31.4 | 96.2 | -13.2 | 60.4 | 7.1 | 1.1 | -18.3 | 61.2 | -22.4 | 61.9 | -26.4 | 62.5 | -31.6 | 63.4 | 45.2 | 28.9 | 30.5 | 36 | 42.9 | 49.1 | 59.2 | 64.5 | 62.7 | 56.7 | 46.3 | 36.4 | 28.4 | 14.6 | 9.24 | 9.62 | 7.6 | 7.37 | 6.46 | 6.23 | 4.23 | 3.86 | 5.33 | 5.84 | 7.95 | 8.8 | 3195 | 654 | 547 | 435 | 226 | 94 | 8 | 0 | 0 | 14 | 139 | 408 | 670 | 7301 | 1119 | 966 | 900 | 664 | 492 | 190 | 59 | 90 | 251 | 578 | 857 | 1135 | 1447 | 0 | 1 | 0 | 12 | 67 | 282 | 449 | 394 | 214 | 26 | 2 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 15 | 43 | 19 | 1 | 0 | 0 | 0 | 4287 | 0 | 0 | 0 | 2 | 42 | 830 | 1636 | 1325 | 429 | 23 | 0 | 0 | 1032 | 0 | 0 | 0 | 0 | 1 | 202 | 473 | 314 | 42 | 0 | 0 | 0 | 6.6 | 4.9 | 6.4 | 7.1 | 8.5 | 8.3 | 8 | 6.5 | 6.2 | 6.1 | 5.8 | 5.5 | 5.7 | 13.6 | 2.2 | 2.1 | 1.7 | 1 | 0.8 | 0.4 | 0.5 | 0.4 | 0.4 | 0.8 | 1 | 2 | 20.7 | 6 | 7 | 6.8 | 3 | 2 | 1.7 | 1.1 | 0.8 | 1.4 | 2.9 | 3.5 | 7.4 | 6.9 | 0.2 | 0.3 | 0.1 | 0.2 | 0.2 | 0 | 0.1 | 0.1 | 0 | 0 | 0.1 | 0.2 | 3.4 | 1.7 | 1.3 | 1.6 | 0.6 | 0.5 | 0.4 | 0.3 | 0.2 | 0.3 | 0.7 | 0.8 | 1.5 | 59.3 | 63.1 | 66.1 | 72.5 | 78.6 | 88.5 | 89.9 | 88.2 | 83.6 | 77.1 | 68.4 | 59.3 | 39.3 | 41 | 43 | 47.1 | 49.2 | 55.1 | 55.3 | 54.4 | 51.5 | 47.9 | 44.1 | 38.9 | 54.4 | 58.8 | 61.4 | 68.4 | 74.6 | 85 | 87.1 | 85.6 | 81.2 | 72.5 | 63.9 | 54.8 | 36.9 | 38.8 | 39.7 | 44.6 | 47.7 | 53.4 | 54.7 | 53.5 | 51.2 | 46.3 | 42.1 | 36.7 | 50 | 54.2 | 57.4 | 65.6 | 71.7 | 82 | 84.8 | 83.7 | 79 | 68.5 | 59.8 | 50.2 | 35.6 | 36.8 | 38.4 | 43.1 | 46.8 | 51.9 | 54.2 | 52.9 | 50.3 | 44.9 | 40 | 35.6 | 45 | 48.1 | 53.9 | 61.7 | 67.9 | 79.2 | 82.3 | 81.4 | 76.6 | 64.5 | 54.8 | 45.8 | 33.7 | 34.8 | 37.5 | 41.5 | 45.3 | 51 | 53.5 | 52.1 | 49.6 | 43.2 | 37.9 | 33.9 | 40.7 | 42.1 | 43.5 | 48.6 | 51 | 57.1 | 59.5 | 58.2 | 56.3 | 50.7 | 45.7 | 41.7 | 54.4 | 59.1 | 63 | 68.3 | 73.5 | 81.9 | 76.7 | 77.4 | 73 | 66.2 | 64.4 | 53.2 | 38.3 | 39.8 | 41.2 | 46.1 | 49.3 | 55.2 | 58 | 56.4 | 53.9 | 48.6 | 43.2 | 39.1 | 49.7 | 55.5 | 58.7 | 65.1 | 70.2 | 80.1 | 76.9 | 76.9 | 74.7 | 66.5 | 60.6 | 49.9 | 36.7 | 37.4 | 39.6 | 44 | 47.9 | 53.5 | 56.7 | 55 | 52.2 | 46.4 | 41.2 | 36.9 | 46.9 | 51.3 | 55.8 | 63.2 | 67.6 | 77.9 | 76.9 | 76.4 | 74.1 | 64.1 | 57.5 | 48.4 | 34.4 | 35.3 | 37.8 | 42.2 | 46.3 | 52 | 55.5 | 53.8 | 50.7 | 44.6 | 38.9 | 34.4 | 43.3 | 47.5 | 51.2 | 60 | 65 | 75.7 | 76.8 | 76.4 | 73.2 | 61.5 | 53.7 | 45.3 | 28.1 | 27 | 27.9 | 29.9 | 30.2 | 34.5 | 36.1 | 37.7 | 37 | 34.9 | 32.9 | 28.2 | 35.6 | 35.2 | 36.1 | 37 | 37.2 | 39.3 | 38.2 | 40.6 | 40.7 | 41.5 | 40.5 | 35.2 | 20.9 | 18.8 | 18.2 | 17.5 | 16.7 | 15.8 | 14.5 | 16.2 | 17.6 | 20 | 21.5 | 20.2 | 29 | 32.2 | 33 | 34.6 | 34.7 | 36.4 | 33.4 | 35.1 | 35.7 | 35.9 | 37.6 | 30.8 | 17.9 | 17.8 | 17 | 16.8 | 15.7 | 14.5 | 12.9 | 14 | 15.4 | 17.6 | 20.2 | 18.1 | 0.245 | 0.26 | 0.261 | 0.298 | 0.303 | 0.298 | 0.314 | 0.298 | 0.282 | 0.269 | 0.244 | 0.242 | 2.427 | 2.383 | 2.436 | 2.402 | 2.466 | 2.503 | 2.503 | 2.532 | 2.582 | 2.592 | 2.599 | 2.485 | 305 | 312 | 321 | 312 | 310 | 310 | 304 | 308 | 310 | 306 | 305 | 299 | 26 | 31 | 33 | 36 | 35 | 34 | 34 | 32 | 29 | 25 | 22 | 23 | 830 | 1112 | 1528 | 1965 | 2269 | 2627 | 2485 | 2318 | 1954 | 1427 | 983 | 736 | 81 | 117 | 117 | 126 | 183 | 167 | 146 | 118 | 76 | 100 | 56 | 84 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.97 | N/A | N/A | 0.79 | N/A | N/A | -85 | -203 | 236 | 119 | 18
4 | USA | CA | PORTERVILLE | 723895 | 23149 | 36.029 | -119.063 | 442 | 14.46 | -8 | NAP | 94-19 | 3B | 12 | 30.2 | 33.1 | 20.8 | 15.9 | 40.8 | 24.8 | 19.2 | 43.3 | 15.3 | 52.3 | 12.3 | 52.3 | 3.1 | 110 | 0.428 | 7 | 31.4 | 101.7 | 70.8 | 99.5 | 69.5 | 97.4 | 68.4 | 73.3 | 96.9 | 71.5 | 94.7 | 70.1 | 93.4 | 9.1 | 320 | 64.2 | 91.4 | 86.4 | 62.9 | 87.3 | 85.1 | 61 | 81.6 | 83.3 | 37 | 96.6 | 35.4 | 95.1 | 34.2 | 92.3 | 79.9 | 12.9 | 11.5 | 10.4 | 27.4 | 106.4 | 2.6 | 2.1 | 25.6 | 107.9 | 24.1 | 109.1 | 22.7 | 110.3 | 20.8 | 111.8 | 26.1 | 75.2 | 2.1 | 2.3 | 24.6 | 76.9 | 23.4 | 78.3 | 22.3 | 79.6 | 20.8 | 81.3 | 63.3 | 47.8 | 50.9 | 55.6 | 60.3 | 67.7 | 75.4 | 80.9 | 79.3 | 74.6 | 64.5 | 54 | 47.3 | 13.13 | 4.97 | 4.91 | 5.72 | 6.87 | 6.91 | 6.54 | 4.8 | 4.53 | 5.87 | 6.09 | 5.63 | 5.16 | 309 | 104 | 43 | 15 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 118 | 2423 | 535 | 395 | 296 | 174 | 49 | 5 | 0 | 0 | 4 | 83 | 332 | 550 | 5148 | 35 | 68 | 188 | 313 | 550 | 763 | 958 | 908 | 739 | 449 | 144 | 33 | 1786 | 0 | 0 | 4 | 33 | 134 | 318 | 493 | 443 | 293 | 67 | 1 | 0 | 25484 | 0 | 6 | 140 | 671 | 2120 | 4701 | 7035 | 5997 | 3758 | 1003 | 53 | 0 | 14120 | 0 | 0 | 23 | 227 | 981 | 2680 | 4286 | 3558 | 2027 | 334 | 4 | 0 | 5 | 3.8 | 4.3 | 4.8 | 5.5 | 6 | 6.2 | 6 | 5.7 | 5.2 | 4.6 | 3.9 | 3.8 | 10.7 | 1.9 | 1.9 | 1.8 | 1.1 | 0.4 | 0.1 | 0 | 0 | 0.2 | 0.6 | 1.5 | 1.5 | 19.4 | 7.9 | 6.5 | 5.3 | 4.8 | 2.9 | 0.5 | 0.2 | 0.3 | 1.5 | 2.6 | 3.5 | 5.6 | 5.2 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 1.7 | 1.7 | 1.3 | 1.1 | 0.6 | 0.1 | 0 | 0 | 0.4 | 0.7 | 1 | 1.2 | 67.7 | 73.5 | 82.4 | 90.8 | 99.2 | 104.3 | 105.8 | 103.8 | 100.2 | 92.8 | 79.8 | 68.2 | 56 | 58.6 | 62.2 | 64 | 67.8 | 71.9 | 73 | 72.1 | 69.7 | 66 | 60.1 | 55.4 | 63.7 | 69.6 | 78.7 | 86.1 | 93.4 | 100.2 | 101.9 | 100.1 | 97.4 | 88 | 74.7 | 63.8 | 53.9 | 57.2 | 60.7 | 62.4 | 65.3 | 68.8 | 71.3 | 69.9 | 67.9 | 64 | 58.4 | 53.3 | 60.9 | 64.3 | 73.3 | 81.8 | 90.2 | 97.4 | 99.6 | 98.7 | 94.6 | 83.5 | 70.5 | 60.9 | 53 | 54.8 | 58.4 | 60.8 | 63.9 | 67.5 | 70.4 | 69.2 | 67.3 | 62 | 56.7 | 52.1 | 57.1 | 61.5 | 70.1 | 77.1 | 85.5 | 93.3 | 97.3 | 95.6 | 91.1 | 80.6 | 65.9 | 57 | 51.2 | 53.1 | 56.8 | 59.1 | 62.8 | 66.2 | 69.1 | 68 | 65.9 | 60.9 | 54.8 | 50.7 | 59.2 | 60.8 | 64.7 | 67.8 | 70.1 | 74.7 | 75.8 | 74.3 | 73.4 | 68.4 | 62.5 | 58.9 | 64 | 68.6 | 77.8 | 84.5 | 94.6 | 99.3 | 99.5 | 99.3 | 95.9 | 87.4 | 75.3 | 64.6 | 56 | 58.7 | 62.1 | 64 | 67.3 | 71.3 | 73.6 | 72.1 | 70.2 | 65.8 | 60.2 | 55.9 | 61.1 | 66.5 | 75.7 | 82.3 | 91 | 95.9 | 97.3 | 95.7 | 92.1 | 83.2 | 71.4 | 60.6 | 54 | 56.4 | 59.7 | 61.8 | 65.2 | 69.2 | 72 | 70.6 | 68.4 | 63.8 | 58.2 | 53.6 | 59 | 63.4 | 71.8 | 79.3 | 87 | 93.9 | 95.3 | 94 | 91.3 | 80 | 68 | 58.5 | 52 | 54.1 | 57.4 | 59.8 | 63.3 | 67.5 | 70.4 | 69.2 | 66.9 | 61.7 | 55.9 | 51.4 | 56.7 | 60.6 | 67.9 | 75.5 | 83.7 | 91.3 | 93.5 | 92.6 | 89.6 | 78.2 | 64.6 | 56.2 | 17.7 | 20.4 | 24.9 | 27.5 | 29.4 | 32.1 | 31.4 | 31.7 | 30.8 | 27.4 | 22.6 | 18.7 | 23.3 | 25.6 | 31.1 | 33.9 | 34.4 | 34.8 | 32.2 | 32.9 | 33 | 32.5 | 29.4 | 23.7 | 15.6 | 16.3 | 16.7 | 15.7 | 14 | 13.9 | 12.7 | 13.1 | 13.8 | 15 | 16.9 | 15.3 | 19.5 | 23.1 | 28.9 | 31.4 | 32.8 | 33.1 | 30.7 | 31.2 | 31.3 | 28.3 | 25.6 | 18.1 | 13.7 | 15.5 | 16.3 | 15.3 | 13.9 | 13.6 | 12.5 | 13 | 13.6 | 13.4 | 15.3 | 12.5 | 0.352 | 0.364 | 0.365 | 0.396 | 0.404 | 0.388 | 0.422 | 0.397 | 0.388 | 0.391 | 0.359 | 0.354 | 2.344 | 2.321 | 2.335 | 2.256 | 2.262 | 2.319 | 2.257 | 2.301 | 2.329 | 2.272 | 2.336 | 2.333 | 264 | 275 | 286 | 281 | 279 | 283 | 272 | 278 | 275 | 261 | 258 | 253 | 30 | 35 | 37 | 43 | 43 | 41 | 43 | 40 | 37 | 36 | 30 | 29 | 827 | 1146 | 1612 | 2040 | 2391 | 2679 | 2534 | 2358 | 1980 | 1449 | 1011 | 758 | 93 | 125 | 125 | 128 | 135 | 102 | 105 | 74 | 55 | 80 | 51 | 86 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.92 | N/A | -2.03 | 0.83 | N/A | N/A | N/A | -221 | 311 | 122 | 25
4 | USA | CA | VISALIA | 723896 | 93144 | 36.317 | -119.4 | 295 | 14.54 | -8 | NAP | 94-19 | 3B | 12 | 29.9 | 32.6 | 22.9 | 17.5 | 42 | 27 | 21.2 | 40.1 | 16.8 | 52.3 | 14 | 52.2 | 2.1 | 120 | 0.42 | 7 | 31 | 100.3 | 71.8 | 98.9 | 71 | 96.7 | 70.1 | 74.9 | 95.7 | 73.2 | 93.6 | 71.7 | 92 | 7.4 | 300 | 68.1 | 104.2 | 85.3 | 65.8 | 96.2 | 84.4 | 63.9 | 89.8 | 83.4 | 38.3 | 95.2 | 36.9 | 94.1 | 35.5 | 91.8 | 83.5 | 15.6 | 12.6 | 11 | 26.8 | 105.7 | 2.9 | 2 | 24.7 | 107.2 | 23 | 108.3 | 21.4 | 109.5 | 19.3 | 110.9 | 25.7 | 77.4 | 3.3 | 1.8 | 23.3 | 78.7 | 21.4 | 79.7 | 19.6 | 80.7 | 17.2 | 82 | 63.1 | 47.5 | 50.9 | 56.4 | 61 | 68.5 | 75.5 | 80.3 | 78.5 | 73.7 | 63.9 | 53.7 | 46.4 | 12.91 | 5.02 | 4.87 | 5.47 | 6.57 | 6.4 | 5.95 | 4.35 | 4.32 | 5.42 | 5.72 | 5.48 | 5.26 | 330 | 111 | 44 | 9 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 137 | 2413 | 544 | 396 | 271 | 154 | 37 | 4 | 0 | 0 | 4 | 87 | 341 | 575 | 5108 | 32 | 68 | 208 | 332 | 573 | 766 | 939 | 883 | 712 | 432 | 136 | 27 | 1714 | 0 | 0 | 4 | 34 | 144 | 320 | 474 | 418 | 266 | 54 | 0 | 0 | 23063 | 0 | 1 | 120 | 622 | 2052 | 4368 | 6296 | 5346 | 3339 | 889 | 30 | 0 | 12346 | 0 | 0 | 18 | 200 | 923 | 2421 | 3696 | 3063 | 1737 | 287 | 1 | 0 | 4.5 | 3.4 | 4 | 4.5 | 5.5 | 6.2 | 6.3 | 5.4 | 4.8 | 4.3 | 3.7 | 3.1 | 3.3 | 9.9 | 1.7 | 1.9 | 1.7 | 1 | 0.2 | 0.1 | 0 | 0 | 0.2 | 0.4 | 1.3 | 1.4 | 18.1 | 7.7 | 5.8 | 5 | 4.8 | 2.2 | 0.7 | 0.2 | 0.2 | 1.5 | 1.9 | 3.5 | 3.8 | 5 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 1.6 | 1.7 | 1.3 | 1.1 | 0.5 | 0.2 | 0.1 | 0 | 0.4 | 0.5 | 1 | 0.9 | 66.2 | 72.7 | 82.2 | 90.5 | 99 | 103.1 | 103.8 | 102.3 | 99.4 | 92.6 | 78.1 | 66.3 | 54.6 | 59.3 | 62.6 | 63.9 | 69.2 | 72.4 | 73.5 | 73.2 | 70 | 66.6 | 59.9 | 55.5 | 63.2 | 67.9 | 77.2 | 85.2 | 93.1 | 99.6 | 100.3 | 99.4 | 96.8 | 87.6 | 73.4 | 62.9 | 54.1 | 57.9 | 60.6 | 63 | 66.4 | 70.2 | 72.7 | 71.7 | 69 | 64.4 | 58.8 | 53.6 | 60.5 | 64 | 73.1 | 81.4 | 89.9 | 96.9 | 98.7 | 97.2 | 93.2 | 82.4 | 69.8 | 59.1 | 53.6 | 55.4 | 58.7 | 60.9 | 64.8 | 68.9 | 72 | 70.7 | 68 | 62.3 | 57.6 | 52 | 56.8 | 61.2 | 70 | 76.7 | 84.7 | 92.7 | 96.3 | 93.9 | 90.5 | 79.3 | 65.5 | 55.7 | 51.7 | 53.6 | 57.6 | 59.3 | 63.1 | 67.2 | 71 | 69.6 | 67 | 61.1 | 55.7 | 50.5 | 59.5 | 61.3 | 64.9 | 67.1 | 71.3 | 75.6 | 77.9 | 76.7 | 74 | 68.8 | 62.8 | 58.7 | 63.2 | 69 | 78.5 | 84.8 | 95.3 | 98.6 | 98.6 | 97.1 | 93.1 | 86.8 | 73.2 | 63.4 | 56 | 59 | 62.3 | 64.3 | 68.3 | 72.8 | 75.3 | 74.1 | 71.2 | 66.2 | 60.6 | 55.5 | 60.2 | 65.9 | 74.7 | 81.7 | 90.2 | 95.1 | 95.9 | 94.4 | 90.7 | 83.1 | 70.5 | 59.8 | 54.1 | 56.9 | 60.1 | 62.1 | 66.2 | 70.6 | 73.6 | 72.5 | 69.4 | 64.1 | 58.5 | 53.5 | 58.1 | 63.1 | 71.3 | 78.5 | 86.4 | 91.9 | 93.9 | 92.6 | 89.8 | 80 | 67.7 | 57.6 | 52.4 | 54.5 | 58 | 60.1 | 64.2 | 68.6 | 72.1 | 71 | 68 | 62.2 | 56.5 | 51.3 | 56.6 | 60.3 | 68 | 74.9 | 83 | 89.5 | 92.2 | 91 | 88 | 76.7 | 64.3 | 55.3 | 16.7 | 19.3 | 23.2 | 25.7 | 27.6 | 30.8 | 31 | 31.8 | 31 | 28.1 | 22.4 | 17.9 | 22.4 | 24.1 | 29.2 | 32.5 | 33.7 | 34.7 | 32.5 | 33.4 | 34 | 33.3 | 28.5 | 22.6 | 15.2 | 15.5 | 15.5 | 14.4 | 12.8 | 12 | 11.2 | 11.7 | 12.5 | 14.5 | 15.8 | 14.9 | 17.6 | 22 | 26.7 | 30.5 | 32 | 32.8 | 30.5 | 31.9 | 31.9 | 29.7 | 25.1 | 16.7 | 12.7 | 14.7 | 15 | 14 | 12.7 | 12 | 11.3 | 11.9 | 12.4 | 13.4 | 14.9 | 11.8 | 0.366 | 0.377 | 0.376 | 0.386 | 0.386 | 0.377 | 0.402 | 0.377 | 0.376 | 0.395 | 0.376 | 0.364 | 2.284 | 2.278 | 2.298 | 2.295 | 2.321 | 2.348 | 2.31 | 2.355 | 2.365 | 2.256 | 2.27 | 2.293 | 256 | 270 | 282 | 284 | 285 | 286 | 278 | 284 | 278 | 259 | 250 | 248 | 32 | 36 | 39 | 41 | 41 | 40 | 41 | 38 | 36 | 36 | 32 | 30 | 776 | 1123 | 1602 | 2034 | 2402 | 2676 | 2550 | 2352 | 1966 | 1433 | 978 | 716 | 109 | 124 | 132 | 141 | 129 | 87 | 94 | 68 | 55 | 75 | 53 | 95 | 1.24 | N/A | N/A | 0.86 | N/A | N/A | N/A | N/A | N/A | N/A | 1.04 | N/A | -1.94 | 0.99 | N/A | N/A | -52 | -257 | 351 | 137 | 21
4 | USA | CA | HANFORD | 723898 | 53119 | 36.319 | -119.629 | 249 | 14.56 | -8 | NAP | 98-19 | 3B | 12 | 28.5 | 30.9 | 22.4 | 17 | 47.3 | 25.7 | 19.9 | 46.3 | 17.5 | 51.8 | 15.5 | 51.5 | 1.3 | 60 | 0.448 | 7 | 31.4 | 102.3 | 69.8 | 99.9 | 69.4 | 97.8 | 68.4 | 73.6 | 95.4 | 72 | 93.8 | 70.4 | 92.5 | 6.8 | 330 | 66.2 | 97.3 | 83.4 | 63.8 | 89.4 | 83.4 | 62.1 | 84.1 | 81.6 | 37.3 | 95.8 | 35.7 | 93.7 | 34.3 | 92.7 | 84.9 | 16.9 | 14.9 | 12.6 | 25 | 106.7 | 2.9 | 2.3 | 22.9 | 108.4 | 21.2 | 109.7 | 19.6 | 111 | 17.5 | 112.6 | 24.1 | 76.8 | 2.9 | 3 | 22 | 79 | 20.3 | 80.7 | 18.6 | 82.4 | 16.5 | 84.5 | 63.6 | 46.9 | 50.8 | 56.6 | 61.6 | 69.2 | 76.5 | 81.6 | 80 | 74.6 | 64.5 | 53.5 | 46.4 | 13.45 | 5.08 | 4.86 | 5.89 | 6.64 | 6.16 | 5.87 | 4.37 | 3.99 | 5.52 | 5.65 | 5.58 | 5.19 | 349 | 125 | 45 | 10 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 139 | 2405 | 563 | 397 | 268 | 141 | 28 | 3 | 0 | 0 | 4 | 76 | 347 | 578 | 5302 | 27 | 68 | 214 | 350 | 594 | 796 | 981 | 929 | 737 | 448 | 132 | 26 | 1881 | 0 | 0 | 6 | 39 | 157 | 348 | 516 | 464 | 291 | 59 | 1 | 0 | 27333 | 0 | 4 | 183 | 738 | 2300 | 5047 | 7495 | 6489 | 4004 | 1022 | 50 | 1 | 15150 | 0 | 0 | 36 | 265 | 1039 | 2846 | 4581 | 3870 | 2170 | 340 | 3 | 0 | 5.2 | 3.2 | 4 | 5.1 | 6.5 | 7.4 | 7.6 | 6.6 | 6.2 | 5.2 | 4 | 3.1 | 3.1 | 8.6 | 1.7 | 1.5 | 1.5 | 0.7 | 0.2 | 0.1 | 0 | 0 | 0.2 | 0.4 | 0.9 | 1.1 | 15.6 | 6.7 | 5 | 6.6 | 3 | 1.5 | 0.8 | 0.2 | 0.4 | 1.5 | 2.4 | 2.9 | 3.3 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1.4 | 1.4 | 1.3 | 0.7 | 0.4 | 0.2 | 0 | 0.1 | 0.4 | 0.6 | 0.8 | 0.9 | 67.4 | 73.9 | 84.3 | 92.6 | 98.9 | 104.1 | 106 | 104.3 | 101.4 | 93.2 | 79.3 | 66.3 | 53.2 | 58.2 | 61.5 | 64 | 69.3 | 70.8 | 70.8 | 69.8 | 68.2 | 66.2 | 60.3 | 55.4 | 63.3 | 69.4 | 79 | 87.3 | 93.9 | 100.3 | 102.6 | 101 | 98.1 | 87.9 | 74.4 | 63 | 53.7 | 56.8 | 60 | 62 | 65.4 | 69.2 | 70.4 | 68.9 | 67.6 | 64.2 | 59.1 | 53.7 | 60.1 | 65.4 | 74.7 | 82.2 | 90 | 97.3 | 100.1 | 98.9 | 95.3 | 83.6 | 70.1 | 59.5 | 52.7 | 55.1 | 58.6 | 60.3 | 63.9 | 67.5 | 70.3 | 68.8 | 66.5 | 61.9 | 57.2 | 52 | 56.7 | 62.2 | 70.7 | 77.5 | 86 | 93.7 | 97.7 | 96.4 | 92 | 80.2 | 65.8 | 56.5 | 51.5 | 53.8 | 57 | 58.7 | 62 | 66.5 | 69 | 67.7 | 65.9 | 60.9 | 55.4 | 50.9 | 58.6 | 61 | 64.2 | 67.3 | 72.5 | 74.9 | 76.7 | 74.5 | 72.8 | 68.7 | 63.4 | 59.3 | 62.2 | 68 | 77.6 | 86.5 | 91.8 | 97.7 | 98.3 | 95 | 92 | 85.9 | 73.5 | 63.2 | 55.8 | 58.5 | 62.1 | 63.9 | 68.1 | 72.3 | 74.1 | 72.3 | 70 | 66.3 | 60.7 | 56.1 | 60 | 66.2 | 75.5 | 82.5 | 89.7 | 94.8 | 96.2 | 94.8 | 92 | 82.3 | 71 | 59.7 | 54 | 56.6 | 60 | 61.6 | 65.6 | 70.3 | 72.3 | 70.6 | 68.3 | 64.1 | 58.5 | 54.1 | 57.7 | 63.8 | 72.2 | 78.9 | 85.7 | 92 | 94.1 | 93.3 | 90.9 | 79.8 | 67.8 | 57.8 | 51.9 | 54.6 | 57.9 | 59.6 | 63.4 | 68.3 | 70.7 | 69.2 | 66.8 | 62.2 | 56.5 | 51.6 | 56.1 | 60.9 | 68.6 | 75.4 | 83 | 89.5 | 92.6 | 91.9 | 89.2 | 77 | 64.3 | 55 | 18.2 | 21.7 | 24.3 | 26.3 | 28.1 | 30.6 | 31.4 | 32.4 | 32.6 | 29.4 | 24.6 | 19.8 | 24.6 | 28 | 31.3 | 34.4 | 34.4 | 34.9 | 33.7 | 34.9 | 36.6 | 35.5 | 31.2 | 24.4 | 15.7 | 16.3 | 14.5 | 13.2 | 12 | 10.9 | 10.6 | 10.7 | 12 | 14.3 | 16.5 | 15.4 | 18.5 | 23.8 | 28.1 | 31.8 | 31.5 | 31.4 | 30.5 | 32.3 | 33.5 | 30.5 | 27.2 | 16.9 | 12.6 | 14.5 | 13.9 | 13 | 11.9 | 11 | 11.1 | 11.4 | 11.9 | 12.9 | 15.3 | 11.7 | 0.361 | 0.371 | 0.371 | 0.371 | 0.371 | 0.364 | 0.384 | 0.363 | 0.367 | 0.391 | 0.38 | 0.357 | 2.313 | 2.304 | 2.32 | 2.346 | 2.367 | 2.386 | 2.358 | 2.393 | 2.392 | 2.272 | 2.252 | 2.329 | 259 | 272 | 284 | 289 | 289 | 290 | 283 | 288 | 281 | 260 | 248 | 251 | 31 | 36 | 38 | 39 | 39 | 38 | 39 | 37 | 35 | 36 | 33 | 29 | 774 | 1127 | 1609 | 2043 | 2417 | 2679 | 2562 | 2354 | 1967 | 1433 | 976 | 715 | 111 | 124 | 133 | 144 | 124 | 81 | 88 | 63 | 54 | 73 | 54 | 96 | 1.44 | N/A | N/A | 1.6 | N/A | N/A | -166 | -506 | 572 | 308 | 1.03 | N/A | -1.98 | 0.99 | N/A | N/A | -49 | -266 | 340 | 110 | 27
4 | USA | CA | POINT MUGU NAS | 723910 | 93111 | 34.117 | -119.117 | 13 | 14.69 | -8 | NAP | 94-19 | 3C | 12 | 38.9 | 41.1 | 8.4 | 8.5 | 62.7 | 14 | 11.2 | 64.9 | 28.6 | 63.2 | 26.3 | 61.2 | 4.9 | 10 | 0.434 | 8 | 14.2 | 82.7 | 61.8 | 79.4 | 63.2 | 76.7 | 63.3 | 70.1 | 76.7 | 68.5 | 75.1 | 67.2 | 73.7 | 12.5 | 60 | 67.7 | 101.7 | 73.9 | 65.8 | 95.3 | 72.8 | 64.2 | 90.1 | 70.6 | 34 | 75.6 | 32.7 | 75.1 | 31.6 | 73.9 | 78.4 | 23.2 | 19.1 | 16.5 | 34.8 | 92.2 | 3 | 4.6 | 32.6 | 95.5 | 30.9 | 98.2 | 29.2 | 100.8 | 27 | 104.1 | 31.4 | 72.1 | 3.3 | 2.7 | 29 | 74 | 27.1 | 75.6 | 25.3 | 77.2 | 22.9 | 79.2 | 60.2 | 56 | 55.1 | 56.3 | 57 | 59.2 | 62.4 | 65.5 | 66.1 | 65.7 | 63.4 | 59.6 | 55.2 | 6.06 | 6.1 | 5.25 | 4.51 | 4.14 | 3.01 | 2.81 | 3.09 | 3.49 | 4.01 | 4.72 | 5.45 | 5.3 | 30 | 8 | 8 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 9 | 2033 | 292 | 283 | 273 | 243 | 181 | 87 | 30 | 27 | 37 | 87 | 182 | 311 | 3735 | 194 | 151 | 198 | 212 | 286 | 371 | 479 | 501 | 470 | 416 | 288 | 169 | 265 | 13 | 6 | 4 | 4 | 2 | 9 | 44 | 62 | 58 | 38 | 19 | 6 | 1291 | 87 | 50 | 41 | 52 | 17 | 21 | 85 | 180 | 250 | 290 | 170 | 48 | 247 | 18 | 13 | 9 | 11 | 3 | 3 | 6 | 12 | 34 | 87 | 43 | 8 | 6.9 | 7.6 | 7.5 | 7.4 | 7.8 | 7.3 | 6.6 | 6.4 | 6.1 | 5.8 | 6.3 | 6.7 | 7.5 | 11.2 | 2.4 | 3.1 | 2.1 | 0.7 | 0.1 | 0 | 0 | 0.1 | 0.1 | 0.2 | 1.9 | 1.8 | 20.6 | 11.6 | 16.6 | 7.3 | 4.2 | 1.5 | 0.3 | 0.2 | 1.2 | 0.9 | 0.8 | 6.4 | 5.3 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1 | 2.6 | 3.8 | 2 | 1 | 0.3 | 0.1 | 0 | 0.2 | 0.2 | 0.2 | 1.6 | 1.6 | 82.1 | 81.9 | 79.8 | 81.1 | 75.3 | 76.4 | 79.7 | 81.4 | 84 | 90.4 | 85.8 | 80.3 | 55.8 | 56.6 | 57.6 | 58 | 62.4 | 65.1 | 69.4 | 69.4 | 68.4 | 58.9 | 58.9 | 53.7 | 75.5 | 72.6 | 72.4 | 73 | 70.6 | 72.6 | 76.3 | 78.1 | 80 | 81.7 | 78.7 | 72.7 | 53.8 | 54.3 | 55.8 | 58.2 | 61.6 | 64.3 | 67.9 | 68 | 68.8 | 60 | 56.3 | 52.9 | 71.3 | 68 | 67.8 | 68.3 | 68.1 | 70.6 | 73.8 | 75.7 | 76.9 | 76.5 | 74 | 68.1 | 52.9 | 55.1 | 56.7 | 58 | 60.3 | 63.2 | 66.3 | 67 | 67.4 | 61.3 | 55.9 | 52.8 | 66.8 | 64 | 64.2 | 65.1 | 66.1 | 69.2 | 72.2 | 73.5 | 74.1 | 72.5 | 70 | 64.9 | 52.6 | 54.5 | 56.7 | 57.4 | 59.4 | 62.4 | 65.4 | 65.8 | 66 | 62 | 56.6 | 53.2 | 61.4 | 61.5 | 62.4 | 62.5 | 65.4 | 67.4 | 72.3 | 70.7 | 71.8 | 70.2 | 64.8 | 62.3 | 66.8 | 69.3 | 69 | 71.1 | 71.1 | 73.2 | 75 | 78.6 | 79.8 | 76.6 | 73.8 | 66.1 | 59.6 | 59.5 | 60.3 | 60.5 | 63.1 | 65.4 | 69.6 | 69 | 70 | 67.3 | 62.5 | 60.1 | 64.5 | 65.8 | 66.6 | 68 | 67.7 | 70.8 | 74.5 | 76.2 | 77.5 | 73.5 | 69.8 | 64.2 | 58.3 | 58.1 | 59.1 | 59.3 | 61.8 | 64.1 | 67.6 | 67.8 | 68.3 | 65.2 | 61 | 58.3 | 63.4 | 63.8 | 64.5 | 65.9 | 66.3 | 68.9 | 73.3 | 74.6 | 75.5 | 71.6 | 67.7 | 62.9 | 56.9 | 56.8 | 57.8 | 58.2 | 60.2 | 63 | 65.9 | 66.4 | 66.7 | 63.7 | 59.6 | 56.7 | 62.3 | 62 | 62.7 | 64.1 | 64.9 | 67.6 | 71.5 | 72.9 | 73.3 | 69.4 | 65.9 | 61.7 | 18 | 16.8 | 15.9 | 16.2 | 14 | 13.2 | 13.1 | 14.2 | 15.2 | 17.3 | 19.2 | 18.7 | 24.1 | 23.5 | 22.9 | 22.6 | 17.3 | 15.8 | 15.1 | 16.5 | 18.9 | 25 | 25.9 | 23.5 | 12.2 | 12.9 | 12.9 | 12.8 | 10.2 | 9.3 | 8.4 | 9.2 | 10.2 | 13.1 | 13.6 | 13.4 | 17.6 | 17 | 16.2 | 18.2 | 15.4 | 14.2 | 13.9 | 15.6 | 17.3 | 18.1 | 19.7 | 17.4 | 12.6 | 11.5 | 11.3 | 11.8 | 9.7 | 8.8 | 8.3 | 8.9 | 10.1 | 12.3 | 13.8 | 12.7 | 0.309 | 0.32 | 0.334 | 0.375 | 0.394 | 0.39 | 0.418 | 0.387 | 0.381 | 0.36 | 0.314 | 0.316 | 2.579 | 2.566 | 2.518 | 2.387 | 2.355 | 2.376 | 2.352 | 2.412 | 2.429 | 2.477 | 2.59 | 2.576 | 288 | 296 | 299 | 289 | 283 | 283 | 274 | 282 | 279 | 277 | 284 | 279 | 25 | 28 | 32 | 38 | 40 | 39 | 39 | 36 | 34 | 30 | 24 | 24 | 990 | 1268 | 1694 | 2096 | 2275 | 2351 | 2321 | 2198 | 1877 | 1433 | 1110 | 899 | 73 | 128 | 108 | 120 | 167 | 126 | 115 | 85 | 80 | 113 | 68 | 71 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.13 | N/A | -3.06 | 1.26 | N/A | N/A | N/A | -230 | 419 | 173 | 48
4 | USA | CA | SANTA BARBARA | 723925 | 23190 | 34.426 | -119.843 | 9 | 14.69 | -8 | NAP | 94-19 | 3C | 12 | 35.4 | 37.3 | 21.5 | 16.1 | 55.7 | 25.4 | 19.4 | 53.9 | 20.8 | 58.5 | 18.7 | 58.3 | 0.7 | 60 | 0.418 | 8 | 15.6 | 83.5 | 63.5 | 80.1 | 63.4 | 77.2 | 63 | 68.8 | 77.3 | 67.3 | 75.4 | 66.1 | 73.8 | 8.8 | 250 | 65.6 | 94.6 | 72.7 | 64 | 89.4 | 70.7 | 63.1 | 86.5 | 69.5 | 32.9 | 77.1 | 31.7 | 75.3 | 30.8 | 73.7 | 76.3 | 18.8 | 16.1 | 12.9 | 30.9 | 92.8 | 2.4 | 4.3 | 29.1 | 96 | 27.7 | 98.5 | 26.4 | 100.9 | 24.6 | 104.1 | 28.5 | 70.5 | 2.4 | 1.9 | 26.8 | 71.9 | 25.4 | 73 | 24 | 74.1 | 22.2 | 75.5 | 59.6 | 53.3 | 54 | 56.2 | 58 | 60.4 | 62.7 | 65.8 | 66.3 | 65.7 | 62.4 | 57.3 | 52.8 | 6.23 | 4.29 | 4.27 | 4.15 | 4.42 | 3.97 | 3.06 | 3.13 | 3.14 | 4.03 | 4.4 | 4.4 | 4.14 | 51 | 16 | 10 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 18 | 2205 | 363 | 308 | 274 | 217 | 156 | 82 | 27 | 20 | 37 | 107 | 235 | 379 | 3555 | 118 | 123 | 195 | 241 | 322 | 381 | 488 | 505 | 472 | 384 | 221 | 105 | 231 | 0 | 0 | 2 | 7 | 12 | 13 | 50 | 60 | 58 | 26 | 3 | 0 | 1509 | 22 | 29 | 46 | 89 | 112 | 68 | 144 | 233 | 339 | 324 | 97 | 6 | 320 | 1 | 2 | 6 | 22 | 33 | 13 | 20 | 30 | 73 | 98 | 22 | 0 | 5.2 | 4.1 | 5.2 | 5.7 | 6.5 | 6.3 | 5.8 | 5.7 | 5.3 | 5 | 4.5 | 4.1 | 4.1 | 16 | 3.2 | 3.7 | 3.1 | 0.9 | 0.2 | 0 | 0 | 0.1 | 0.1 | 0.5 | 2 | 2.2 | 35.1 | 12.2 | 13.6 | 11.5 | 5.7 | 1.8 | 0.5 | 0.4 | 1.9 | 1.3 | 2.4 | 6.9 | 5.8 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7 | 3.1 | 3.3 | 2.8 | 1.4 | 0.4 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 2 | 1.9 | 77 | 78.5 | 79.6 | 82.7 | 84.6 | 81.5 | 82.2 | 83.8 | 86.6 | 89.3 | 82.8 | 74.5 | 54.7 | 57.1 | 59.2 | 59.9 | 60.6 | 63.6 | 67 | 68.3 | 65.3 | 61.6 | 58.6 | 55.5 | 71.7 | 71.9 | 73.1 | 75.4 | 76.2 | 75 | 77.4 | 79.3 | 81.4 | 81.9 | 76.1 | 70 | 54.2 | 55.9 | 57 | 57.5 | 60.1 | 62.9 | 66.2 | 67 | 66.8 | 61 | 57.5 | 54.6 | 67.4 | 66.8 | 69.1 | 71.2 | 71.9 | 72.3 | 74.9 | 76.3 | 77.6 | 76.9 | 71.7 | 66.3 | 54.2 | 54.5 | 55.9 | 57.1 | 59.4 | 62.1 | 65.4 | 66 | 65.5 | 60.8 | 57.3 | 54.4 | 63.8 | 63.3 | 65.4 | 67.4 | 68.4 | 70 | 72.7 | 73.7 | 74.6 | 72.9 | 68 | 63.4 | 54.8 | 53.9 | 55.2 | 56.3 | 58.7 | 61.6 | 64.5 | 65 | 64.8 | 61 | 57 | 53.8 | 62.7 | 61 | 62.2 | 63.3 | 65.3 | 66.3 | 69.7 | 69.9 | 71 | 69.3 | 63.6 | 61.5 | 65.8 | 68.6 | 72.5 | 75 | 75.6 | 75.7 | 77.4 | 80 | 79.3 | 77.5 | 72.5 | 66.5 | 59.3 | 59 | 59.9 | 60.5 | 62.8 | 64.6 | 67.5 | 68.1 | 69 | 66 | 61.7 | 59.3 | 63.6 | 64.8 | 67.2 | 69.7 | 71.3 | 72.3 | 74.9 | 77.1 | 77.1 | 74.1 | 68.6 | 64.1 | 57.7 | 57.5 | 58.5 | 59.2 | 61.3 | 63.5 | 66.2 | 66.7 | 67.2 | 64.1 | 60.3 | 57.5 | 62.2 | 62.8 | 64.8 | 67.1 | 68.7 | 70.3 | 73.5 | 74.8 | 74.8 | 71.3 | 66.9 | 62.1 | 56.3 | 56.2 | 57.3 | 57.8 | 59.9 | 62.3 | 64.9 | 65.6 | 65.8 | 62.5 | 59 | 55.8 | 61.2 | 61.4 | 63 | 65 | 66.3 | 68.5 | 71.9 | 72.9 | 72.9 | 69.3 | 65.5 | 61.1 | 21.5 | 19.5 | 18 | 18.3 | 16.4 | 14.8 | 14.7 | 15.6 | 17.5 | 20.7 | 22.4 | 22 | 29.3 | 27.5 | 25.8 | 25.8 | 23 | 19.9 | 18 | 19.9 | 23.4 | 29.4 | 29.3 | 28.1 | 16.4 | 14.9 | 13.4 | 12.8 | 11.3 | 10.3 | 8.8 | 9.6 | 11.3 | 14.6 | 15.8 | 16.8 | 19.7 | 19.5 | 19.4 | 20.9 | 18.5 | 17 | 16.4 | 18.1 | 19.7 | 21.6 | 22.2 | 20.8 | 13.8 | 12 | 11.7 | 11.7 | 10.1 | 9.2 | 8.1 | 8.9 | 9.9 | 12.4 | 14 | 14.5 | 0.304 | 0.318 | 0.326 | 0.364 | 0.379 | 0.365 | 0.395 | 0.374 | 0.363 | 0.351 | 0.309 | 0.311 | 2.592 | 2.566 | 2.543 | 2.421 | 2.396 | 2.438 | 2.409 | 2.435 | 2.474 | 2.5 | 2.599 | 2.585 | 290 | 297 | 302 | 292 | 287 | 290 | 280 | 286 | 285 | 280 | 286 | 280 | 24 | 28 | 31 | 36 | 38 | 36 | 37 | 36 | 33 | 30 | 24 | 23 | 974 | 1248 | 1685 | 2102 | 2320 | 2411 | 2332 | 2184 | 1869 | 1433 | 1099 | 882 | 74 | 131 | 109 | 119 | 152 | 111 | 92 | 82 | 75 | 105 | 60 | 71 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | N/A | -2.92 | 1.22 | N/A | N/A | N/A | -229 | 396 | 149 | 37
4 | USA | CA | CAMARILLO | 723926 | 23136 | 34.217 | -119.083 | 77 | 14.66 | -8 | NAP | 94-19 | 3C | 12 | 37.7 | 40 | 5.6 | 7.3 | 65.5 | 11.3 | 9.8 | 64.1 | 33.6 | 63 | 30.2 | 64.5 | 2.7 | 70 | 0.409 | 8 | 16.7 | 87.8 | 63 | 83.7 | 62.9 | 80.9 | 63.4 | 69.6 | 80.1 | 68.4 | 78.5 | 67.2 | 76.9 | 12.9 | 70 | 65.8 | 95.4 | 75.5 | 64.2 | 90 | 73 | 63.3 | 87.2 | 71.6 | 33.7 | 80.4 | 32.6 | 78.7 | 31.7 | 76.9 | 76.1 | 24.9 | 20 | 16.3 | 33.7 | 97.9 | 2 | 4.1 | 32.3 | 100.9 | 31.1 | 103.3 | 30 | 105.6 | 28.5 | 108.6 | 29.5 | 71.9 | 2.2 | 1.8 | 27.9 | 73.2 | 26.6 | 74.2 | 25.4 | 75.2 | 23.8 | 76.5 | 61.7 | 56 | 55.6 | 57.5 | 59 | 61.7 | 64.9 | 68.3 | 68.8 | 68.1 | 64.8 | 59.9 | 55.3 | 6.81 | 6.05 | 5.36 | 4.64 | 4.62 | 3.79 | 3.09 | 3.41 | 3.34 | 4.28 | 5.36 | 5.78 | 5.25 | 28 | 8 | 7 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 9 | 1717 | 290 | 270 | 240 | 191 | 119 | 37 | 7 | 5 | 12 | 66 | 175 | 305 | 4294 | 195 | 163 | 234 | 270 | 361 | 447 | 568 | 582 | 543 | 459 | 299 | 173 | 508 | 12 | 6 | 6 | 10 | 15 | 34 | 109 | 122 | 105 | 61 | 23 | 5 | 3498 | 120 | 106 | 128 | 186 | 157 | 139 | 449 | 580 | 642 | 631 | 297 | 63 | 889 | 21 | 28 | 37 | 57 | 52 | 22 | 56 | 95 | 172 | 247 | 94 | 8 | 5.8 | 6.9 | 6.6 | 6.1 | 6.3 | 5.8 | 5.3 | 5.1 | 4.8 | 4.7 | 5.5 | 6 | 6.9 | 15 | 3.5 | 3.9 | 2.4 | 0.7 | 0.4 | 0.1 | 0 | 0 | 0.1 | 0.5 | 1.1 | 2.2 | 30 | 16.6 | 17.7 | 8.2 | 3.5 | 2 | 0.8 | 0.4 | 0.1 | 0.7 | 3.6 | 3.8 | 9.5 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9 | 3.5 | 3.7 | 2.1 | 0.8 | 0.5 | 0.2 | 0.1 | 0 | 0.1 | 0.8 | 0.9 | 2.2 | 82.8 | 84.4 | 84.9 | 87.8 | 86.1 | 83.4 | 85 | 87.3 | 90.5 | 94.7 | 89.6 | 80.9 | 54.8 | 56.5 | 57.6 | 59.8 | 60.5 | 67 | 69.2 | 69.1 | 67.4 | 61.3 | 59.8 | 54.7 | 77.2 | 76.5 | 77 | 79.2 | 77.4 | 77.6 | 81.1 | 82.2 | 84.3 | 86.6 | 81.8 | 74.6 | 52.9 | 54.5 | 55.8 | 57.9 | 61.6 | 64.7 | 67.7 | 68 | 67.2 | 60 | 57.1 | 52.9 | 72.6 | 70.6 | 71.6 | 73.3 | 73 | 74.7 | 78.8 | 79.5 | 80.8 | 80.5 | 76.4 | 69.9 | 52.6 | 53.4 | 55.7 | 57.2 | 60.7 | 63.8 | 67 | 67.2 | 66.4 | 60.4 | 55.6 | 52.2 | 67.7 | 65.6 | 67.4 | 69.3 | 70.1 | 72.4 | 76.2 | 77 | 77.1 | 75.5 | 71.4 | 65.9 | 51.4 | 53.3 | 55.9 | 56.7 | 59.9 | 62.7 | 66.1 | 66.1 | 65.3 | 60.2 | 55.5 | 51.9 | 60.5 | 60.6 | 62.1 | 62.7 | 66.1 | 68.2 | 71.5 | 70.9 | 71.4 | 68.8 | 64.2 | 61.4 | 68.6 | 69.8 | 74.2 | 77.1 | 78.4 | 80 | 80.7 | 83.2 | 83.2 | 79.6 | 76.2 | 68 | 58.7 | 58.8 | 59.9 | 60.5 | 63.7 | 66.1 | 69.3 | 69.2 | 69.3 | 66.3 | 62 | 59.2 | 65.2 | 67 | 69.7 | 72 | 73.9 | 75.9 | 78.3 | 80.1 | 79.9 | 76.6 | 72 | 65.1 | 57.2 | 57.3 | 58.5 | 59.2 | 62 | 64.7 | 68 | 68 | 67.7 | 64.5 | 60.3 | 57.4 | 63.4 | 65 | 67 | 69.6 | 70.9 | 73.3 | 77 | 77.9 | 77.9 | 73.8 | 69.1 | 63.1 | 55.7 | 55.9 | 57.2 | 57.8 | 60.4 | 63.3 | 66.5 | 66.7 | 66.3 | 62.9 | 58.9 | 55.5 | 62.9 | 62.8 | 64.6 | 66.8 | 68.3 | 71.2 | 75.2 | 75.9 | 75.6 | 71.6 | 67 | 61.6 | 20.3 | 19.7 | 19.3 | 19.5 | 16.7 | 15.1 | 15.6 | 16.7 | 17.8 | 20.1 | 21.8 | 21 | 27.3 | 28.4 | 28.6 | 28.5 | 23.1 | 19 | 18.4 | 20.3 | 23.2 | 29.9 | 30 | 26.7 | 12.8 | 14 | 14.4 | 13.6 | 11.7 | 9.8 | 8.6 | 9.9 | 11 | 13.7 | 14.4 | 14 | 18.8 | 20.5 | 20.4 | 21.4 | 18.7 | 16.9 | 16.6 | 18.1 | 19.4 | 21.1 | 22.2 | 19.3 | 12 | 12.1 | 12.1 | 11.5 | 10.1 | 9.1 | 8.3 | 9.5 | 9.7 | 12 | 13.9 | 13 | 0.311 | 0.323 | 0.337 | 0.38 | 0.4 | 0.396 | 0.425 | 0.392 | 0.386 | 0.365 | 0.317 | 0.319 | 2.562 | 2.547 | 2.496 | 2.362 | 2.328 | 2.353 | 2.324 | 2.392 | 2.405 | 2.447 | 2.573 | 2.557 | 287 | 295 | 298 | 288 | 281 | 281 | 272 | 280 | 278 | 275 | 283 | 277 | 25 | 29 | 32 | 39 | 41 | 40 | 41 | 37 | 35 | 31 | 25 | 24 | 986 | 1264 | 1696 | 2101 | 2300 | 2404 | 2367 | 2237 | 1902 | 1446 | 1112 | 898 | 74 | 132 | 108 | 118 | 159 | 124 | 110 | 77 | 71 | 107 | 64 | 70 | 1.62 | 1.3 | -4.32 | 2.47 | N/A | N/A | N/A | -454 | 693 | 319 | 1.13 | N/A | -3.06 | 1.26 | N/A | N/A | N/A | -230 | 419 | 173 | 47
4 | USA | CA | OXNARD | 723927 | 93110 | 34.201 | -119.207 | 36 | 14.68 | -8 | NAP | 98-19 | 3C | 12 | 40.8 | 42.9 | 7.9 | 8.3 | 63.5 | 13.6 | 11 | 61.5 | 28.4 | 61.4 | 25.9 | 62.4 | 5.8 | 50 | 0.437 | 7 | 10.7 | 82.4 | 60.1 | 78.8 | 60.6 | 75.5 | 61.9 | 68.8 | 75.4 | 67.3 | 73.6 | 66.1 | 72.1 | 12.4 | 70 | 66.1 | 96.4 | 72.9 | 64.4 | 90.6 | 70.6 | 63.4 | 87.5 | 68.9 | 33 | 75.2 | 31.7 | 73.7 | 30.7 | 72.1 | 74.7 | 23.9 | 19.3 | 16.7 | 36.6 | 93.1 | 2.2 | 5.5 | 35 | 97.1 | 33.7 | 100.4 | 32.5 | 103.5 | 30.9 | 107.5 | 31.7 | 69.7 | 2.1 | 1.9 | 30.2 | 71.1 | 29 | 72.2 | 27.8 | 73.3 | 26.3 | 74.7 | 60.6 | 56.3 | 55.5 | 56.8 | 57.8 | 60.3 | 63.1 | 66.2 | 66.1 | 65.8 | 63.5 | 59.4 | 55.6 | 5.82 | 5.68 | 4.99 | 4.36 | 4.03 | 3.07 | 2.29 | 2.99 | 2.76 | 3.92 | 4.8 | 5.03 | 4.82 | 20 | 6 | 5 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 1885 | 278 | 270 | 260 | 220 | 152 | 65 | 20 | 19 | 33 | 88 | 184 | 296 | 3876 | 201 | 159 | 212 | 236 | 318 | 394 | 503 | 500 | 473 | 418 | 283 | 179 | 268 | 9 | 5 | 5 | 5 | 6 | 9 | 58 | 54 | 56 | 41 | 17 | 3 | 1096 | 81 | 54 | 53 | 54 | 53 | 12 | 68 | 69 | 184 | 305 | 133 | 30 | 265 | 13 | 13 | 12 | 17 | 20 | 2 | 4 | 4 | 39 | 103 | 34 | 4 | 6.8 | 7 | 7.2 | 7.2 | 7.6 | 7.1 | 6.5 | 6.7 | 6.5 | 6.1 | 6.1 | 6.5 | 7.1 | 15 | 3.5 | 3.9 | 2.4 | 0.7 | 0.4 | 0.1 | 0 | 0 | 0.1 | 0.5 | 1.1 | 2.2 | 30 | 16.6 | 17.7 | 8.2 | 3.5 | 2 | 0.8 | 0.4 | 0.1 | 0.7 | 3.6 | 3.8 | 9.5 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9 | 3.5 | 3.7 | 2.1 | 0.8 | 0.5 | 0.2 | 0.1 | 0 | 0.1 | 0.8 | 0.9 | 2.2 | 81.8 | 81.7 | 80.6 | 80.6 | 80.6 | 74.9 | 79.2 | 79.8 | 84.4 | 90.6 | 84.8 | 78.4 | 54.9 | 55.8 | 56.6 | 57.9 | 57.9 | 64.4 | 68.3 | 68.1 | 66.7 | 59.5 | 57.7 | 53.2 | 75.3 | 72.8 | 72.7 | 72.6 | 71.3 | 71.7 | 75.5 | 75.5 | 78.7 | 81.5 | 77.5 | 71.7 | 52.4 | 53 | 54.9 | 56.8 | 60.1 | 63.1 | 66.9 | 66.6 | 66.8 | 59.7 | 55.8 | 52.6 | 70.3 | 67.6 | 67.2 | 67.9 | 67.8 | 69.9 | 73.4 | 73.4 | 75 | 76.1 | 72.4 | 67 | 52.3 | 53.6 | 55.4 | 56.3 | 59 | 62.1 | 65.6 | 65.4 | 65.7 | 60.5 | 55 | 52.4 | 65.8 | 63.5 | 64 | 64.8 | 66 | 68.2 | 72 | 72.1 | 72.7 | 72 | 68.2 | 63.9 | 51.8 | 53.2 | 55.5 | 56.3 | 58.4 | 61.1 | 64.7 | 64.7 | 64.8 | 60.7 | 55.8 | 52.1 | 60 | 60.2 | 60.7 | 61.2 | 63.2 | 65.9 | 70 | 69.4 | 70.8 | 69.3 | 63.1 | 61.3 | 65.8 | 66.2 | 68.7 | 70.7 | 69.5 | 73 | 76.4 | 76.7 | 78 | 76.6 | 71.4 | 66.4 | 58.5 | 58.4 | 59.2 | 59.4 | 61.7 | 64.1 | 68.2 | 67.6 | 68.8 | 66.1 | 61.4 | 59 | 64.1 | 64.3 | 65.8 | 67.2 | 67.3 | 69.8 | 74.3 | 74.1 | 75.2 | 73 | 68.1 | 63.6 | 57.3 | 57.2 | 58 | 58.3 | 60.4 | 63 | 66.5 | 66.4 | 67 | 64.2 | 60.1 | 57.3 | 63.2 | 63 | 64.1 | 65.3 | 65.9 | 68 | 72.2 | 72.4 | 73.3 | 70.6 | 66.5 | 61.8 | 55.8 | 55.8 | 56.9 | 57.2 | 59.3 | 62 | 65.5 | 65.3 | 65.6 | 62.7 | 58.8 | 55.7 | 61.6 | 61.4 | 62.5 | 63.5 | 64.8 | 66.9 | 70.8 | 70.9 | 71.7 | 68.7 | 65 | 60.7 | 17.2 | 15.9 | 14.8 | 14.4 | 12.2 | 10.5 | 10.7 | 11.3 | 12.8 | 15.5 | 17.3 | 16.9 | 24.1 | 23 | 21.8 | 20.8 | 15.8 | 12.6 | 12.4 | 13.1 | 16.1 | 24.1 | 24.2 | 21.5 | 11.8 | 12.1 | 11.7 | 11 | 8.4 | 6.8 | 6 | 6.7 | 9 | 12.8 | 13.4 | 12.6 | 16.1 | 16.3 | 15.7 | 15.9 | 13.2 | 11.4 | 11.6 | 12.6 | 13.7 | 16.8 | 17.6 | 15.6 | 11 | 10.9 | 9.7 | 9.2 | 7.4 | 6.3 | 5.7 | 6.7 | 7.7 | 11.2 | 12.5 | 11.8 | 0.308 | 0.319 | 0.331 | 0.376 | 0.397 | 0.39 | 0.42 | 0.388 | 0.382 | 0.359 | 0.313 | 0.315 | 2.578 | 2.566 | 2.522 | 2.381 | 2.343 | 2.374 | 2.342 | 2.405 | 2.422 | 2.472 | 2.588 | 2.573 | 289 | 297 | 300 | 289 | 282 | 283 | 274 | 282 | 279 | 277 | 284 | 279 | 25 | 28 | 31 | 38 | 40 | 39 | 40 | 37 | 35 | 30 | 24 | 24 | 986 | 1264 | 1694 | 2101 | 2295 | 2385 | 2348 | 2218 | 1891 | 1441 | 1111 | 897 | 73 | 130 | 109 | 120 | 163 | 121 | 110 | 81 | 75 | 110 | 65 | 70 | 1.46 | N/A | -4.79 | 3.26 | 1.44 | N/A | N/A | -414 | 569 | 169 | 1.15 | N/A | -3.13 | 1.21 | N/A | N/A | N/A | -230 | 421 | 171 | 45
4 | USA | CA | VANDENBERG AFB | 723930 | 93214 | 34.717 | -120.567 | 369 | 14.5 | -8 | NAP | 95-19 | 3C | 12 | 35.7 | 37.2 | 20.7 | 15.7 | 51.8 | 24.7 | 19 | 51 | 27.7 | 56 | 25.7 | 55.8 | 6.9 | 110 | 0.55 | 9 | 16.1 | 80.6 | 60.3 | 75.7 | 59.2 | 72.5 | 59 | 65 | 72.9 | 63.4 | 70.2 | 62.2 | 68.5 | 8.3 | 270 | 62.5 | 85.7 | 66.5 | 60.9 | 81 | 65.2 | 59.5 | 76.9 | 64.1 | 30.1 | 72.4 | 28.9 | 70.4 | 28 | 68.5 | 77.9 | 26.3 | 23.5 | 20.1 | 30.2 | 91.6 | 3.6 | 5.7 | 27.6 | 95.7 | 25.5 | 99.1 | 23.5 | 102.3 | 20.9 | 106.5 | 27.5 | 68.5 | 3.3 | 3.3 | 25.1 | 70.8 | 23.2 | 72.8 | 21.3 | 74.6 | 18.9 | 77 | 56.2 | 52.2 | 52.5 | 53.3 | 54.1 | 55.6 | 57.1 | 59.8 | 60.5 | 61.1 | 59.8 | 56.2 | 52 | 5.36 | 5.01 | 5.19 | 4.13 | 4.27 | 3.5 | 3.1 | 2.78 | 2.82 | 4.08 | 5.04 | 5.13 | 4.72 | 117 | 33 | 27 | 12 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32 | 3265 | 397 | 351 | 362 | 331 | 295 | 240 | 165 | 142 | 132 | 178 | 269 | 403 | 2385 | 102 | 98 | 116 | 130 | 173 | 213 | 303 | 327 | 333 | 304 | 192 | 94 | 56 | 0 | 1 | 1 | 2 | 2 | 3 | 3 | 4 | 16 | 18 | 6 | 0 | 607 | 10 | 25 | 19 | 37 | 43 | 38 | 10 | 26 | 123 | 200 | 71 | 5 | 172 | 0 | 4 | 3 | 10 | 16 | 19 | 2 | 5 | 36 | 62 | 15 | 0 | 8.8 | 8.9 | 9.5 | 9.6 | 10.8 | 10.5 | 9.2 | 7.5 | 7.2 | 7.2 | 7.9 | 8.2 | 9 | 16.6 | 3.6 | 3.7 | 2.7 | 1.1 | 0.4 | 0.1 | 0 | 0 | 0.1 | 0.8 | 1.3 | 2.8 | 32.6 | 16.3 | 15.7 | 12.6 | 4.3 | 2.4 | 0.7 | 0.3 | 0.1 | 0.4 | 4 | 4.5 | 9.3 | 6.2 | 0.2 | 0.1 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 6.6 | 3.5 | 3.3 | 2.8 | 1.1 | 0.6 | 0.2 | 0.1 | 0 | 0.1 | 0.9 | 1.1 | 2.2 | 75.3 | 78 | 76.5 | 79 | 79.3 | 77.3 | 74.3 | 77 | 85.1 | 87.3 | 81.4 | 73.2 | 54.4 | 57.8 | 57.9 | 58.9 | 58.5 | 61.6 | 63.6 | 64.6 | 63.8 | 61 | 58.6 | 53.4 | 69.9 | 71.1 | 69.6 | 70.3 | 69.8 | 69.3 | 70.8 | 71.8 | 77.2 | 79.4 | 74.6 | 67.9 | 53.2 | 54.7 | 54.9 | 55.7 | 58.9 | 59.8 | 62.4 | 62.5 | 63 | 59.5 | 56.6 | 53.3 | 64.9 | 65.2 | 64.7 | 64.8 | 65 | 65.8 | 68.1 | 69.2 | 72.5 | 73.5 | 69.4 | 63.7 | 53.1 | 54.2 | 54.5 | 55.7 | 57.1 | 58.7 | 61.1 | 61.6 | 62.1 | 58.5 | 55.8 | 53.1 | 61 | 61.3 | 61.5 | 61.9 | 62.6 | 63.5 | 65.9 | 66.7 | 69.4 | 69.4 | 65.4 | 60.9 | 53.1 | 53.2 | 54.1 | 54.5 | 55.9 | 57.3 | 59.9 | 60.5 | 61.3 | 58.8 | 55.5 | 53.5 | 60.1 | 60.4 | 60.2 | 60.9 | 62.3 | 63.2 | 65.5 | 65.8 | 68.2 | 66.8 | 62.1 | 60.7 | 63.6 | 67.2 | 68.6 | 70.8 | 71.2 | 75.3 | 71.7 | 74.1 | 77.9 | 75.5 | 71 | 64.2 | 57.6 | 58.3 | 58.3 | 58.4 | 60 | 60.6 | 63.1 | 63.4 | 65.3 | 63.8 | 60.1 | 58.8 | 61.2 | 64.4 | 64.9 | 66.2 | 67 | 67.3 | 69.4 | 69.6 | 72.9 | 70.2 | 67.4 | 61.8 | 56.3 | 56.5 | 56.6 | 56.7 | 58 | 59.2 | 61.5 | 62.1 | 63.4 | 62 | 58.6 | 56.8 | 60.2 | 62.4 | 62.3 | 63.4 | 64.2 | 64.7 | 66.7 | 67.7 | 70 | 68.5 | 65.1 | 59.8 | 54.7 | 54.9 | 55 | 55.2 | 56.3 | 57.9 | 60.2 | 60.9 | 61.9 | 60.2 | 57.2 | 54.8 | 58.9 | 60.4 | 60 | 60.8 | 61.7 | 62.6 | 64.9 | 65.9 | 67.9 | 66.7 | 63.2 | 58.5 | 18.7 | 18 | 17.3 | 16.6 | 14.6 | 13.4 | 12.6 | 13.4 | 16.1 | 19.2 | 19.6 | 18.5 | 25 | 25.5 | 24.2 | 23.2 | 20.7 | 18.6 | 16.2 | 16.7 | 22.5 | 27.3 | 26.3 | 23.2 | 13.7 | 13.7 | 13.1 | 12.7 | 11.8 | 10.7 | 8.6 | 8.8 | 11.6 | 14 | 14 | 14 | 17.1 | 19.1 | 18.9 | 19.7 | 18.9 | 16.3 | 15.2 | 15.8 | 19.2 | 20.9 | 20.3 | 15 | 11.4 | 11.7 | 11.7 | 11.7 | 11.1 | 9.6 | 8.3 | 8.5 | 10.6 | 11.9 | 12.4 | 11 | 0.302 | 0.316 | 0.323 | 0.339 | 0.349 | 0.349 | 0.357 | 0.342 | 0.343 | 0.335 | 0.304 | 0.306 | 2.603 | 2.571 | 2.552 | 2.493 | 2.486 | 2.479 | 2.513 | 2.528 | 2.528 | 2.553 | 2.611 | 2.603 | 290 | 297 | 302 | 300 | 296 | 295 | 292 | 296 | 292 | 286 | 287 | 282 | 24 | 28 | 30 | 34 | 35 | 35 | 34 | 32 | 31 | 28 | 23 | 23 | 955 | 1227 | 1668 | 2076 | 2294 | 2354 | 2215 | 2051 | 1789 | 1389 | 1066 | 851 | 73 | 123 | 107 | 128 | 152 | 111 | 84 | 97 | 98 | 105 | 60 | 75 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.17 | N/A | -2.45 | 1.44 | N/A | N/A | N/A | -301 | 432 | 137 | 26
4 | USA | CA | SANTA MARIA | 723940 | 23273 | 34.899 | -120.449 | 242 | 14.57 | -8 | NAP | 94-19 | 3C | 12 | 33.6 | 35.9 | 21.2 | 16 | 55.6 | 25 | 19.3 | 50.7 | 23.7 | 58.6 | 20.5 | 58.1 | 2.9 | 120 | 0.504 | 9 | 20.3 | 85.1 | 62.3 | 80.9 | 61.8 | 77.4 | 61.3 | 66.5 | 78.4 | 65 | 76.2 | 63.8 | 74.2 | 9.8 | 310 | 62.2 | 84.4 | 69.8 | 60.5 | 79.4 | 68.5 | 59.3 | 76.1 | 67.3 | 31.2 | 78.5 | 30 | 76 | 29.1 | 74.2 | 74.8 | 24.4 | 20.6 | 18.3 | 28.9 | 95 | 2.5 | 4.6 | 27.1 | 98.2 | 25.7 | 100.9 | 24.3 | 103.5 | 22.5 | 106.8 | 26.8 | 69.4 | 2.5 | 2.4 | 25 | 71.1 | 23.6 | 72.5 | 22.2 | 73.9 | 20.4 | 75.7 | 58.4 | 52.9 | 53.4 | 55.4 | 56.3 | 58.7 | 61 | 63.5 | 63.9 | 64.2 | 61.9 | 57 | 52.4 | 6.2 | 4.99 | 5.31 | 4.86 | 4.9 | 3.9 | 3.4 | 3.15 | 3.08 | 4.26 | 5.23 | 5.43 | 4.85 | 102 | 27 | 22 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 31 | 2554 | 374 | 327 | 301 | 265 | 203 | 127 | 67 | 58 | 65 | 127 | 248 | 392 | 3170 | 118 | 116 | 175 | 196 | 268 | 330 | 420 | 432 | 425 | 370 | 216 | 104 | 148 | 0 | 1 | 2 | 5 | 7 | 8 | 22 | 24 | 40 | 32 | 7 | 0 | 1700 | 30 | 50 | 67 | 112 | 122 | 109 | 135 | 146 | 351 | 427 | 135 | 16 | 482 | 2 | 9 | 13 | 36 | 41 | 33 | 18 | 30 | 114 | 154 | 32 | 0 | 6.6 | 5.8 | 6.6 | 7.3 | 8.1 | 8.4 | 7.6 | 6.4 | 6 | 5.8 | 5.9 | 5.6 | 5.7 | 12.6 | 2.4 | 2.8 | 2.3 | 0.9 | 0.2 | 0 | 0 | 0 | 0.2 | 0.6 | 1.3 | 1.9 | 26.8 | 11.8 | 11.6 | 9.4 | 3.9 | 2.4 | 0.9 | 0.4 | 0.9 | 1.6 | 2.4 | 4.7 | 9.8 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4 | 2.3 | 2.7 | 2 | 1.1 | 0.4 | 0.1 | 0.1 | 0.1 | 0.3 | 0.6 | 1.2 | 1.7 | 78.2 | 80.7 | 81 | 84.8 | 85.3 | 83.3 | 82.3 | 83.5 | 90.4 | 91.6 | 84.4 | 76.2 | 55.1 | 59.1 | 60.1 | 60.6 | 61.2 | 65.3 | 66.4 | 65.7 | 64.8 | 63.2 | 60.4 | 54.3 | 72.2 | 73.5 | 74.4 | 76.1 | 76.1 | 76.2 | 77.5 | 77.4 | 82.6 | 84.2 | 77.7 | 70.8 | 55 | 56.9 | 57.7 | 58.7 | 60.6 | 62.5 | 64.7 | 64.8 | 63.9 | 60.1 | 57.4 | 54.3 | 67.9 | 67.9 | 69.8 | 70.7 | 70.9 | 72.3 | 74.3 | 74.4 | 77.3 | 78.3 | 72.6 | 66.2 | 54 | 55.3 | 56.6 | 57.9 | 59 | 61.2 | 63.5 | 63.5 | 63.5 | 59.5 | 56.4 | 53.6 | 63.2 | 63.4 | 65.5 | 66.6 | 67.5 | 69.7 | 71.6 | 72.1 | 73.4 | 73.1 | 68 | 62.6 | 53.8 | 53.9 | 55.8 | 56.3 | 57.8 | 59.8 | 62 | 62.4 | 62.4 | 59.2 | 55.9 | 53.2 | 61.3 | 62.1 | 63 | 63.8 | 65 | 65.5 | 68.2 | 67.8 | 69.8 | 67.4 | 63 | 61.2 | 67.4 | 72.5 | 75 | 78.3 | 78.4 | 79.7 | 79 | 80 | 82.1 | 81.5 | 75 | 67.1 | 58.8 | 59.3 | 60.3 | 60.7 | 61.9 | 63.4 | 65.5 | 65.4 | 66.4 | 64.3 | 60.8 | 58.8 | 64.9 | 67.8 | 70 | 72.1 | 73.6 | 74.7 | 76.5 | 76.1 | 77.6 | 75.9 | 70.3 | 63.5 | 57 | 57.4 | 58.5 | 58.9 | 59.7 | 61.8 | 63.9 | 64 | 64.3 | 62.3 | 59.2 | 56.9 | 62.6 | 65 | 66.9 | 69.1 | 69.4 | 71.8 | 73.6 | 73.9 | 74.9 | 73.1 | 67.7 | 61.5 | 55.2 | 55.4 | 56.8 | 57 | 58.2 | 60.1 | 62.3 | 62.5 | 62.7 | 60.4 | 57.6 | 55 | 61.2 | 61.8 | 64.1 | 65.3 | 66.6 | 68.7 | 71 | 71.4 | 72.2 | 70.2 | 65.9 | 60.3 | 22.1 | 21 | 21.2 | 21.6 | 19.5 | 18.7 | 17.7 | 17.9 | 20.3 | 23.1 | 23.6 | 22.4 | 29.6 | 29.2 | 28.8 | 29.2 | 26.2 | 23.3 | 21.3 | 21 | 27 | 32.7 | 30.9 | 28.4 | 16.3 | 16.1 | 15.5 | 15.2 | 13.3 | 11.5 | 10.3 | 10 | 12.6 | 15.2 | 15.3 | 16 | 20.9 | 22.9 | 23.1 | 24.9 | 22.6 | 21.7 | 20.1 | 20 | 23.2 | 25.6 | 24 | 19.1 | 13.3 | 13.7 | 13.7 | 14 | 11.8 | 10.9 | 10 | 9.7 | 11.4 | 13.1 | 13.3 | 12.6 | 0.304 | 0.32 | 0.324 | 0.341 | 0.352 | 0.352 | 0.361 | 0.347 | 0.347 | 0.342 | 0.304 | 0.308 | 2.583 | 2.543 | 2.537 | 2.476 | 2.465 | 2.461 | 2.49 | 2.497 | 2.503 | 2.517 | 2.599 | 2.583 | 289 | 295 | 302 | 299 | 295 | 294 | 290 | 294 | 290 | 283 | 286 | 280 | 24 | 28 | 31 | 35 | 35 | 36 | 34 | 33 | 32 | 29 | 24 | 23 | 945 | 1219 | 1669 | 2087 | 2343 | 2447 | 2326 | 2151 | 1846 | 1411 | 1065 | 844 | 75 | 126 | 112 | 131 | 140 | 102 | 77 | 79 | 82 | 96 | 58 | 75 | 1.13 | N/A | N/A | 1.85 | N/A | N/A | N/A | -385 | 425 | 63 | 1.17 | N/A | -2.3 | 1.35 | N/A | N/A | N/A | -301 | 432 | 137 | 27
4 | USA | CA | PASO ROBLES | 723965 | 93209 | 35.67 | -120.628 | 810 | 14.27 | -8 | NAP | 94-19 | 3B | 12 | 27.1 | 29.6 | 16.2 | 12.8 | 49.3 | 20 | 15.5 | 47.8 | 21.2 | 54.4 | 19.1 | 53.4 | 1.7 | 80 | 0.523 | 7 | 37.3 | 102.3 | 66.6 | 99 | 65.8 | 95.4 | 64.6 | 69.3 | 95.5 | 67.7 | 93.6 | 66.1 | 91.3 | 8.8 | 210 | 60 | 79.5 | 72.7 | 57.9 | 73.8 | 71.2 | 56.5 | 70.1 | 69.9 | 33.8 | 95.7 | 32.2 | 93.7 | 31.1 | 91.3 | 81 | 20.7 | 18.9 | 17.4 | 22.5 | 108.8 | 3.6 | 2.8 | 19.9 | 110.8 | 17.8 | 112.5 | 15.8 | 114 | 13.3 | 116.1 | 21 | 73.2 | 3.6 | 3.3 | 18.4 | 75.6 | 16.3 | 77.5 | 14.3 | 79.4 | 11.7 | 81.8 | 60.6 | 48.9 | 50.5 | 54.2 | 57.6 | 63.9 | 69.8 | 74.1 | 74 | 70.4 | 62.3 | 53.6 | 47.7 | 10.92 | 4.91 | 5.07 | 5.33 | 6.11 | 6.14 | 6 | 5.57 | 5.13 | 5.7 | 5.75 | 5.78 | 5.12 | 294 | 78 | 52 | 20 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 106 | 2611 | 498 | 407 | 334 | 233 | 97 | 21 | 2 | 1 | 16 | 121 | 344 | 537 | 4173 | 45 | 65 | 152 | 236 | 430 | 593 | 746 | 742 | 611 | 383 | 137 | 33 | 1015 | 0 | 0 | 1 | 10 | 62 | 164 | 284 | 279 | 176 | 38 | 1 | 0 | 16335 | 7 | 16 | 142 | 489 | 1368 | 2727 | 3898 | 3807 | 2694 | 1055 | 131 | 1 | 8895 | 1 | 0 | 28 | 174 | 648 | 1521 | 2297 | 2265 | 1491 | 443 | 27 | 0 | 6.4 | 4.8 | 5.3 | 5.9 | 7.4 | 8.6 | 9 | 8.1 | 7.3 | 6.2 | 5.2 | 4.5 | 4.6 | 12.4 | 2.6 | 2.7 | 2.2 | 0.9 | 0.1 | 0 | 0 | 0 | 0.2 | 0.4 | 1.4 | 1.9 | 24.4 | 12.2 | 8.8 | 9 | 4.5 | 1.7 | 0.1 | 0.3 | 0.9 | 1.3 | 2.4 | 5.2 | 6.8 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 2.4 | 2.6 | 1.9 | 1 | 0.3 | 0 | 0.1 | 0.2 | 0.3 | 0.6 | 1.3 | 1.5 | 73.4 | 76.6 | 83.7 | 91.5 | 98.9 | 104.2 | 106.4 | 106.4 | 103.1 | 95.9 | 83.7 | 71.4 | 52.6 | 57.8 | 60.7 | 61.2 | 65.1 | 67.4 | 68.8 | 69 | 66.5 | 63.9 | 58.3 | 51.7 | 68.1 | 71.3 | 78 | 85.1 | 92.9 | 99 | 101.6 | 101.6 | 98.6 | 89.7 | 77.8 | 66.1 | 52.8 | 56 | 58.6 | 60.1 | 63 | 65.3 | 67 | 66.2 | 65.1 | 61.1 | 57 | 51.9 | 63.6 | 66 | 73 | 79.7 | 87.4 | 94.4 | 97.5 | 97.5 | 94.2 | 84.9 | 72.3 | 62.6 | 52.7 | 54 | 56.5 | 58.4 | 61 | 64 | 65.8 | 65.4 | 63.7 | 59.5 | 55.3 | 52.1 | 59.7 | 61.7 | 68.4 | 74.3 | 81.9 | 89.5 | 93.1 | 92.9 | 89.5 | 80 | 67.2 | 58.8 | 51.6 | 52.5 | 55.1 | 56.3 | 59.5 | 62.7 | 64.6 | 64.2 | 63 | 58.4 | 53.8 | 51 | 59.6 | 60.9 | 63.5 | 64.9 | 67.6 | 70.8 | 71.5 | 71.6 | 70.6 | 66.8 | 61.3 | 59.5 | 64.2 | 70 | 78.2 | 83.8 | 94.2 | 99.3 | 101.5 | 99.7 | 92.2 | 86.4 | 74.5 | 64.3 | 56.6 | 58.1 | 60.2 | 61.6 | 64.7 | 67.7 | 69 | 68.6 | 67.4 | 63.7 | 59.3 | 56.8 | 62.1 | 66.1 | 74.1 | 80.3 | 89.1 | 93.7 | 95.8 | 96.2 | 90.2 | 83.4 | 71.8 | 60.9 | 54.7 | 55.9 | 58 | 59.4 | 62.4 | 65.5 | 67.2 | 66.8 | 65.4 | 61.5 | 57.5 | 54.5 | 60 | 63.4 | 70.4 | 77 | 84.2 | 90.5 | 93.6 | 93.7 | 90.1 | 79.2 | 68 | 58.7 | 52.8 | 53.7 | 55.8 | 57.3 | 60.2 | 63.4 | 65.5 | 65.1 | 63.6 | 59.6 | 55.5 | 52.1 | 58.2 | 60.3 | 66.2 | 72.5 | 79.2 | 86.7 | 90.8 | 90.2 | 87.1 | 76.4 | 64.9 | 56.9 | 24.3 | 23.6 | 27 | 30.5 | 32.7 | 36.5 | 37.3 | 38.2 | 37.4 | 34.3 | 28.9 | 24.4 | 32.2 | 32.8 | 36.2 | 40.6 | 43.1 | 44.8 | 44.2 | 45.1 | 45.1 | 43.2 | 37.9 | 31 | 19.1 | 18.7 | 18.8 | 18.6 | 17.5 | 16.8 | 15.6 | 16.1 | 17.6 | 19.1 | 19.3 | 18.6 | 22.6 | 26.1 | 31.9 | 36.4 | 39.3 | 40.7 | 40 | 41.3 | 39.8 | 37.2 | 30.5 | 19.8 | 14.8 | 15.8 | 17.4 | 17.9 | 16.9 | 16.8 | 15.2 | 16 | 16.3 | 17.2 | 16.7 | 13.7 | 0.301 | 0.314 | 0.32 | 0.337 | 0.354 | 0.34 | 0.362 | 0.339 | 0.345 | 0.335 | 0.308 | 0.305 | 2.554 | 2.524 | 2.509 | 2.457 | 2.418 | 2.464 | 2.43 | 2.474 | 2.461 | 2.491 | 2.54 | 2.552 | 288 | 296 | 302 | 300 | 294 | 297 | 290 | 296 | 289 | 283 | 282 | 279 | 25 | 29 | 31 | 35 | 37 | 35 | 36 | 34 | 33 | 29 | 25 | 23 | 895 | 1178 | 1641 | 2068 | 2408 | 2608 | 2478 | 2273 | 1924 | 1427 | 1031 | 797 | 81 | 129 | 125 | 148 | 121 | 89 | 75 | 59 | 58 | 78 | 54 | 82 | N/A | N/A | -3.67 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.9 | N/A | -1.75 | 0.97 | N/A | N/A | N/A | -266 | 319 | 76 | 29
4 | USA | CA | EASTERN SIERRA | 724800 | 23157 | 37.371 | -118.358 | 4102 | 12.64 | -8 | NAP | 94-19 | 4B | 12 | 16.1 | 19.3 | -6.5 | 4.5 | 43.8 | -2.7 | 5.5 | 46.2 | 28.4 | 45.5 | 25.9 | 45 | 5.6 | 320 | 0.561 | 7 | 39.3 | 101.5 | 62 | 99.3 | 61.3 | 97.2 | 60.5 | 65.9 | 93 | 64.2 | 91.4 | 62.8 | 90.3 | 10.1 | 160 | 57.3 | 81.7 | 72.6 | 53.8 | 71.8 | 75.3 | 50.6 | 63.6 | 75 | 32.7 | 92.4 | 31.3 | 91 | 30.2 | 90.3 | 72.7 | 25.5 | 22.5 | 19.5 | 9.1 | 105.5 | 3.1 | 1.7 | 6.9 | 106.8 | 5.1 | 107.8 | 3.4 | 108.8 | 1.2 | 110 | 7.3 | 67.6 | 3.2 | 2.2 | 5 | 69.1 | 3.1 | 70.4 | 1.3 | 71.6 | -1 | 73.2 | 57.1 | 39.8 | 42.3 | 49.2 | 54.6 | 62.9 | 72.4 | 78.1 | 75.7 | 68.1 | 56.9 | 45.5 | 38.2 | 15.04 | 6.3 | 6.62 | 6.65 | 7.11 | 6.95 | 6.29 | 4.08 | 3.75 | 5.42 | 6.45 | 6.98 | 6.16 | 1230 | 318 | 225 | 97 | 37 | 3 | 0 | 0 | 0 | 0 | 18 | 164 | 368 | 4063 | 781 | 635 | 490 | 314 | 122 | 16 | 0 | 0 | 32 | 257 | 584 | 832 | 3812 | 2 | 10 | 72 | 177 | 404 | 673 | 871 | 795 | 543 | 234 | 30 | 1 | 1170 | 0 | 0 | 0 | 4 | 58 | 239 | 406 | 331 | 125 | 7 | 0 | 0 | 23725 | 1 | 4 | 71 | 390 | 1685 | 4725 | 7130 | 6124 | 2984 | 589 | 22 | 0 | 13385 | 0 | 0 | 6 | 81 | 693 | 2745 | 4500 | 3730 | 1479 | 150 | 1 | 0 | 7.9 | 7 | 8 | 9 | 9.9 | 8.8 | 8.2 | 7.9 | 7.8 | 7.5 | 7.6 | 6.9 | 6.8 | 5.4 | 0.9 | 1 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.6 | 0.7 | 17.1 | 8.9 | 6 | 3 | 1.6 | 1.3 | 1.3 | 0.7 | 0.6 | 1.2 | 0.8 | 2.6 | 5.8 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 1.5 | 1.5 | 0.6 | 0.3 | 0.4 | 0.3 | 0.2 | 0.2 | 0.3 | 0.2 | 0.7 | 1.1 | 69.2 | 73.6 | 80.3 | 86.5 | 95.1 | 102.9 | 105.1 | 102.5 | 97 | 88.6 | 76.9 | 67.3 | 46.2 | 47.2 | 50.8 | 54.1 | 58.5 | 61.1 | 63.5 | 63.1 | 60.6 | 56.2 | 50.3 | 45.6 | 64.4 | 68.7 | 75.7 | 82.2 | 90.9 | 99.4 | 102.3 | 100.1 | 94.2 | 84.2 | 72.6 | 62.4 | 44.1 | 45.5 | 48.7 | 51.9 | 56.4 | 59.9 | 62.8 | 61.8 | 59.4 | 54.3 | 48.7 | 43 | 60.4 | 64.6 | 72.2 | 78.8 | 87.5 | 96.8 | 100.1 | 98 | 91.9 | 80.5 | 68.4 | 58.4 | 42.6 | 44.1 | 47.4 | 50.7 | 55.1 | 59.4 | 61.9 | 60.8 | 58.5 | 52.5 | 46.7 | 41.4 | 55.7 | 59.6 | 68.5 | 74.8 | 83.8 | 94.1 | 97.9 | 95.9 | 89.1 | 76.8 | 63.8 | 53.9 | 40.7 | 42 | 45.9 | 49 | 53.9 | 58.6 | 61.2 | 60.1 | 57.2 | 50.7 | 44.5 | 39.5 | 49.5 | 49.2 | 52.2 | 56.1 | 60.4 | 65.5 | 68.4 | 67.8 | 64.3 | 59.2 | 52.2 | 48.1 | 64.8 | 67.7 | 76.2 | 82.5 | 90.8 | 97.1 | 96.2 | 96.1 | 89.6 | 77 | 73.1 | 62.4 | 46.2 | 46.9 | 50 | 53.1 | 57.8 | 62.5 | 66.4 | 65.1 | 62.3 | 56.1 | 49.8 | 45.2 | 59 | 65.7 | 73 | 79.3 | 86.6 | 94.4 | 93.2 | 92.7 | 88 | 79.1 | 69.6 | 58 | 44.1 | 44.9 | 48.3 | 51.2 | 56.3 | 60.9 | 64.9 | 63.5 | 60.4 | 53.8 | 47.7 | 42.4 | 57.3 | 61.8 | 70.2 | 76.5 | 84.1 | 92.8 | 91.4 | 91.3 | 86.1 | 77.4 | 66.2 | 55.6 | 41.8 | 42.9 | 46.4 | 49.7 | 54.6 | 59.4 | 63.5 | 62 | 58.4 | 51.7 | 45.5 | 40.2 | 55.1 | 57.8 | 67 | 73.6 | 81.1 | 90.6 | 90.1 | 89.6 | 84.9 | 74.2 | 62.9 | 53 | 29.4 | 29.6 | 33 | 33.3 | 35 | 38.6 | 39.3 | 40.5 | 39.3 | 36.6 | 33.8 | 29.5 | 37.2 | 38.6 | 39.1 | 40 | 40.6 | 42.2 | 41.9 | 42.6 | 42.6 | 41.9 | 39.6 | 36.9 | 20.7 | 19.7 | 18.6 | 17.3 | 15.6 | 14.9 | 14.7 | 15.6 | 17.3 | 19.2 | 20.7 | 21.3 | 32.6 | 34.6 | 37.1 | 38 | 38.7 | 39.9 | 36.7 | 38.2 | 39.6 | 38.2 | 37.3 | 33.6 | 18.9 | 18.3 | 18 | 17 | 15.3 | 15.4 | 13.9 | 15.1 | 17.1 | 17.8 | 19.8 | 20 | 0.262 | 0.276 | 0.287 | 0.318 | 0.333 | 0.33 | 0.34 | 0.328 | 0.305 | 0.289 | 0.265 | 0.261 | 2.473 | 2.446 | 2.443 | 2.398 | 2.415 | 2.437 | 2.47 | 2.478 | 2.545 | 2.567 | 2.576 | 2.513 | 298 | 306 | 312 | 305 | 300 | 300 | 296 | 298 | 302 | 298 | 297 | 292 | 25 | 30 | 33 | 37 | 37 | 36 | 35 | 34 | 30 | 26 | 23 | 23 | 857 | 1146 | 1571 | 2014 | 2292 | 2636 | 2454 | 2307 | 1962 | 1446 | 1013 | 764 | 74 | 107 | 107 | 107 | 177 | 168 | 148 | 125 | 75 | 97 | 56 | 76 | 0.68 | N/A | -2.63 | N/A | N/A | N/A | N/A | N/A | 220 | 146 | 0.97 | N/A | N/A | 0.72 | N/A | N/A | -81 | N/A | 274 | 166 | 14
4 | USA | CA | MERCED | 724815 | 23257 | 37.285 | -120.513 | 152 | 14.62 | -8 | NAP | 98-19 | 3B | 12 | 29.7 | 32.1 | 21.5 | 16.2 | 48.7 | 25.4 | 19.6 | 46.5 | 24.7 | 53.8 | 20.6 | 52.2 | 2.4 | 100 | 0.464 | 7 | 32.2 | 101.5 | 69.5 | 99 | 68.7 | 96.7 | 67.6 | 72.2 | 96 | 70.6 | 94.1 | 69.1 | 92.2 | 9.3 | 330 | 63.6 | 88.5 | 81.7 | 61.5 | 81.9 | 79.9 | 59.9 | 77.5 | 79.2 | 35.9 | 96.1 | 34.4 | 94 | 33.2 | 92.3 | 85.8 | 19.5 | 16.8 | 14.4 | 26 | 106.2 | 2.4 | 2 | 24.3 | 107.6 | 22.9 | 108.8 | 21.5 | 109.9 | 19.8 | 111.3 | 24.6 | 75.4 | 2.8 | 4.1 | 22.6 | 78.4 | 21 | 80.8 | 19.4 | 83.1 | 17.4 | 86.1 | 62.4 | 46.4 | 50.2 | 55.2 | 59.8 | 67.5 | 74.8 | 79.5 | 77.7 | 73.4 | 64.1 | 53.5 | 46.5 | 12.86 | 4.84 | 4.68 | 5.5 | 6.35 | 6.22 | 6 | 4.95 | 4.29 | 5.87 | 5.6 | 5.54 | 5.18 | 365 | 131 | 51 | 16 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 135 | 2533 | 575 | 413 | 305 | 181 | 43 | 4 | 0 | 0 | 7 | 84 | 346 | 575 | 4907 | 21 | 57 | 177 | 297 | 544 | 743 | 914 | 858 | 702 | 436 | 133 | 25 | 1601 | 0 | 0 | 1 | 24 | 122 | 297 | 449 | 393 | 259 | 55 | 1 | 0 | 22521 | 0 | 0 | 95 | 507 | 1920 | 4216 | 6227 | 5229 | 3421 | 873 | 33 | 0 | 12184 | 0 | 0 | 12 | 164 | 841 | 2321 | 3739 | 3016 | 1806 | 282 | 3 | 0 | 6.1 | 4.6 | 5.5 | 5.9 | 7 | 7.8 | 8 | 7.5 | 7 | 5.9 | 5.2 | 4.3 | 4.9 | 12.4 | 2.4 | 2.2 | 2 | 1 | 0.4 | 0.1 | 0 | 0 | 0.2 | 0.7 | 1.6 | 1.9 | 21.7 | 7.1 | 6.1 | 5.5 | 4.6 | 2.1 | 0.6 | 0.4 | 0.5 | 1.3 | 3.8 | 4.9 | 4.5 | 6.6 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 3.9 | 1.8 | 1.6 | 1.5 | 0.9 | 0.6 | 0.2 | 0.1 | 0.1 | 0.3 | 0.9 | 1.3 | 1.2 | 66.3 | 71.5 | 81.5 | 91.1 | 97.5 | 103.9 | 105.3 | 103.3 | 100.3 | 92.9 | 78.2 | 65 | 53.2 | 57.7 | 61.3 | 64.4 | 67.2 | 70.6 | 71.1 | 69.5 | 67.7 | 65.1 | 60.2 | 55 | 61.9 | 67.5 | 76.4 | 84.4 | 93.3 | 99.4 | 101.9 | 99.7 | 97.7 | 86.8 | 73.1 | 61.3 | 52.8 | 56.3 | 59.7 | 61.9 | 65.4 | 69.4 | 69.7 | 68.8 | 66.7 | 63.5 | 58.1 | 53 | 58.7 | 64 | 72.6 | 80.1 | 89 | 96.2 | 99.2 | 97.2 | 94.3 | 82.3 | 69.3 | 58.5 | 52 | 54.5 | 58.4 | 60.5 | 63.5 | 67.4 | 69.4 | 67.8 | 65.9 | 61.4 | 56.9 | 52.1 | 55.5 | 61.1 | 68.7 | 75.1 | 84.2 | 92.3 | 96.3 | 94.2 | 90.7 | 79 | 65.2 | 55.9 | 50.5 | 53 | 56.8 | 58.4 | 61.8 | 66 | 68.1 | 67 | 65.1 | 59.9 | 55 | 50.7 | 57.4 | 60.3 | 64.5 | 67.1 | 70.3 | 73.3 | 74.7 | 73.2 | 72.4 | 67.8 | 62.4 | 58.8 | 61.3 | 67.5 | 76.1 | 83 | 93.3 | 98.2 | 97.3 | 96.1 | 91.1 | 84.3 | 73.8 | 62.9 | 55 | 58 | 61.6 | 63.8 | 67.1 | 71 | 72.4 | 71 | 69.3 | 65.4 | 59.9 | 55.7 | 58.7 | 64.7 | 73.6 | 81.2 | 89.8 | 95.4 | 97.3 | 94.7 | 90.5 | 82.2 | 70.4 | 58.9 | 53.1 | 55.8 | 59.5 | 61.5 | 64.7 | 69.1 | 70.6 | 69.3 | 67.6 | 63.4 | 57.9 | 53.7 | 56.2 | 62.4 | 70.2 | 77.8 | 85.7 | 92 | 95 | 92.7 | 90.2 | 80.1 | 66.5 | 56.9 | 51.3 | 54 | 57.4 | 59.5 | 62.7 | 67.4 | 69.1 | 68 | 66 | 61.4 | 56.1 | 51.6 | 55.2 | 59.8 | 66.9 | 73.2 | 82.2 | 89.7 | 92.8 | 91 | 88.1 | 75.6 | 63.6 | 54.8 | 17 | 20.5 | 23.5 | 25.8 | 28.8 | 31.4 | 32.2 | 32.3 | 31.5 | 27.6 | 22.4 | 17.8 | 22.8 | 25.6 | 30.1 | 33.7 | 35.3 | 35 | 34.3 | 35.1 | 36 | 33.3 | 28.6 | 21.5 | 14.9 | 15.4 | 15.4 | 14.5 | 13.6 | 12.1 | 11.5 | 11.7 | 12.1 | 14.2 | 15.2 | 13.8 | 16.6 | 22.3 | 27.6 | 31.2 | 33.2 | 33.3 | 32 | 33.1 | 33.1 | 29.2 | 24.2 | 14.6 | 11.8 | 14.3 | 15.3 | 14.3 | 13.7 | 12.3 | 11.8 | 11.8 | 12 | 12.6 | 13.7 | 10.3 | 0.347 | 0.352 | 0.359 | 0.361 | 0.361 | 0.352 | 0.366 | 0.355 | 0.356 | 0.367 | 0.355 | 0.335 | 2.384 | 2.393 | 2.369 | 2.381 | 2.402 | 2.436 | 2.409 | 2.417 | 2.425 | 2.378 | 2.373 | 2.445 | 263 | 278 | 286 | 292 | 292 | 293 | 288 | 290 | 284 | 268 | 257 | 260 | 29 | 32 | 36 | 37 | 37 | 36 | 37 | 36 | 34 | 32 | 29 | 25 | 744 | 1093 | 1564 | 2003 | 2397 | 2663 | 2591 | 2351 | 1935 | 1404 | 935 | 683 | 119 | 121 | 140 | 160 | 121 | 84 | 80 | 66 | 61 | 80 | 56 | 99 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.72 | N/A | -2.07 | N/A | N/A | N/A | N/A | -205 | 248 | 63 | 45
4 | USA | CA | VACAVILLE NUT TREE | 724828 | 93241 | 38.378 | -121.958 | 109 | 14.64 | -8 | NAP | 01-19 | 3A | 1 | 30.5 | 33.8 | 13.6 | 11 | 57.7 | 17.9 | 13.6 | 57.2 | 22 | 51 | 18.9 | 52.3 | 0.5 | 350 | 0.455 | 7 | 33.1 | 101.9 | 68.7 | 99.1 | 67.8 | 95.8 | 67 | 71.2 | 97 | 69.7 | 94.3 | 68.4 | 92.2 | 8.3 | 220 | 61.3 | 81.4 | 80.6 | 59.8 | 76.9 | 79 | 58.3 | 73 | 77.1 | 34.9 | 97.3 | 33.6 | 94.5 | 32.5 | 92.3 | 77 | 19.9 | 17.3 | 15.3 | 26.3 | 107.7 | 3.3 | 2.9 | 23.9 | 109.8 | 22 | 111.5 | 20.2 | 113.1 | 17.8 | 115.2 | 24.8 | 73.8 | 3.2 | 2.2 | 22.5 | 75.4 | 20.6 | 76.7 | 18.8 | 77.9 | 16.5 | 79.6 | 62.6 | 48.3 | 51.7 | 56 | 59.8 | 66.1 | 73.4 | 77.8 | 76 | 73.1 | 65 | 54.8 | 48.2 | 11.73 | 4.6 | 4.92 | 5.54 | 6.13 | 5.94 | 6.18 | 5.06 | 4.57 | 5.41 | 5.53 | 5.61 | 5.03 | 246 | 86 | 36 | 11 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 94 | 2319 | 517 | 374 | 283 | 180 | 56 | 7 | 0 | 0 | 4 | 68 | 308 | 522 | 4835 | 35 | 82 | 197 | 295 | 500 | 702 | 861 | 807 | 692 | 464 | 163 | 37 | 1430 | 0 | 0 | 4 | 23 | 90 | 259 | 396 | 342 | 247 | 67 | 2 | 0 | 19751 | 2 | 9 | 121 | 461 | 1427 | 3639 | 5265 | 4368 | 3295 | 1094 | 70 | 0 | 10493 | 0 | 1 | 14 | 149 | 587 | 1976 | 3128 | 2465 | 1768 | 399 | 6 | 0 | 5.8 | 3.9 | 5.3 | 6 | 6.6 | 7.3 | 7.2 | 6.9 | 6.4 | 5.5 | 5.1 | 4.2 | 4.7 | 26.3 | 5.7 | 4.6 | 3.5 | 1.3 | 0.6 | 0.1 | 0 | 0.1 | 0.3 | 1.2 | 3.5 | 4.9 | 48.9 | 16.7 | 15.2 | 10.7 | 6.4 | 3.4 | 1.6 | 1.2 | 1.4 | 1.7 | 8.2 | 8.9 | 18.4 | 8.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 8.7 | 4.2 | 3.9 | 2.7 | 1.5 | 0.8 | 0.3 | 0.2 | 0.2 | 0.4 | 1.5 | 2.7 | 4.1 | 70.5 | 75.1 | 81.8 | 90.1 | 96.7 | 104.1 | 107.7 | 104.4 | 102 | 94.1 | 80 | 66.2 | 51.4 | 57.6 | 60.8 | 63.5 | 67.1 | 70.3 | 71.2 | 68.4 | 66.2 | 63.3 | 58.9 | 52.1 | 65.6 | 71.2 | 77.4 | 84.2 | 90.7 | 99.8 | 102.1 | 99.7 | 98.6 | 88.5 | 75.4 | 63.1 | 51.7 | 55.2 | 59.5 | 61.3 | 65.2 | 68.6 | 69.6 | 67.6 | 65.9 | 61.6 | 57.7 | 52.2 | 61.6 | 66.3 | 73.1 | 79.5 | 86.9 | 95.3 | 98.9 | 96.7 | 94.5 | 84.1 | 71.1 | 60.5 | 51.1 | 53.2 | 57.5 | 60 | 63.1 | 67.3 | 68.7 | 67.2 | 64.9 | 60 | 55.7 | 51.9 | 58 | 62.9 | 69.6 | 74.4 | 82 | 91 | 94.9 | 92.6 | 90.5 | 80.7 | 66.3 | 57.4 | 50.1 | 52 | 55.5 | 57.8 | 61.6 | 65.4 | 67.5 | 66.2 | 63.8 | 59 | 54 | 51.1 | 58 | 60.4 | 63.3 | 66.9 | 70.3 | 73.4 | 73.4 | 71.4 | 70.2 | 66.5 | 62.5 | 59.4 | 62.5 | 69.2 | 77.4 | 84.6 | 90.7 | 97.7 | 102.5 | 97.5 | 94.5 | 85.7 | 74.6 | 62.3 | 55.4 | 58 | 61 | 63.7 | 67.3 | 70.8 | 71.3 | 69.7 | 67.9 | 64.4 | 60.2 | 57 | 60.7 | 66.2 | 74.5 | 80.5 | 88.3 | 95.6 | 98.4 | 94.4 | 92 | 83 | 69.2 | 59.4 | 53.6 | 55.9 | 58.9 | 61.2 | 64.9 | 68.6 | 69.8 | 68.4 | 66.4 | 62.5 | 58.5 | 54.7 | 57.2 | 63.1 | 70.8 | 76.1 | 83.8 | 91.9 | 95.7 | 92.4 | 90 | 79 | 66.3 | 57.2 | 51.8 | 54 | 56.9 | 59.1 | 62.7 | 66.8 | 68.4 | 67.2 | 65 | 60.8 | 56.7 | 52.9 | 56.4 | 60.2 | 66.5 | 72.7 | 79.7 | 88.7 | 92.9 | 90.4 | 87.7 | 75.7 | 64.1 | 55.5 | 18.3 | 20.2 | 21.5 | 23.4 | 26.4 | 30.1 | 33.1 | 32.7 | 32 | 27.5 | 22.3 | 17.3 | 26.3 | 28.2 | 30 | 32.4 | 34.4 | 37.2 | 37.9 | 37.5 | 38.5 | 35.2 | 29.3 | 22.6 | 15.2 | 15.2 | 15.5 | 15.3 | 14.5 | 13.9 | 13.5 | 13.2 | 14 | 14.4 | 14.5 | 13.4 | 17.9 | 22 | 27.4 | 29.9 | 32.2 | 34.8 | 35.8 | 34.6 | 34.4 | 29.7 | 22.2 | 13 | 12 | 13.1 | 14.9 | 15.2 | 14.9 | 14.2 | 13.6 | 13 | 13.5 | 13.5 | 12.5 | 9.4 | 0.319 | 0.321 | 0.332 | 0.353 | 0.358 | 0.356 | 0.358 | 0.343 | 0.343 | 0.328 | 0.321 | 0.324 | 2.525 | 2.524 | 2.48 | 2.402 | 2.414 | 2.425 | 2.411 | 2.444 | 2.452 | 2.519 | 2.524 | 2.513 | 274 | 289 | 295 | 293 | 292 | 292 | 290 | 293 | 287 | 282 | 271 | 263 | 24 | 28 | 32 | 36 | 37 | 36 | 37 | 35 | 32 | 27 | 24 | 23 | 709 | 1029 | 1462 | 1934 | 2324 | 2583 | 2550 | 2277 | 1865 | 1323 | 866 | 628 | 123 | 133 | 149 | 163 | 138 | 106 | 73 | 70 | 62 | 88 | 61 | 103 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.72 | N/A | -2.03 | N/A | N/A | N/A | N/A | -216 | 245 | 54 | 51
4 | USA | CA | SACRAMENTO EXECUTIVE | 724830 | 23232 | 38.507 | -121.495 | 15 | 14.69 | -8 | NAP | 94-19 | 3A | 12 | 31.5 | 34 | 20.3 | 15.3 | 53.2 | 24.1 | 18.3 | 51.3 | 24.8 | 54.3 | 21.2 | 52 | 1.1 | 330 | 0.463 | 7 | 31.8 | 100.2 | 69.6 | 97 | 68.3 | 93.7 | 67.3 | 72.1 | 95.1 | 70.3 | 92.5 | 68.7 | 90 | 6.9 | 220 | 63.6 | 87.9 | 83.1 | 61.5 | 81.7 | 79.1 | 60.1 | 77.6 | 76.8 | 35.7 | 94.9 | 34.1 | 92.8 | 32.8 | 90 | 81 | 19.9 | 17.5 | 15.3 | 27.6 | 106.1 | 2.8 | 2.5 | 25.6 | 107.9 | 24 | 109.3 | 22.4 | 110.7 | 20.4 | 112.5 | 26.4 | 74.3 | 2.8 | 2.3 | 24.4 | 75.9 | 22.7 | 77.3 | 21.2 | 78.6 | 19.1 | 80.3 | 61.7 | 47.9 | 51.3 | 55.5 | 59.3 | 65.7 | 72 | 75.7 | 75 | 72.1 | 64 | 53.9 | 47.6 | 11.38 | 4.65 | 4.54 | 5.19 | 5.99 | 6.17 | 6.03 | 5.16 | 4.75 | 5.11 | 5.25 | 5.36 | 5.06 | 278 | 95 | 36 | 12 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 109 | 2436 | 530 | 385 | 297 | 190 | 64 | 9 | 0 | 0 | 5 | 81 | 334 | 541 | 4556 | 30 | 71 | 181 | 282 | 488 | 660 | 796 | 777 | 663 | 435 | 140 | 33 | 1238 | 0 | 0 | 1 | 20 | 86 | 219 | 331 | 312 | 218 | 50 | 1 | 0 | 15445 | 0 | 1 | 61 | 364 | 1276 | 2836 | 3973 | 3611 | 2550 | 745 | 28 | 0 | 7894 | 0 | 0 | 3 | 107 | 552 | 1474 | 2238 | 1985 | 1291 | 243 | 1 | 0 | 6 | 4.9 | 5.7 | 6.2 | 6.9 | 7.3 | 7.4 | 7.1 | 6.5 | 5.5 | 5.1 | 4.3 | 5.1 | 19.8 | 3.7 | 3.5 | 2.9 | 1.4 | 0.8 | 0.2 | 0 | 0 | 0.1 | 1.1 | 2 | 4 | 32.8 | 9.5 | 10.9 | 8.7 | 4.4 | 3.7 | 1.5 | 0.2 | 0.5 | 0.5 | 3.9 | 4.6 | 9.8 | 7.8 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.2 | 5.5 | 2.9 | 2.4 | 2.5 | 1 | 0.9 | 0.4 | 0 | 0.1 | 0.2 | 0.9 | 1.2 | 2.6 | 66 | 71.9 | 79.6 | 88.5 | 96.6 | 103 | 104.2 | 104.1 | 100.2 | 92.3 | 77.7 | 64.6 | 52.3 | 57.3 | 61.3 | 63.6 | 68.1 | 70.8 | 71.6 | 70.2 | 67.6 | 64.7 | 59.6 | 54.8 | 61.8 | 67.4 | 75.2 | 82.9 | 91.2 | 97.9 | 99.9 | 98.9 | 96 | 86.1 | 72.9 | 61.2 | 53 | 55.9 | 59.4 | 61.1 | 66 | 68.9 | 70.3 | 69.2 | 66.5 | 62.4 | 57.9 | 54 | 58.9 | 63.8 | 71.4 | 78.2 | 86.5 | 93.6 | 96.1 | 95.1 | 92.2 | 81.9 | 68.1 | 58.9 | 52.5 | 53.9 | 57.7 | 60.3 | 63.2 | 67 | 68.8 | 67.8 | 65.3 | 60.3 | 56.2 | 52.8 | 56.2 | 60.6 | 67.4 | 73 | 81.4 | 88.6 | 92.2 | 91 | 88 | 77.7 | 64.2 | 56.6 | 51.2 | 52.9 | 55.9 | 57.9 | 61.7 | 65.8 | 68.1 | 66.9 | 64.4 | 59.2 | 54.7 | 51.3 | 58.5 | 60.5 | 63.9 | 67.2 | 70.6 | 73.3 | 75.3 | 75.2 | 71.6 | 67.3 | 62.5 | 59.1 | 60.9 | 66.4 | 75.9 | 81.5 | 91.3 | 97.6 | 98.4 | 97.1 | 92.6 | 85.2 | 73.1 | 62.3 | 55.6 | 58.2 | 61.3 | 63.8 | 67.7 | 70.8 | 72.1 | 71.1 | 68.5 | 64.6 | 60 | 56.8 | 58.7 | 64.3 | 72.5 | 78.8 | 88 | 93.7 | 95.6 | 94.2 | 89.1 | 81.6 | 68.6 | 59.3 | 53.6 | 56.1 | 59.2 | 61.6 | 65.3 | 68.7 | 70.3 | 69.1 | 66.9 | 62.6 | 58.2 | 54.6 | 56.4 | 61.4 | 68.8 | 75.4 | 83.6 | 90 | 92.7 | 91.2 | 87.6 | 77.3 | 65.2 | 57 | 52.1 | 54.1 | 57 | 59.4 | 63 | 66.8 | 68.6 | 67.6 | 65.4 | 60.8 | 56.3 | 52.5 | 55.2 | 58.9 | 65.4 | 70.9 | 78.6 | 86.4 | 89.9 | 88.7 | 85.6 | 73.7 | 62.3 | 55.3 | 15.4 | 17.9 | 20.7 | 23.2 | 26.4 | 29.7 | 31.8 | 31.5 | 30.2 | 26.3 | 20.3 | 16 | 20.6 | 24 | 27.9 | 31.7 | 34.5 | 36.6 | 36.4 | 36.7 | 36.6 | 33.4 | 26.9 | 19.3 | 12.6 | 14 | 14.5 | 14.1 | 13.2 | 13 | 13.1 | 12.6 | 12 | 12.5 | 13.4 | 11.9 | 13.8 | 19.3 | 24.9 | 28.7 | 32.6 | 34.2 | 34.5 | 33.8 | 32.6 | 28.6 | 21.7 | 11.5 | 9.4 | 12.2 | 13.9 | 14.2 | 13.8 | 13.7 | 13.8 | 12.8 | 11.8 | 11.6 | 12.1 | 8.3 | 0.324 | 0.326 | 0.341 | 0.356 | 0.365 | 0.362 | 0.363 | 0.347 | 0.351 | 0.345 | 0.331 | 0.333 | 2.503 | 2.504 | 2.449 | 2.399 | 2.395 | 2.413 | 2.407 | 2.442 | 2.437 | 2.463 | 2.486 | 2.473 | 271 | 286 | 292 | 292 | 290 | 290 | 289 | 292 | 284 | 275 | 266 | 258 | 25 | 28 | 33 | 37 | 37 | 37 | 37 | 35 | 33 | 29 | 25 | 24 | 685 | 1025 | 1464 | 1939 | 2352 | 2618 | 2603 | 2332 | 1892 | 1338 | 857 | 616 | 130 | 128 | 148 | 161 | 138 | 102 | 73 | 73 | 64 | 85 | 60 | 102 | N/A | N/A | N/A | N/A | -0.94 | N/A | N/A | N/A | N/A | N/A | 0.72 | N/A | -1.94 | N/A | N/A | N/A | N/A | -209 | 248 | 76 | 48
4 | USA | CA | SACRAMENTO MATHER | 724833 | 23206 | 38.567 | -121.3 | 99 | 14.64 | -8 | NAP | 86-19 | 3A | 12 | 28.2 | 30.9 | 17.8 | 13.5 | 45 | 22.2 | 16.7 | 45.3 | 29.7 | 52.1 | 26.7 | 51 | 2.4 | 110 | 0.458 | 7 | 35.2 | 101.2 | 68.7 | 98.3 | 67.4 | 94.8 | 66.5 | 70.9 | 96.6 | 69.3 | 93.6 | 68 | 91.3 | 5.9 | 260 | 61.4 | 81.5 | 75.7 | 60 | 77.5 | 75.9 | 58.6 | 73.7 | 74.6 | 34.5 | 96.9 | 33.3 | 93.9 | 32.2 | 91.3 | 76.3 | 20.6 | 17 | 13.8 | 24.3 | 107.7 | 4.3 | 2.8 | 21.2 | 109.7 | 18.7 | 111.3 | 16.3 | 112.9 | 13.2 | 114.9 | 22.6 | 74.4 | 3.8 | 1.5 | 19.9 | 75.5 | 17.7 | 76.4 | 15.6 | 77.2 | 12.8 | 78.3 | 60.7 | 45.4 | 50.3 | 54.4 | 58.1 | 64.2 | 70.7 | 76.4 | 74.6 | 71.2 | 64.3 | 52.5 | 45.2 | 12.16 | 4.92 | 5.43 | 5.1 | 6.22 | 7.36 | 6.39 | 5.19 | 5.23 | 5.7 | 6.14 | 5.25 | 5.6 | 448 | 159 | 59 | 17 | 9 | 4 | 0 | 0 | 0 | 0 | 1 | 34 | 165 | 2774 | 608 | 410 | 329 | 219 | 102 | 20 | 0 | 1 | 12 | 85 | 376 | 612 | 4345 | 16 | 69 | 154 | 253 | 444 | 623 | 818 | 763 | 636 | 444 | 108 | 17 | 1197 | 0 | 0 | 0 | 13 | 78 | 192 | 353 | 299 | 199 | 63 | 0 | 0 | 17082 | 0 | 1 | 48 | 373 | 1438 | 2886 | 4707 | 3919 | 2671 | 1026 | 13 | 0 | 9098 | 0 | 0 | 4 | 116 | 632 | 1498 | 2814 | 2239 | 1400 | 395 | 0 | 0 | 5.3 | 4.2 | 5.2 | 6 | 5.8 | 5.9 | 6.3 | 6 | 5.6 | 4.8 | 4.3 | 4.3 | 5.4 | 16.5 | 3.3 | 2.9 | 2.5 | 1.1 | 0.4 | 0.2 | 0 | 0.1 | 0.3 | 0.9 | 2.3 | 2.4 | 33.5 | 9.1 | 8.6 | 7.1 | 4.2 | 2.1 | 1.3 | 0.8 | 0.6 | 2.8 | 6.9 | 7.4 | 6.3 | 6.3 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3 | 2.5 | 2.3 | 1.9 | 1.1 | 0.5 | 0.2 | 0.2 | 0.2 | 0.6 | 1.2 | 2 | 1.7 | 63.8 | 71.7 | 79.2 | 88.4 | 95.3 | 101.8 | 106.9 | 104.4 | 100.7 | 94.8 | 75.7 | 63.9 | 53.3 | 56.6 | 61.6 | 64 | 66.6 | 67.9 | 71.4 | 68.9 | 68.3 | 65 | 59 | 53.3 | 59.6 | 68.2 | 74.3 | 83.6 | 91.3 | 97.4 | 101.7 | 100.1 | 96.6 | 89.2 | 71.4 | 60.6 | 51.1 | 56 | 59.5 | 61.6 | 65.6 | 67.1 | 69.8 | 67.5 | 65.5 | 62.4 | 57.2 | 51.4 | 56.8 | 64.3 | 70.3 | 78 | 87.9 | 93.2 | 98.6 | 96.7 | 92.6 | 84 | 67.9 | 57.2 | 51.1 | 54.1 | 57.6 | 59.2 | 64.3 | 65.7 | 68.4 | 66.7 | 64.4 | 61.1 | 54.9 | 50.8 | 54.3 | 61 | 66.2 | 73.1 | 82.4 | 89.3 | 94.4 | 92.2 | 89.1 | 79.9 | 64 | 54.6 | 49.5 | 52.3 | 56.2 | 57.6 | 61.6 | 64.7 | 67.2 | 65.8 | 63.5 | 59.9 | 53.8 | 49.7 | 56.8 | 60.1 | 64 | 67.7 | 69.4 | 71.5 | 73.3 | 71.8 | 70.7 | 66.2 | 62.2 | 57.4 | 60 | 67.7 | 75.6 | 84.1 | 89.6 | 96.7 | 101.4 | 99.1 | 96.2 | 88.8 | 72.1 | 61.2 | 54.5 | 57.3 | 60.8 | 63.4 | 67.8 | 69.4 | 71.3 | 69.6 | 67.9 | 64.1 | 59.1 | 54.3 | 57.2 | 64.4 | 71.2 | 78.7 | 88.2 | 92.1 | 98.1 | 95.1 | 91 | 84.8 | 66.1 | 56.4 | 52.2 | 55.4 | 59.1 | 60.9 | 65.5 | 67.6 | 69.5 | 68.2 | 65.7 | 62.6 | 57.1 | 52.5 | 55.8 | 61.7 | 68.5 | 74.8 | 84.1 | 89.6 | 95.1 | 92.6 | 88.1 | 80.9 | 63.9 | 55.5 | 50.2 | 53.9 | 57.3 | 58.8 | 63 | 65.9 | 68.1 | 66.7 | 64.2 | 61.1 | 55.4 | 50.4 | 54.1 | 59.5 | 64.7 | 71.1 | 79.3 | 86.5 | 92.2 | 89.6 | 85.8 | 76.7 | 61.4 | 54.7 | 15.7 | 20 | 21.9 | 26.8 | 31.3 | 33.6 | 35.2 | 34.4 | 32.2 | 28.1 | 21.8 | 16.4 | 20.3 | 24.5 | 30.4 | 35.5 | 38.1 | 40.9 | 38.7 | 39.3 | 37.8 | 35.5 | 28 | 20.8 | 13.8 | 14.2 | 17.1 | 16.9 | 15.8 | 16.5 | 13.8 | 13.6 | 14.2 | 14.7 | 15 | 13.2 | 17.3 | 20.5 | 25.4 | 31.7 | 35.5 | 37.5 | 37.1 | 36.3 | 35 | 31.4 | 22.9 | 16 | 12.4 | 12.8 | 14.9 | 16.7 | 15.2 | 15.6 | 14 | 13.3 | 13.7 | 13.6 | 13.2 | 10.9 | 0.324 | 0.326 | 0.347 | 0.356 | 0.369 | 0.364 | 0.364 | 0.348 | 0.355 | 0.351 | 0.333 | 0.336 | 2.501 | 2.504 | 2.43 | 2.402 | 2.384 | 2.409 | 2.41 | 2.445 | 2.431 | 2.443 | 2.477 | 2.454 | 271 | 286 | 290 | 292 | 289 | 289 | 288 | 291 | 283 | 272 | 264 | 256 | 25 | 28 | 33 | 36 | 38 | 37 | 37 | 35 | 33 | 30 | 25 | 24 | 694 | 1017 | 1450 | 1919 | 2336 | 2622 | 2609 | 2340 | 1895 | 1340 | 859 | 619 | 126 | 133 | 157 | 169 | 148 | 108 | 78 | 74 | 67 | 89 | 62 | 103 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.72 | N/A | -1.94 | N/A | N/A | N/A | N/A | -209 | 248 | 76 | 47
4 | USA | CA | BEALE AFB | 724837 | 93216 | 39.133 | -121.433 | 113 | 14.64 | -8 | NAP | 94-19 | 3A | 12 | 31.1 | 33.8 | 20.6 | 15.5 | 48.1 | 24.2 | 18.4 | 47.2 | 29.9 | 53 | 25.9 | 53.8 | 3.6 | 90 | 0.457 | 7 | 31.5 | 101.2 | 70.1 | 98.4 | 69.3 | 95.4 | 68.1 | 73.1 | 95.7 | 71.3 | 93.3 | 69.9 | 91.4 | 7 | 200 | 65 | 92.9 | 82.8 | 63.3 | 87.3 | 80 | 61.4 | 81.8 | 78.7 | 36.6 | 95.6 | 35.1 | 93.8 | 33.8 | 91.4 | 79.5 | 23.5 | 19.5 | 17 | 25.9 | 105.8 | 3.6 | 1.5 | 23.4 | 106.9 | 21.3 | 107.7 | 19.3 | 108.6 | 16.7 | 109.7 | 25.3 | 76.2 | 3.6 | 2.1 | 22.7 | 77.7 | 20.6 | 78.9 | 18.6 | 80.1 | 15.9 | 81.6 | 62.6 | 48 | 51.4 | 55.3 | 59.9 | 66.5 | 74 | 78.6 | 77.3 | 73.7 | 64 | 54.2 | 47 | 12.3 | 4.84 | 4.85 | 5.1 | 6.05 | 6.49 | 6.61 | 4.67 | 4.69 | 5.44 | 5.05 | 5.56 | 5.36 | 294 | 94 | 38 | 12 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 125 | 2413 | 526 | 380 | 302 | 174 | 57 | 7 | 0 | 0 | 5 | 78 | 325 | 559 | 4877 | 33 | 78 | 176 | 301 | 511 | 720 | 887 | 847 | 712 | 435 | 147 | 30 | 1523 | 0 | 0 | 2 | 21 | 103 | 278 | 422 | 382 | 266 | 48 | 1 | 0 | 20536 | 0 | 1 | 56 | 434 | 1481 | 3789 | 5646 | 4972 | 3331 | 795 | 31 | 0 | 10742 | 0 | 0 | 5 | 115 | 610 | 2046 | 3259 | 2772 | 1691 | 242 | 2 | 0 | 6.8 | 6.5 | 7.5 | 7.7 | 7.6 | 7.6 | 7.3 | 6.7 | 6.2 | 6.1 | 6 | 5.9 | 6.7 | 26.9 | 5.3 | 4.5 | 4.2 | 1.8 | 1.3 | 0.4 | 0 | 0.1 | 0.2 | 1.3 | 2.3 | 5.4 | 44 | 14.2 | 12.2 | 13.4 | 6.2 | 4.7 | 1.6 | 0.2 | 0.9 | 0.7 | 4.1 | 5.6 | 12.2 | 8.9 | 0.5 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 8 | 3.6 | 3.2 | 3.7 | 1.5 | 1.3 | 0.5 | 0 | 0.2 | 0.2 | 1.1 | 1.6 | 3.5 | 66.5 | 71.9 | 80.3 | 88.1 | 96.8 | 104.3 | 104.3 | 104.1 | 100.6 | 91.5 | 77.5 | 64.2 | 52.8 | 57.8 | 61.6 | 63.8 | 69.4 | 71.8 | 71.3 | 70 | 70 | 63.8 | 59.3 | 53.8 | 62.1 | 68 | 74.8 | 83.4 | 91 | 99.8 | 100.8 | 99.9 | 96.5 | 86.1 | 73.4 | 61 | 53 | 56.7 | 59.2 | 63 | 65.5 | 70 | 70 | 69.6 | 67.2 | 62.4 | 58 | 53.3 | 59.3 | 64.1 | 71.3 | 79.4 | 87.1 | 95.5 | 98 | 96.5 | 93.3 | 82 | 69.3 | 58.6 | 53.1 | 54.7 | 57.6 | 61.1 | 64.6 | 67.8 | 69.4 | 68.3 | 66.3 | 60.4 | 56.2 | 52.6 | 56.9 | 61.1 | 67.5 | 74.8 | 82.2 | 91.2 | 94.8 | 93.3 | 90.1 | 78.6 | 64.6 | 56.1 | 51.9 | 53.7 | 55.9 | 59.4 | 62.8 | 66.4 | 68.9 | 67.5 | 65.3 | 59.2 | 55 | 51.1 | 59.2 | 61.1 | 63.8 | 68.1 | 71.9 | 75.4 | 75.6 | 73.5 | 72.4 | 67 | 62.6 | 59.2 | 60.3 | 67.2 | 74.5 | 82.2 | 90.5 | 98.3 | 97.4 | 98.5 | 95.7 | 83.7 | 69.9 | 60.6 | 56.5 | 58.9 | 61.1 | 64.4 | 68.8 | 72.5 | 73.2 | 71.5 | 69.7 | 64.4 | 60.5 | 56.8 | 59.3 | 64.2 | 71.2 | 79.4 | 86.8 | 93.8 | 96 | 95.2 | 90.7 | 80.3 | 68.2 | 58.6 | 54.5 | 57 | 59.1 | 62.3 | 66.2 | 70.3 | 71.4 | 70 | 68 | 62.7 | 58.8 | 54.6 | 57 | 62 | 67.9 | 76.3 | 83.6 | 90.8 | 93.3 | 92.7 | 89.2 | 76.9 | 65.7 | 56.6 | 52.9 | 55.1 | 57.2 | 60.4 | 63.9 | 68.2 | 69.8 | 68.5 | 66.3 | 61.1 | 56.9 | 52.7 | 55.4 | 59.6 | 65 | 72.6 | 79.5 | 88.2 | 91.7 | 90.4 | 86.9 | 74 | 63.1 | 54.7 | 15.6 | 17.9 | 20.6 | 24.3 | 25.9 | 29.4 | 31.5 | 31.2 | 29.6 | 26.6 | 20.1 | 16.1 | 20.5 | 23.8 | 28.4 | 32.3 | 32.8 | 34.5 | 34.2 | 34.2 | 34.5 | 32.8 | 27.2 | 19.3 | 13.1 | 14.1 | 15.2 | 15.1 | 13 | 12.7 | 13.6 | 13.8 | 13.7 | 14.2 | 13.7 | 12 | 13.4 | 19.2 | 24.2 | 28.9 | 30.2 | 32.3 | 32 | 32.3 | 31.5 | 27.1 | 20.6 | 11.8 | 9.9 | 12.3 | 14.2 | 14.9 | 13.2 | 12.2 | 13.6 | 13.6 | 13.1 | 12.5 | 11.6 | 8.9 | 0.323 | 0.326 | 0.35 | 0.358 | 0.371 | 0.363 | 0.361 | 0.345 | 0.353 | 0.345 | 0.324 | 0.335 | 2.505 | 2.505 | 2.429 | 2.401 | 2.391 | 2.421 | 2.415 | 2.454 | 2.44 | 2.462 | 2.51 | 2.454 | 270 | 285 | 288 | 291 | 288 | 289 | 289 | 292 | 283 | 274 | 267 | 254 | 25 | 28 | 33 | 36 | 38 | 36 | 36 | 34 | 33 | 29 | 24 | 24 | 679 | 987 | 1407 | 1885 | 2314 | 2612 | 2616 | 2336 | 1880 | 1307 | 821 | 595 | 123 | 134 | 164 | 178 | 154 | 114 | 81 | 78 | 70 | 96 | 68 | 103 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.74 | N/A | -2.03 | N/A | N/A | N/A | N/A | -193 | 247 | 79 | 41
4 | USA | CA | YUBA COUNTY AP | 724838 | 93205 | 39.102 | -121.568 | 62 | 14.66 | -8 | NAP | 00-19 | 3A | 1 | 30.2 | 33.3 | 19.1 | 14.4 | 51.5 | 22.9 | 17.3 | 50.1 | 27.8 | 51.2 | 24.4 | 52.8 | 1.7 | 340 | 0.471 | 7 | 33.3 | 101.8 | 69.6 | 99.1 | 69.1 | 96.5 | 68 | 72.5 | 96 | 70.9 | 94.1 | 69.4 | 92.3 | 6.8 | 210 | 63.7 | 88.6 | 83.4 | 62.3 | 84 | 81.5 | 60.7 | 79.5 | 79.7 | 36.1 | 96.1 | 34.6 | 94.3 | 33.5 | 92.6 | 85.3 | 22.4 | 18.9 | 16.7 | 25.8 | 107.4 | 3.1 | 2 | 23.5 | 108.9 | 21.7 | 110.1 | 20 | 111.2 | 17.8 | 112.7 | 24.6 | 75.7 | 3.1 | 2.8 | 22.4 | 77.7 | 20.6 | 79.4 | 18.8 | 80.9 | 16.6 | 83 | 62.4 | 47.3 | 50.8 | 55.5 | 59.4 | 67.4 | 74.6 | 78.8 | 76.9 | 72.8 | 63.9 | 53.3 | 47.1 | 12.42 | 4.63 | 4.64 | 5.42 | 6.28 | 6.21 | 6.23 | 4.85 | 4.22 | 5.36 | 5.43 | 5.68 | 5.09 | 316 | 109 | 42 | 12 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 119 | 2481 | 550 | 397 | 297 | 189 | 44 | 6 | 0 | 0 | 6 | 84 | 353 | 555 | 4838 | 24 | 66 | 182 | 286 | 539 | 739 | 894 | 834 | 683 | 432 | 130 | 29 | 1525 | 0 | 0 | 3 | 22 | 117 | 295 | 429 | 369 | 238 | 51 | 1 | 0 | 20920 | 0 | 1 | 86 | 440 | 1790 | 4058 | 5812 | 4764 | 3079 | 862 | 28 | 0 | 11378 | 0 | 0 | 6 | 136 | 789 | 2269 | 3512 | 2756 | 1629 | 280 | 1 | 0 | 6.6 | 5.6 | 7 | 7.4 | 7.5 | 7.8 | 7.5 | 6.8 | 6.3 | 5.8 | 5.8 | 5.3 | 6.3 | 21.2 | 4.3 | 3.5 | 3.2 | 1.6 | 0.7 | 0.2 | 0 | 0.1 | 0.3 | 1.3 | 3.1 | 3.7 | 46.3 | 12 | 9.5 | 11.2 | 4.7 | 3.8 | 1.7 | 1.7 | 1 | 1.9 | 9.3 | 7.4 | 14.1 | 7.4 | 0.5 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2 | 2.8 | 2.7 | 2.4 | 1.3 | 0.9 | 0.4 | 0.2 | 0.2 | 0.4 | 1.6 | 2 | 2.7 | 68.1 | 72.4 | 80.9 | 89.2 | 97.5 | 105.1 | 106.2 | 104 | 100.9 | 92.7 | 77.4 | 64 | 50.8 | 57.1 | 61 | 64.2 | 68.2 | 70.9 | 71.6 | 68.7 | 67 | 64.1 | 59.4 | 53.7 | 62.8 | 68.2 | 76.3 | 83.9 | 92.6 | 100.2 | 102 | 99.7 | 97.2 | 86.6 | 73.1 | 61.1 | 51.5 | 55.5 | 59.3 | 62.1 | 66.2 | 69.3 | 70.4 | 69.2 | 66.5 | 61.9 | 57.5 | 52.9 | 59 | 64.2 | 72.4 | 79.3 | 88.8 | 96.6 | 99.1 | 96.9 | 93.4 | 82.4 | 68.7 | 58.7 | 51.3 | 52.9 | 57.4 | 60.3 | 63.7 | 67.5 | 69.8 | 68.3 | 65.9 | 60.3 | 55.2 | 52.1 | 55.9 | 61.2 | 68.1 | 73.8 | 84 | 92.3 | 96 | 93.3 | 90.1 | 79 | 64.2 | 56.2 | 50.3 | 52.2 | 55.5 | 58.2 | 62.5 | 66.1 | 68.8 | 67.3 | 64.9 | 59.2 | 54.2 | 50.8 | 57.1 | 59.8 | 63.3 | 67 | 71 | 74.1 | 75.4 | 72.9 | 71.2 | 66.8 | 62.1 | 58.8 | 61.2 | 67.2 | 77 | 84.3 | 90.7 | 97 | 99.2 | 96.8 | 93.2 | 85.4 | 72.6 | 61.8 | 54.4 | 57.4 | 60.9 | 63.9 | 68.1 | 71.4 | 73.1 | 71.1 | 68.9 | 64.4 | 59.7 | 56.2 | 57.9 | 64.6 | 73.1 | 80.3 | 88.8 | 94.3 | 97.2 | 94.8 | 91.8 | 82.1 | 68.3 | 58.8 | 53 | 55.4 | 59 | 61.7 | 65.9 | 69.4 | 71.3 | 69.5 | 67.3 | 62.5 | 57.7 | 54.1 | 56.4 | 62.1 | 69.4 | 76.3 | 84.8 | 92 | 95 | 92.9 | 89.7 | 78.2 | 64.8 | 56.4 | 51.2 | 53.5 | 56.9 | 59.4 | 63.8 | 67.7 | 69.7 | 68.3 | 65.7 | 60.6 | 56 | 52.4 | 55.3 | 58.8 | 65.8 | 71.9 | 81.2 | 89.2 | 92.8 | 90.8 | 87.1 | 74.4 | 62.3 | 54.7 | 17 | 19.3 | 21.3 | 24.2 | 28 | 31.2 | 33.3 | 33.3 | 31.9 | 27.5 | 21.2 | 16.4 | 24.4 | 26.1 | 29.3 | 33 | 34.9 | 36.1 | 35.9 | 36.7 | 37.5 | 34.4 | 28 | 20 | 14.8 | 14.9 | 15 | 14.6 | 13 | 12.1 | 12.7 | 13.5 | 13.9 | 14.1 | 14.2 | 12.3 | 16.6 | 21.4 | 25.7 | 30.3 | 33 | 34 | 33.9 | 34 | 34.4 | 29.5 | 22.6 | 11.2 | 11.3 | 13.1 | 14 | 14.3 | 13.4 | 12.7 | 13.5 | 13.4 | 13.6 | 12.7 | 12.8 | 8.2 | 0.322 | 0.325 | 0.342 | 0.355 | 0.365 | 0.359 | 0.358 | 0.342 | 0.348 | 0.34 | 0.322 | 0.33 | 2.511 | 2.51 | 2.456 | 2.409 | 2.41 | 2.431 | 2.416 | 2.457 | 2.449 | 2.476 | 2.517 | 2.48 | 271 | 286 | 291 | 292 | 290 | 291 | 290 | 293 | 285 | 276 | 268 | 257 | 24 | 28 | 32 | 36 | 37 | 36 | 36 | 34 | 32 | 28 | 24 | 24 | 677 | 989 | 1412 | 1891 | 2319 | 2609 | 2613 | 2332 | 1879 | 1307 | 822 | 595 | 124 | 134 | 162 | 176 | 150 | 112 | 78 | 77 | 69 | 95 | 68 | 103 | 0.7 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.74 | N/A | -2.03 | N/A | N/A | N/A | N/A | -198 | 250 | 81 | 43
4 | USA | CA | SACRAMENTO INTL | 724839 | 93225 | 38.696 | -121.59 | 23 | 14.68 | -8 | NAP | 94-19 | 3A | 12 | 30.8 | 33.6 | 20.7 | 15.5 | 50.8 | 24.8 | 18.9 | 50.8 | 29.5 | 54.3 | 26.5 | 54.2 | 3 | 320 | 0.494 | 7 | 32.6 | 100.3 | 70.1 | 97.5 | 69.1 | 94.6 | 67.8 | 72.6 | 95.7 | 71 | 93.4 | 69.4 | 90.9 | 6.9 | 200 | 63.8 | 88.8 | 84.1 | 62.4 | 84.5 | 82.3 | 60.8 | 79.8 | 79.8 | 36.2 | 95.4 | 34.6 | 93.7 | 33.4 | 91 | 80.1 | 23.8 | 19.7 | 17.3 | 26.8 | 105.9 | 3.5 | 2.2 | 24.3 | 107.5 | 22.3 | 108.8 | 20.3 | 110 | 17.8 | 111.6 | 25.8 | 75.5 | 3.7 | 2.4 | 23.1 | 77.2 | 20.9 | 78.6 | 18.8 | 79.9 | 16.1 | 81.7 | 61.9 | 47.5 | 50.8 | 55.3 | 59.4 | 66.5 | 73.1 | 76.8 | 75.8 | 72.4 | 63.9 | 53.6 | 47.3 | 11.84 | 4.74 | 4.61 | 5.21 | 6.01 | 6.28 | 5.95 | 4.91 | 4.61 | 5.09 | 5.36 | 5.57 | 5.38 | 309 | 105 | 42 | 13 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 119 | 2475 | 541 | 398 | 304 | 187 | 56 | 6 | 0 | 0 | 6 | 85 | 342 | 550 | 4657 | 28 | 64 | 175 | 285 | 511 | 693 | 830 | 800 | 671 | 431 | 135 | 34 | 1348 | 0 | 0 | 1 | 18 | 102 | 249 | 365 | 335 | 227 | 50 | 1 | 0 | 17645 | 0 | 0 | 63 | 406 | 1520 | 3280 | 4557 | 4080 | 2854 | 854 | 31 | 0 | 9195 | 0 | 0 | 4 | 118 | 661 | 1737 | 2630 | 2295 | 1461 | 288 | 1 | 0 | 7.5 | 6.5 | 7.6 | 7.7 | 8.2 | 8.6 | 8.7 | 8.6 | 8.1 | 7 | 6.7 | 6 | 6.9 | 17.6 | 2.9 | 2.9 | 2.4 | 1.3 | 0.6 | 0.2 | 0 | 0 | 0.1 | 0.9 | 1.7 | 3.9 | 24.4 | 8.7 | 6.2 | 7.4 | 3.7 | 1.6 | 1.4 | 0 | 0.7 | 0.6 | 3.5 | 3.9 | 9.4 | 6.2 | 0 | 0.1 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 2.2 | 1.8 | 2 | 1 | 0.5 | 0.4 | 0 | 0.2 | 0.2 | 1.1 | 0.9 | 2.8 | 66.1 | 71.4 | 79.7 | 89 | 97.1 | 103.1 | 104.7 | 103.7 | 99.7 | 93 | 78 | 65.1 | 53.1 | 57.3 | 62.1 | 63.5 | 68.5 | 71 | 72.2 | 70 | 68.2 | 64.5 | 59.5 | 55.5 | 61.9 | 66.8 | 75.1 | 83.3 | 91.9 | 98.8 | 100.3 | 99.4 | 96.3 | 86.8 | 73.1 | 61.5 | 53.4 | 56.5 | 59.6 | 61.1 | 65.7 | 69.7 | 70.8 | 69.8 | 66.9 | 62.5 | 58.2 | 54.4 | 58.8 | 63.3 | 71.8 | 78.9 | 87.8 | 94.3 | 97.1 | 95.7 | 92.6 | 82.5 | 68.7 | 59 | 52.5 | 54.5 | 58 | 60 | 63.8 | 67.5 | 69.7 | 68.4 | 66 | 60.7 | 56.1 | 52.9 | 56 | 60.3 | 67.5 | 73.6 | 82.4 | 90.1 | 93.3 | 91.9 | 89.3 | 78.8 | 64.2 | 56.6 | 51.2 | 53.3 | 56.1 | 58.1 | 62.2 | 66.4 | 68.6 | 67.3 | 65 | 59.3 | 55 | 51.5 | 59 | 60.8 | 64.9 | 66.5 | 70.9 | 74 | 75.4 | 74.1 | 71.8 | 67.8 | 63.1 | 59.6 | 62.1 | 66.5 | 75.7 | 82.9 | 90.2 | 97 | 99.4 | 98.3 | 94.1 | 86.9 | 74.1 | 62.6 | 55.9 | 58.6 | 61.7 | 63.6 | 68 | 71.4 | 73 | 71.3 | 69 | 64.8 | 60.4 | 57 | 59.2 | 64.3 | 72 | 78.8 | 88.3 | 94.1 | 96.1 | 95.4 | 90.7 | 81.8 | 68.8 | 59.9 | 53.7 | 56.3 | 59.4 | 61.5 | 65.8 | 69.4 | 71.2 | 69.6 | 67.4 | 62.7 | 58.5 | 54.8 | 56.4 | 61.4 | 68.7 | 75.5 | 84.8 | 90.4 | 93.6 | 92 | 88.7 | 78.1 | 65.4 | 57.2 | 52.1 | 54.3 | 57.3 | 59.6 | 63.5 | 67.6 | 69.5 | 68.3 | 65.9 | 60.9 | 56.6 | 52.6 | 55.2 | 58.7 | 65.3 | 72 | 80.4 | 87.8 | 90.8 | 89.7 | 86.3 | 74.8 | 62.7 | 55.2 | 15.6 | 17.8 | 21.3 | 24.3 | 27.1 | 30.3 | 32.6 | 32.5 | 31.3 | 27.9 | 20.7 | 16 | 21.6 | 23.7 | 29.2 | 33.1 | 34.9 | 36.1 | 36.1 | 36.8 | 36.8 | 34.9 | 27.9 | 19.1 | 13.8 | 14.5 | 15.8 | 15.1 | 13.7 | 13.3 | 13.7 | 13.2 | 13.4 | 14.7 | 14.6 | 12.1 | 14.1 | 19.4 | 25.7 | 29.7 | 32.7 | 33.9 | 34.5 | 34.4 | 33.8 | 30.3 | 22 | 11.1 | 10.2 | 12.7 | 14.9 | 14.7 | 14.1 | 13.8 | 14.2 | 13.1 | 13.2 | 13.7 | 13 | 8.2 | 0.322 | 0.325 | 0.338 | 0.354 | 0.364 | 0.36 | 0.361 | 0.344 | 0.349 | 0.343 | 0.327 | 0.331 | 2.511 | 2.509 | 2.461 | 2.405 | 2.402 | 2.42 | 2.406 | 2.446 | 2.442 | 2.468 | 2.5 | 2.479 | 272 | 287 | 293 | 293 | 290 | 290 | 289 | 292 | 285 | 275 | 267 | 258 | 25 | 28 | 32 | 36 | 37 | 36 | 37 | 35 | 33 | 29 | 25 | 24 | 685 | 1014 | 1446 | 1923 | 2339 | 2611 | 2602 | 2327 | 1885 | 1326 | 846 | 610 | 128 | 131 | 153 | 166 | 141 | 106 | 75 | 74 | 65 | 89 | 62 | 103 | N/A | N/A | -2.09 | N/A | -1.03 | -1.15 | N/A | N/A | N/A | N/A | 0.72 | N/A | -1.94 | N/A | N/A | N/A | N/A | -209 | 248 | 76 | 47
4 | USA | CA | MONTEREY | 724915 | 23259 | 36.588 | -121.845 | 165 | 14.61 | -8 | NAP | 98-19 | 3C | 12 | 36.8 | 38.9 | 21 | 15.9 | 48.7 | 25.1 | 19.3 | 49.3 | 20.5 | 54.7 | 17.9 | 55.7 | 4.9 | 100 | 0.473 | 9 | 14.1 | 79.2 | 60 | 74.5 | 59.4 | 71.6 | 59.2 | 63.4 | 72.5 | 62.2 | 70.6 | 61.2 | 68.8 | 5.7 | 310 | 60.3 | 78.6 | 65.8 | 58.7 | 74.2 | 64.7 | 57.4 | 70.8 | 63.7 | 28.8 | 72.2 | 27.9 | 70.5 | 27.1 | 68.8 | 82.2 | 16.9 | 14.8 | 12.6 | 32.7 | 90 | 2.3 | 5.1 | 31 | 93.7 | 29.7 | 96.6 | 28.4 | 99.5 | 26.8 | 103.2 | 29.4 | 67.4 | 2.4 | 4.4 | 27.6 | 70.6 | 26.2 | 73.2 | 24.8 | 75.7 | 23.1 | 78.9 | 56.7 | 52.1 | 52.7 | 53.7 | 54.7 | 56.8 | 59.4 | 60.6 | 61.5 | 61.8 | 59.5 | 55.2 | 51.6 | 5.43 | 4.64 | 4.57 | 4.05 | 4.09 | 3.39 | 3.35 | 2.88 | 3.05 | 4.2 | 4.71 | 4.43 | 4.42 | 103 | 31 | 20 | 9 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 34 | 3113 | 402 | 346 | 351 | 314 | 257 | 175 | 139 | 116 | 117 | 185 | 296 | 415 | 2530 | 94 | 95 | 124 | 143 | 211 | 281 | 330 | 357 | 353 | 296 | 163 | 83 | 64 | 0 | 0 | 1 | 4 | 4 | 5 | 4 | 9 | 20 | 15 | 2 | 0 | 462 | 7 | 8 | 10 | 43 | 34 | 53 | 11 | 31 | 122 | 120 | 23 | 0 | 126 | 1 | 1 | 1 | 12 | 11 | 20 | 0 | 4 | 39 | 33 | 4 | 0 | 5.8 | 4.9 | 5.7 | 6 | 6.8 | 7 | 6.9 | 6.4 | 5.9 | 5.1 | 4.8 | 4.7 | 5.1 | 17.9 | 3.6 | 3.5 | 2.7 | 1.3 | 0.5 | 0.2 | 0 | 0 | 0 | 0.9 | 1.8 | 3.3 | 35.8 | 11.8 | 14.1 | 8.4 | 3.8 | 2.4 | 1.1 | 0.1 | 0.2 | 0.4 | 3.5 | 6.4 | 8.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3.1 | 2.8 | 2.3 | 1.1 | 0.6 | 0.2 | 0 | 0 | 0.1 | 1.1 | 1.5 | 2.2 | 73.7 | 74.5 | 74.1 | 80.1 | 78.6 | 81.1 | 75.2 | 78 | 85.2 | 84.1 | 77.2 | 69.5 | 54.3 | 57 | 56.5 | 59 | 58.9 | 60.9 | 62.7 | 62.9 | 63.7 | 60.2 | 58.3 | 53.5 | 67 | 67.9 | 67.3 | 69.7 | 69.2 | 72.3 | 71.5 | 72.5 | 76.5 | 76.6 | 69.9 | 64.5 | 52.7 | 55.2 | 55.3 | 56.4 | 57.6 | 60.2 | 61.2 | 61.6 | 61.4 | 58.3 | 56 | 54.5 | 63.1 | 63.6 | 63.7 | 64.2 | 65.2 | 68.3 | 68.5 | 69.8 | 72.2 | 71 | 65.8 | 62.2 | 53.4 | 54.1 | 54.7 | 54.9 | 56.3 | 58.9 | 60.1 | 60.9 | 60.6 | 57.9 | 55.5 | 54.5 | 59.8 | 60.5 | 61.1 | 61.4 | 63 | 65.5 | 65.9 | 67.1 | 69.3 | 67.3 | 63.1 | 59.7 | 53.1 | 53.4 | 54 | 53.6 | 55.5 | 57.5 | 58.9 | 59.9 | 60 | 57.2 | 55.3 | 53.2 | 58.7 | 60.3 | 60 | 60.8 | 61.9 | 63.8 | 63.8 | 64.5 | 66.2 | 63.7 | 61.9 | 60.1 | 62.9 | 66.2 | 69.1 | 74.4 | 72.5 | 76.5 | 73.2 | 73.3 | 77.6 | 73 | 67.5 | 63.5 | 57 | 57.8 | 57.9 | 57.8 | 59 | 61.1 | 61.9 | 62.7 | 63.4 | 61.9 | 59.5 | 58.1 | 61.3 | 64.1 | 64.2 | 66.4 | 66.6 | 70.1 | 70 | 70.3 | 72.6 | 70 | 65.6 | 61.7 | 55.3 | 55.9 | 56.3 | 56.1 | 57.2 | 59.4 | 60.5 | 61.4 | 62 | 60.2 | 57.9 | 56.4 | 60.2 | 61.6 | 61.9 | 63.1 | 64.1 | 66.9 | 67.1 | 68.7 | 70.3 | 67.8 | 63.7 | 60 | 53.7 | 54.2 | 54.6 | 54.4 | 55.8 | 58.1 | 59.3 | 60.2 | 60.5 | 58.7 | 56.4 | 54.5 | 58.8 | 59.3 | 59.8 | 60.5 | 62.1 | 64.6 | 64.9 | 66.3 | 67.8 | 65.8 | 61.7 | 58.2 | 16.3 | 14.8 | 14.3 | 13.3 | 12.3 | 12.9 | 11.8 | 11.9 | 14.1 | 16 | 16.2 | 15.8 | 21.9 | 21 | 19.6 | 19.5 | 17.8 | 18.8 | 15.4 | 15.5 | 20.8 | 23.6 | 21.3 | 19 | 13.1 | 12.2 | 11.4 | 10.9 | 9.4 | 9.5 | 7.4 | 7.8 | 10.6 | 12.9 | 12.4 | 11.7 | 16.5 | 17.1 | 16.8 | 17.1 | 16.3 | 17.2 | 14.7 | 14.6 | 18.3 | 18.8 | 16.8 | 13.4 | 10.8 | 10.7 | 10.5 | 10.1 | 9.1 | 9 | 7.1 | 7.5 | 9.5 | 11.1 | 10.8 | 9.5 | 0.317 | 0.321 | 0.326 | 0.349 | 0.359 | 0.349 | 0.353 | 0.336 | 0.345 | 0.323 | 0.31 | 0.314 | 2.567 | 2.562 | 2.545 | 2.461 | 2.447 | 2.487 | 2.496 | 2.536 | 2.504 | 2.591 | 2.593 | 2.587 | 280 | 292 | 299 | 296 | 292 | 294 | 292 | 296 | 289 | 287 | 281 | 274 | 24 | 27 | 30 | 35 | 36 | 35 | 34 | 32 | 31 | 26 | 23 | 23 | 836 | 1109 | 1558 | 1967 | 2245 | 2422 | 2234 | 2018 | 1761 | 1333 | 958 | 735 | 89 | 119 | 124 | 164 | 136 | 106 | 75 | 93 | 74 | 80 | 51 | 90 | 0.86 | N/A | -2.84 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.72 | N/A | -2.18 | N/A | N/A | N/A | N/A | -223 | 263 | 63 | 37
4 | USA | CA | STOCKTON | 724920 | 23237 | 37.889 | -121.226 | 26 | 14.68 | -8 | NAP | 94-19 | 3A | 12 | 30.7 | 33.1 | 21.8 | 16.4 | 51 | 25.3 | 19.3 | 48.8 | 26.6 | 54.6 | 24.1 | 53.3 | 2.9 | 130 | 0.495 | 7 | 32.8 | 101.5 | 69.7 | 98.3 | 68.8 | 95.3 | 68 | 73.1 | 96 | 70.8 | 94.2 | 69.1 | 91.9 | 10 | 310 | 64.5 | 91 | 84.5 | 61.7 | 82.2 | 80 | 59.9 | 77.2 | 77.7 | 36.6 | 96 | 34.5 | 94.5 | 33.1 | 92 | 88.9 | 22.6 | 19.3 | 17.2 | 26.8 | 107 | 3.2 | 2.5 | 24.5 | 108.8 | 22.6 | 110.3 | 20.8 | 111.7 | 18.4 | 113.5 | 25.5 | 76.4 | 3.5 | 5.5 | 23 | 80.4 | 20.9 | 83.6 | 19 | 86.7 | 16.5 | 90.7 | 62.4 | 47.7 | 51.3 | 55.7 | 60 | 66.7 | 73.4 | 77.4 | 76.4 | 73 | 64.5 | 54.2 | 47.5 | 11.9 | 4.9 | 4.55 | 5.13 | 5.89 | 6.07 | 6.02 | 5.13 | 4.63 | 5.07 | 5.15 | 5.45 | 5.28 | 286 | 102 | 36 | 10 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 114 | 2377 | 535 | 385 | 288 | 170 | 50 | 5 | 0 | 0 | 3 | 71 | 326 | 544 | 4802 | 32 | 71 | 188 | 302 | 518 | 701 | 850 | 820 | 690 | 449 | 146 | 35 | 1419 | 0 | 0 | 1 | 20 | 103 | 256 | 385 | 355 | 244 | 54 | 1 | 0 | 19026 | 0 | 1 | 77 | 459 | 1586 | 3474 | 5061 | 4452 | 3008 | 871 | 37 | 0 | 9999 | 0 | 0 | 6 | 140 | 703 | 1881 | 2955 | 2497 | 1532 | 284 | 1 | 0 | 7.5 | 6.1 | 7 | 7.3 | 8.6 | 9.5 | 9.6 | 8.5 | 8 | 7.2 | 6.1 | 5.4 | 6.4 | 14 | 2.8 | 2.4 | 2 | 1 | 0.4 | 0.1 | 0 | 0 | 0.3 | 0.7 | 2 | 2 | 26.7 | 7 | 8.2 | 6.5 | 3.1 | 3.7 | 0.7 | 0.6 | 0.8 | 2.5 | 2.7 | 6.2 | 5.3 | 5.6 | 0.2 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4 | 2 | 1.9 | 1.5 | 0.8 | 0.7 | 0.1 | 0.1 | 0.2 | 0.6 | 0.7 | 1.6 | 1.4 | 66.1 | 72.2 | 80.2 | 90.3 | 98.2 | 104 | 105.5 | 103.8 | 100.4 | 92.7 | 78.2 | 65.2 | 54.9 | 58 | 62 | 65 | 68.3 | 70.7 | 71.9 | 70.6 | 69.1 | 65.5 | 60 | 56.4 | 62.4 | 67.7 | 76 | 83.9 | 92.4 | 99.5 | 101.5 | 99.8 | 96.6 | 86.8 | 73.9 | 61.9 | 54.1 | 56.5 | 59.9 | 62.4 | 66 | 69.3 | 70 | 69.2 | 68.4 | 63.4 | 58.6 | 54.4 | 59.3 | 64.3 | 72.5 | 79.5 | 87.9 | 95.1 | 97.8 | 96.4 | 93.1 | 82.7 | 69.5 | 59.2 | 52.9 | 54.5 | 58 | 60.3 | 63.7 | 67.1 | 69.2 | 68.2 | 66.8 | 61.1 | 57.1 | 53.3 | 56.6 | 61.1 | 68.5 | 74.9 | 83 | 90.7 | 94.4 | 92.7 | 89.3 | 78.8 | 65.4 | 56.8 | 51.6 | 53.5 | 56.5 | 58.5 | 62 | 65.7 | 68.6 | 67.3 | 65.4 | 60.1 | 54.9 | 51.7 | 59.1 | 61 | 64.4 | 67.3 | 71.7 | 73.6 | 78.8 | 75.2 | 78.4 | 67.8 | 63.3 | 59.8 | 62.6 | 67.5 | 76.5 | 83.2 | 90.7 | 100.2 | 95.9 | 97.1 | 92.3 | 86.9 | 74 | 63.3 | 56.1 | 58.6 | 61.7 | 64.1 | 67.6 | 70.7 | 73 | 71.5 | 70.7 | 65.2 | 60.5 | 57.1 | 59.5 | 64.9 | 73.1 | 80.4 | 89.3 | 95.3 | 96.5 | 95.7 | 90.4 | 83 | 70.1 | 59.9 | 54 | 56.5 | 59.5 | 61.8 | 65.2 | 68.7 | 70.6 | 69.4 | 68 | 63.3 | 58.6 | 54.8 | 57.3 | 62.3 | 69.6 | 76.9 | 85.4 | 91.7 | 94.7 | 92.4 | 88.5 | 79.1 | 66.5 | 57.3 | 52.3 | 54.5 | 57.4 | 59.5 | 63 | 66.8 | 68.9 | 67.9 | 66.2 | 61.4 | 56.8 | 52.6 | 55.6 | 59.8 | 66.5 | 72.2 | 80.8 | 88.4 | 92.4 | 90.2 | 86.7 | 75.6 | 63.6 | 55.6 | 16.1 | 19.4 | 22.7 | 25.1 | 28 | 31.1 | 32.8 | 32.2 | 30.9 | 27.6 | 21.7 | 16.9 | 21.3 | 25.1 | 29.3 | 33.7 | 35.8 | 37.1 | 36.5 | 36.1 | 36.3 | 34 | 28 | 20 | 13.5 | 14.7 | 15.3 | 15.1 | 14.5 | 14 | 13.8 | 13.6 | 14.4 | 14.8 | 15 | 12.7 | 15.3 | 21.1 | 26.2 | 30.5 | 33.7 | 34.6 | 34.6 | 33.7 | 32.7 | 30.1 | 23.3 | 12.8 | 10.5 | 13.2 | 14.6 | 15 | 15.4 | 14.1 | 15.1 | 13.9 | 14.7 | 14.2 | 13.3 | 8.9 | 0.333 | 0.331 | 0.343 | 0.362 | 0.365 | 0.362 | 0.368 | 0.352 | 0.355 | 0.353 | 0.342 | 0.332 | 2.469 | 2.486 | 2.439 | 2.38 | 2.391 | 2.411 | 2.402 | 2.431 | 2.425 | 2.439 | 2.445 | 2.478 | 268 | 285 | 292 | 291 | 290 | 290 | 287 | 290 | 284 | 273 | 262 | 260 | 26 | 29 | 33 | 37 | 38 | 37 | 37 | 35 | 33 | 30 | 26 | 24 | 729 | 1051 | 1499 | 1953 | 2355 | 2636 | 2601 | 2342 | 1910 | 1368 | 896 | 656 | 117 | 129 | 150 | 170 | 137 | 98 | 70 | 64 | 62 | 84 | 57 | 101 | N/A | N/A | N/A | N/A | -1.12 | N/A | N/A | N/A | N/A | N/A | 0.72 | N/A | -2.02 | N/A | N/A | N/A | N/A | -211 | 239 | 54 | 49
4 | USA | CA | MODESTO CITY | 724926 | 23258 | 37.624 | -120.951 | 73 | 14.66 | -8 | NAP | 98-19 | 3B | 12 | 31.2 | 33.7 | 21 | 15.8 | 55.6 | 24.7 | 18.9 | 54.4 | 22.5 | 53.7 | 19.6 | 52.3 | 2.3 | 120 | 0.464 | 7 | 30.2 | 101.7 | 69.4 | 98.6 | 68.3 | 95.8 | 67.2 | 71.6 | 96.3 | 70 | 94.3 | 68.7 | 92.3 | 9.9 | 330 | 62.4 | 84.5 | 82.6 | 60.5 | 78.8 | 79.6 | 58.8 | 74.3 | 77.6 | 35.3 | 96.4 | 33.9 | 94.4 | 32.8 | 92.4 | 79 | 19 | 17 | 15.4 | 27.4 | 106.6 | 2.2 | 2.5 | 25.8 | 108.4 | 24.5 | 109.8 | 23.3 | 111.2 | 21.7 | 113 | 26.6 | 73.8 | 2.3 | 2 | 25 | 75.2 | 23.6 | 76.4 | 22.3 | 77.6 | 20.7 | 79.1 | 63.4 | 47.7 | 51.8 | 56.9 | 61.3 | 68.5 | 75.3 | 79.6 | 78.1 | 74 | 64.9 | 54.6 | 47.7 | 12.5 | 4.7 | 4.61 | 5.43 | 6.28 | 6.51 | 6.46 | 5.5 | 4.67 | 5.49 | 5.22 | 5.33 | 4.97 | 261 | 100 | 31 | 7 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 104 | 2260 | 535 | 368 | 255 | 144 | 36 | 5 | 0 | 0 | 3 | 64 | 314 | 536 | 5166 | 29 | 83 | 220 | 340 | 574 | 760 | 918 | 871 | 721 | 462 | 154 | 34 | 1691 | 0 | 0 | 4 | 32 | 145 | 314 | 453 | 406 | 275 | 61 | 1 | 0 | 21782 | 0 | 1 | 113 | 544 | 1930 | 4102 | 5979 | 5041 | 3238 | 807 | 27 | 0 | 11481 | 0 | 0 | 13 | 174 | 857 | 2236 | 3515 | 2819 | 1627 | 240 | 0 | 0 | 6.5 | 4.4 | 5.5 | 6.4 | 7.6 | 8.6 | 8.8 | 8.2 | 7.7 | 6.5 | 5.5 | 4.4 | 4.9 | 12.4 | 2.2 | 1.9 | 2.1 | 1 | 0.2 | 0.1 | 0 | 0.1 | 0.3 | 0.7 | 2 | 1.7 | 27.4 | 5.7 | 5.9 | 6.5 | 3 | 1.1 | 0.5 | 0.7 | 0.7 | 2.2 | 2.4 | 6 | 3.9 | 6.4 | 0.2 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 1.6 | 1.6 | 1.7 | 0.9 | 0.2 | 0.1 | 0.2 | 0.2 | 0.6 | 0.7 | 1.5 | 1 | 66.7 | 72.9 | 81.9 | 91 | 98.2 | 104.3 | 105.9 | 103.5 | 100.4 | 91.6 | 77.4 | 65 | 53.4 | 58 | 60.8 | 64.6 | 67.6 | 70.5 | 71.2 | 69.2 | 67.5 | 64.1 | 60.5 | 55.2 | 62.6 | 69 | 77.1 | 84.8 | 93.6 | 100 | 102 | 99.6 | 96.6 | 85.9 | 73.4 | 61.6 | 53.4 | 56.4 | 59.6 | 61.6 | 65.4 | 68.6 | 69.8 | 68.6 | 66.6 | 62.5 | 58.3 | 53.3 | 59.5 | 65.2 | 73.5 | 80.5 | 89.2 | 95.9 | 98.7 | 96.4 | 93.1 | 82.1 | 69.1 | 59.1 | 52.1 | 54.4 | 58 | 59.8 | 63.2 | 66.9 | 68.8 | 67.6 | 65.9 | 60.8 | 56.7 | 52.5 | 56.7 | 62.1 | 69.4 | 75.7 | 84.4 | 91.9 | 95.5 | 93.3 | 89.6 | 78.6 | 65.2 | 56.8 | 51 | 53.2 | 56.4 | 58.2 | 61.6 | 65.5 | 67.5 | 66.9 | 64.7 | 59.7 | 54.8 | 51 | 58.3 | 60.3 | 63.8 | 66.4 | 70.1 | 73 | 74.7 | 72.7 | 72.2 | 66.7 | 63 | 59.2 | 62.1 | 67.8 | 77 | 86 | 94.5 | 100.4 | 100.5 | 98.1 | 91.7 | 84.6 | 73.7 | 62.6 | 55.2 | 58.1 | 61.3 | 63.5 | 67 | 70.3 | 71.9 | 70.5 | 69 | 64.5 | 60.3 | 56.3 | 59 | 66 | 73.9 | 81.9 | 90.1 | 95.6 | 97.4 | 94.9 | 90.3 | 81.5 | 69.7 | 59.3 | 53.4 | 56.1 | 59.4 | 61.3 | 64.8 | 68.4 | 70.2 | 69 | 67.3 | 62.8 | 58.3 | 54.1 | 57.3 | 63.4 | 70.9 | 77.2 | 86.1 | 92.4 | 94.9 | 92.9 | 89.1 | 78.2 | 66.2 | 57.2 | 51.6 | 54.2 | 57.3 | 59.3 | 62.6 | 66.7 | 68.6 | 67.7 | 65.8 | 61.1 | 56.5 | 52 | 55.6 | 60.8 | 67.5 | 73.1 | 81.6 | 89.3 | 92.8 | 90.8 | 87.2 | 75.3 | 63.3 | 55.5 | 16.3 | 19.1 | 21.4 | 23.6 | 26.7 | 29.1 | 30.2 | 29.7 | 28.4 | 25.6 | 20.7 | 16.7 | 21.9 | 24.6 | 27.7 | 31.3 | 32.7 | 33.2 | 32 | 32.4 | 33 | 31.7 | 26.5 | 20 | 13.3 | 13.8 | 12.9 | 12.5 | 11.7 | 11.4 | 11.3 | 11.3 | 10.7 | 12.1 | 13.2 | 12.2 | 15.8 | 21.5 | 25.3 | 28.6 | 30.9 | 31.6 | 30.3 | 30.5 | 30.2 | 27.5 | 22.2 | 12.8 | 10.4 | 13 | 12.6 | 12.6 | 12 | 11.8 | 11.8 | 11.4 | 10.7 | 11.1 | 11.8 | 8.8 | 0.339 | 0.335 | 0.341 | 0.358 | 0.362 | 0.355 | 0.366 | 0.35 | 0.352 | 0.353 | 0.343 | 0.326 | 2.434 | 2.465 | 2.44 | 2.393 | 2.4 | 2.43 | 2.412 | 2.437 | 2.436 | 2.436 | 2.435 | 2.492 | 266 | 284 | 293 | 292 | 291 | 292 | 288 | 291 | 285 | 273 | 262 | 264 | 27 | 30 | 33 | 37 | 37 | 36 | 37 | 35 | 33 | 30 | 27 | 24 | 736 | 1065 | 1524 | 1969 | 2366 | 2646 | 2596 | 2344 | 1918 | 1382 | 912 | 667 | 117 | 126 | 147 | 168 | 131 | 92 | 72 | 62 | 61 | 82 | 56 | 100 | 1.53 | N/A | N/A | N/A | N/A | N/A | N/A | -256 | 319 | N/A | 0.74 | N/A | N/A | N/A | N/A | N/A | N/A | -216 | 248 | 58 | 47
4 | USA | CA | LIVERMORE | 724927 | 23285 | 37.693 | -121.814 | 393 | 14.49 | -8 | NAP | 98-19 | 3A | 1 | 30.9 | 33.4 | 16.2 | 12.7 | 51.8 | 20.7 | 15.7 | 52 | 20 | 51.1 | 17.7 | 53.3 | 1.6 | 70 | 0.494 | 7 | 29.2 | 99 | 67.4 | 95 | 65.9 | 91.1 | 64.9 | 69.4 | 93.3 | 67.8 | 90.4 | 66.2 | 87.5 | 9.9 | 280 | 60.9 | 81 | 75.9 | 59.2 | 76.1 | 72.5 | 57.8 | 72.4 | 70.5 | 33.6 | 93.4 | 32.1 | 90.2 | 31 | 87.9 | 78.8 | 19.2 | 17.7 | 16.2 | 26.9 | 105.5 | 2 | 2.9 | 25.5 | 107.6 | 24.3 | 109.3 | 23.2 | 110.9 | 21.7 | 113 | 24.9 | 72.2 | 2.2 | 2.8 | 23.3 | 74.2 | 22 | 75.9 | 20.8 | 77.4 | 19.1 | 79.5 | 60.3 | 48.3 | 50.7 | 54.2 | 57.4 | 62.5 | 68.6 | 72.5 | 72.3 | 70.4 | 63.7 | 54.3 | 48.4 | 10.41 | 4.88 | 4.87 | 5.22 | 5.71 | 5.88 | 6.41 | 5.85 | 5.02 | 5.75 | 5.35 | 5.48 | 5.08 | 271 | 91 | 46 | 18 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 91 | 2587 | 517 | 400 | 334 | 239 | 122 | 28 | 5 | 3 | 14 | 88 | 322 | 515 | 4044 | 39 | 66 | 149 | 226 | 387 | 558 | 698 | 692 | 612 | 426 | 150 | 41 | 884 | 0 | 0 | 1 | 10 | 44 | 136 | 237 | 230 | 176 | 49 | 1 | 0 | 10910 | 0 | 2 | 57 | 269 | 742 | 1827 | 2703 | 2451 | 2058 | 761 | 40 | 0 | 5288 | 0 | 0 | 3 | 79 | 316 | 922 | 1412 | 1236 | 1052 | 266 | 2 | 0 | 6.2 | 4.6 | 5 | 5.5 | 6.6 | 8.1 | 8.5 | 8.6 | 7.9 | 6.3 | 5 | 4.1 | 4.6 | 14.9 | 2.9 | 2.6 | 2.2 | 1.1 | 0.4 | 0.1 | 0 | 0.1 | 0.2 | 0.8 | 2 | 2.4 | 32.4 | 6.7 | 7.3 | 6.7 | 4.6 | 2 | 0.7 | 0.7 | 0.9 | 1.5 | 3.6 | 5.4 | 7 | 6.4 | 0.3 | 0.1 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 5.2 | 2 | 1.9 | 1.7 | 1 | 0.5 | 0.2 | 0.1 | 0.2 | 0.4 | 0.9 | 1.6 | 1.7 | 68.8 | 72.8 | 79.5 | 87.9 | 95 | 102 | 103.7 | 101.9 | 100.6 | 92.7 | 78.6 | 67.2 | 51.9 | 56.4 | 60.5 | 62.8 | 65.9 | 68.8 | 69.3 | 68.1 | 66.5 | 63.7 | 58.5 | 54.9 | 64.2 | 68.5 | 74.9 | 81.5 | 88.4 | 95.8 | 97.8 | 96.7 | 96.2 | 86.5 | 73.9 | 63.4 | 52.2 | 55.2 | 58.7 | 61.5 | 63.5 | 66.6 | 67.6 | 66.4 | 65.2 | 61.1 | 57.5 | 53 | 60.9 | 64.4 | 70.5 | 75.8 | 82.4 | 90.7 | 93 | 91.8 | 91.4 | 82.2 | 69 | 60.8 | 52.2 | 54 | 56.7 | 58.7 | 60.9 | 64.9 | 66.4 | 65.6 | 63.8 | 59.3 | 55.4 | 52.8 | 57.6 | 61 | 66.2 | 70.5 | 76.4 | 84.7 | 88.2 | 87 | 86.4 | 77.8 | 65.2 | 58.3 | 50.9 | 52.2 | 54.7 | 56.4 | 59.1 | 62.9 | 65.3 | 64.6 | 62.5 | 58.1 | 53.8 | 51.5 | 57.9 | 59.7 | 63 | 65.5 | 68.2 | 70.9 | 72.7 | 71.2 | 70.9 | 66 | 62 | 59.6 | 62 | 67.2 | 76.3 | 81.9 | 91.1 | 97 | 99.2 | 96.7 | 89.6 | 85 | 72.9 | 63.4 | 55.4 | 57.4 | 60.1 | 62.4 | 64.9 | 68.2 | 69.3 | 68.4 | 67.3 | 63.5 | 59.7 | 57.2 | 59.8 | 65 | 71.7 | 78.7 | 85.2 | 92.5 | 92.9 | 91.7 | 89.7 | 81.1 | 69 | 60.8 | 53.6 | 55.3 | 58 | 59.6 | 62.2 | 66 | 67.4 | 66.6 | 65.5 | 61.7 | 57.9 | 55.1 | 57.5 | 62.5 | 68.2 | 73.4 | 79.7 | 87.9 | 89.8 | 87.6 | 87 | 77.3 | 65.4 | 58.5 | 51.8 | 53.5 | 55.8 | 57.3 | 59.8 | 63.9 | 65.8 | 65.2 | 63.9 | 59.9 | 56.2 | 52.8 | 56.5 | 59.7 | 64.2 | 68.8 | 74.1 | 82.8 | 86.6 | 84.8 | 83.4 | 73.3 | 63 | 56.2 | 18.1 | 19.2 | 21.5 | 22.6 | 23.9 | 27.4 | 29.2 | 28.9 | 28.5 | 25.9 | 21.4 | 18.3 | 23 | 25.5 | 29.4 | 32.9 | 35.1 | 37.1 | 36.1 | 36.7 | 37.6 | 34.2 | 27.1 | 22 | 13.8 | 14.9 | 15.9 | 15.8 | 15 | 14.5 | 13.2 | 13.4 | 14.6 | 14.8 | 13.9 | 13.3 | 16.7 | 21.1 | 26.5 | 29.3 | 32.1 | 34.3 | 33.6 | 32.9 | 32.6 | 28.6 | 22 | 14.3 | 11.3 | 13.2 | 15.3 | 15 | 14.6 | 14.1 | 13.2 | 12.6 | 13.2 | 13.2 | 12.6 | 9.8 | 0.32 | 0.325 | 0.339 | 0.359 | 0.365 | 0.36 | 0.365 | 0.35 | 0.35 | 0.333 | 0.325 | 0.324 | 2.527 | 2.518 | 2.459 | 2.383 | 2.388 | 2.41 | 2.398 | 2.431 | 2.426 | 2.507 | 2.51 | 2.52 | 275 | 289 | 293 | 292 | 290 | 291 | 288 | 291 | 285 | 281 | 270 | 265 | 25 | 28 | 33 | 37 | 38 | 37 | 37 | 35 | 33 | 28 | 25 | 23 | 749 | 1059 | 1503 | 1959 | 2312 | 2558 | 2480 | 2224 | 1843 | 1338 | 901 | 666 | 109 | 128 | 140 | 164 | 138 | 99 | 69 | 71 | 63 | 81 | 56 | 98 | 0.99 | N/A | N/A | N/A | N/A | N/A | -50 | -234 | 356 | 108 | N/A | N/A | -2.11 | N/A | N/A | N/A | N/A | -198 | 243 | N/A | 44
4 | USA | CA | OAKLAND INTL | 724930 | 23230 | 37.7444 | -122.2236 | 8 | 14.69 | -8 | NAP | 94-19 | 3C | 1 | 36.9 | 39.2 | 20.1 | 15.1 | 53 | 25.8 | 19.8 | 51.6 | 26.5 | 53.1 | 23.4 | 53.3 | 3.1 | 50 | 0.521 | 9 | 16.6 | 83.9 | 64.4 | 79.5 | 63.1 | 75.4 | 62.1 | 66.5 | 78.6 | 65 | 75.8 | 63.8 | 73.4 | 10.7 | 310 | 62.7 | 85.1 | 69 | 61.1 | 80.4 | 67.9 | 59.7 | 76.4 | 66.8 | 31.1 | 78.6 | 29.9 | 75.9 | 29 | 73.5 | 73.6 | 23.5 | 20 | 18.2 | 32.5 | 93.7 | 2.4 | 3.7 | 30.8 | 96.4 | 29.3 | 98.6 | 28 | 100.7 | 26.2 | 103.4 | 30 | 69.7 | 2.7 | 2.2 | 28 | 71.3 | 26.4 | 72.6 | 24.9 | 73.8 | 22.9 | 75.4 | 58.4 | 50.6 | 52.7 | 55.4 | 57.4 | 59.9 | 62.6 | 63.8 | 64.6 | 65 | 61.9 | 55.5 | 50.7 | 6.6 | 4.07 | 4.1 | 4.13 | 4.33 | 4.12 | 4.12 | 3.38 | 3.61 | 4.52 | 4.42 | 4.55 | 4.45 | 119 | 42 | 18 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 44 | 2602 | 447 | 344 | 299 | 232 | 171 | 96 | 64 | 50 | 52 | 117 | 287 | 443 | 3176 | 60 | 94 | 172 | 224 | 308 | 377 | 427 | 453 | 451 | 370 | 173 | 67 | 184 | 0 | 0 | 1 | 6 | 13 | 24 | 26 | 38 | 53 | 22 | 1 | 0 | 1207 | 0 | 1 | 11 | 53 | 108 | 193 | 125 | 170 | 360 | 178 | 8 | 0 | 346 | 0 | 0 | 1 | 9 | 31 | 63 | 31 | 49 | 120 | 42 | 0 | 0 | 8.5 | 6.6 | 7.9 | 8.7 | 9.9 | 10.4 | 10.1 | 10 | 9.4 | 8.3 | 7.1 | 6.3 | 6.9 | 17.9 | 3.7 | 2.8 | 2.8 | 1.2 | 0.2 | 0.1 | 0 | 0 | 0.2 | 1.3 | 2.7 | 2.6 | 35.5 | 9.1 | 7.2 | 8 | 5.4 | 2.4 | 1.2 | 0.7 | 0.9 | 1.5 | 8.2 | 7.9 | 6.1 | 7.2 | 0.3 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 6.9 | 2.6 | 2.1 | 2 | 1.3 | 0.4 | 0.3 | 0.2 | 0.2 | 0.4 | 1.6 | 2 | 1.5 | 66.5 | 69.6 | 75 | 80.8 | 84.1 | 87.9 | 84.1 | 86.5 | 89.9 | 84.9 | 74.1 | 65.6 | 51.3 | 57.3 | 58.2 | 61.5 | 63 | 65.3 | 66.7 | 66.2 | 65.5 | 62.1 | 59 | 53.1 | 61.7 | 65 | 69.7 | 73.2 | 75.9 | 79.3 | 77.3 | 78.5 | 82.9 | 79 | 69.3 | 62.5 | 53.9 | 54.8 | 57.4 | 58.8 | 61 | 63.4 | 64.6 | 64.6 | 64.5 | 60.4 | 57.2 | 53.9 | 59.1 | 62.2 | 65.6 | 68.3 | 70.4 | 73.6 | 72.8 | 73.6 | 77.5 | 74 | 65.4 | 60.1 | 53.1 | 53.8 | 55.8 | 57.4 | 59.5 | 61.6 | 62.6 | 63.3 | 63.2 | 59.6 | 56.5 | 53.9 | 57.1 | 59.7 | 62.9 | 64.5 | 66.5 | 70.2 | 70.3 | 71.5 | 72.9 | 70.4 | 63.2 | 57.9 | 52.3 | 53.7 | 54.9 | 55.9 | 57.8 | 60.5 | 61.4 | 62.4 | 62.4 | 59.1 | 56 | 52.9 | 58.4 | 59.8 | 61.5 | 63.7 | 66 | 68.1 | 68 | 67.9 | 68.4 | 65.7 | 62.5 | 59.8 | 60.5 | 63.8 | 71.5 | 75.6 | 78.9 | 80.7 | 81.4 | 81.6 | 81.8 | 77 | 70.1 | 62 | 56.4 | 57.7 | 59.2 | 60.5 | 62.7 | 64.7 | 64.9 | 65.6 | 66.2 | 63.5 | 60.2 | 57.9 | 58.8 | 62.2 | 65.6 | 69.3 | 72.5 | 76.3 | 76.1 | 75.5 | 78.1 | 72.9 | 65.5 | 60.1 | 54.8 | 56.2 | 57.5 | 58.9 | 60.4 | 62.6 | 63.2 | 64.1 | 64.6 | 62 | 58.9 | 56.1 | 57.2 | 60.5 | 62.9 | 66.2 | 68.5 | 72.7 | 72.1 | 73 | 74.8 | 70.7 | 63.4 | 58.5 | 53.4 | 54.6 | 56.1 | 57.2 | 58.7 | 60.8 | 61.9 | 62.6 | 63.2 | 60.4 | 57.4 | 54.2 | 55.9 | 58.5 | 61.3 | 63.5 | 65.8 | 69.3 | 69.7 | 70.3 | 72 | 68.1 | 61.7 | 56.7 | 13.2 | 13.5 | 14.8 | 14.9 | 13.9 | 15 | 13.8 | 14 | 16.6 | 17.3 | 15 | 13.3 | 16 | 17.4 | 20.6 | 22 | 21.7 | 22.9 | 18.8 | 18.9 | 27.2 | 25.1 | 19.2 | 15 | 9.5 | 10.1 | 11.2 | 11.4 | 10.3 | 10.4 | 8.7 | 8.8 | 11.6 | 12.1 | 10.9 | 9.3 | 10.8 | 14.2 | 16.3 | 19.1 | 19.1 | 20.7 | 17.8 | 18.7 | 22.2 | 20 | 14.7 | 9.4 | 7.8 | 9 | 9.8 | 10.7 | 9.7 | 10 | 8.5 | 8.9 | 10.3 | 10.4 | 9.6 | 7.2 | 0.324 | 0.33 | 0.342 | 0.36 | 0.364 | 0.36 | 0.369 | 0.349 | 0.348 | 0.34 | 0.324 | 0.325 | 2.549 | 2.532 | 2.484 | 2.401 | 2.417 | 2.435 | 2.413 | 2.465 | 2.454 | 2.521 | 2.548 | 2.551 | 274 | 287 | 292 | 292 | 291 | 291 | 287 | 292 | 286 | 279 | 272 | 265 | 24 | 28 | 32 | 37 | 37 | 36 | 37 | 34 | 32 | 28 | 24 | 23 | 754 | 1054 | 1491 | 1950 | 2253 | 2466 | 2339 | 2086 | 1763 | 1297 | 892 | 662 | 107 | 128 | 134 | 155 | 145 | 104 | 77 | 88 | 66 | 82 | 57 | 97 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | -2.14 | N/A | N/A | N/A | N/A | -198 | 243 | N/A | 44
|  |  | PALO-ALTO-AP | 724937
|  |  | SAN-CARLOS-AP | 724938
4 | USA | CA | SAN FRANCISCO INTL | 724940 | 23234 | 37.62 | -122.365 | 8 | 14.69 | -8 | NAP | 94-19 | 3C | 1 | 40.3 | 42.2 | 26.2 | 20.2 | 52.1 | 29.8 | 23.9 | 51.5 | 31.4 | 56.3 | 26.5 | 55.3 | 3.5 | 150 | 0.583 | 9 | 16 | 82.9 | 62.8 | 78.1 | 62 | 74.5 | 61.5 | 65.9 | 77.4 | 64.2 | 74.4 | 63 | 72.1 | 12.6 | 290 | 61.6 | 81.9 | 68.9 | 60.2 | 77.9 | 67.5 | 59 | 74.6 | 66.3 | 30.5 | 77.4 | 29.3 | 74.5 | 28.4 | 72 | 78.1 | 28.5 | 25.5 | 23.3 | 36.2 | 92.9 | 2.1 | 3.6 | 34.7 | 95.5 | 33.5 | 97.6 | 32.3 | 99.6 | 30.8 | 102.2 | 33.3 | 69.4 | 2.4 | 2.4 | 31.5 | 71.1 | 30.1 | 72.5 | 28.7 | 73.8 | 27 | 75.5 | 58.3 | 51.3 | 53 | 55.2 | 56.8 | 59.2 | 62 | 63.3 | 64.2 | 64.8 | 62.2 | 56.2 | 51.4 | 6.29 | 3.78 | 3.99 | 4.17 | 4.34 | 4.25 | 4.22 | 3.29 | 3.44 | 4.65 | 4.55 | 4.2 | 4.11 | 84 | 29 | 14 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 31 | 2606 | 424 | 336 | 305 | 251 | 191 | 112 | 74 | 56 | 57 | 113 | 266 | 421 | 3128 | 70 | 98 | 166 | 206 | 287 | 359 | 413 | 441 | 445 | 378 | 190 | 75 | 173 | 0 | 0 | 1 | 5 | 12 | 21 | 22 | 32 | 52 | 27 | 1 | 0 | 945 | 0 | 0 | 10 | 46 | 90 | 154 | 97 | 125 | 278 | 140 | 5 | 0 | 267 | 0 | 0 | 0 | 10 | 26 | 52 | 22 | 34 | 89 | 34 | 0 | 0 | 10.3 | 6.6 | 8.3 | 10 | 12.4 | 13.5 | 13.7 | 12.7 | 12.2 | 10.9 | 9 | 7 | 7 | 21.9 | 4.2 | 4.1 | 3 | 1.5 | 0.7 | 0.2 | 0 | 0.1 | 0.1 | 1.1 | 2.3 | 4.6 | 38 | 10.4 | 14.3 | 8.7 | 5 | 3.3 | 1.6 | 0.1 | 0.9 | 0.5 | 3.7 | 7.2 | 11.8 | 8.1 | 0.3 | 0 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.4 | 6.3 | 3.1 | 3 | 2.4 | 1.2 | 0.8 | 0.4 | 0 | 0.2 | 0.1 | 1.1 | 1.8 | 3.2 | 65.1 | 70 | 74.6 | 80.1 | 83.5 | 86.8 | 82.5 | 85.1 | 88.9 | 84.5 | 73 | 64.5 | 53.1 | 56.8 | 59 | 60.7 | 61.7 | 63.6 | 65.2 | 64.7 | 64.4 | 61 | 59.3 | 57.3 | 61.4 | 64.6 | 68.4 | 72.2 | 74.7 | 77.8 | 76 | 76.6 | 81.5 | 77.5 | 68 | 61.6 | 54.1 | 55.9 | 56.6 | 57.9 | 59.6 | 61.7 | 63.2 | 63.7 | 63.3 | 59.5 | 57.3 | 56.3 | 59.1 | 61.6 | 64.2 | 66.6 | 69.3 | 72.3 | 72.3 | 73 | 76 | 73 | 65.1 | 59.8 | 53.5 | 55.1 | 55.6 | 56.2 | 58.6 | 60.6 | 61.8 | 62.5 | 62.6 | 59.2 | 56.7 | 55.2 | 57.2 | 59.1 | 61.5 | 63.3 | 65.7 | 69.1 | 69.8 | 70.5 | 72.1 | 69.5 | 62.7 | 58 | 52.7 | 53.7 | 54.7 | 54.9 | 56.7 | 59.1 | 60.7 | 61.4 | 61.8 | 59 | 56.2 | 53.8 | 58.9 | 60.3 | 61.6 | 62.7 | 65.3 | 66.2 | 66.3 | 66.9 | 68.4 | 65.6 | 62.4 | 60.8 | 60.8 | 64.1 | 70.1 | 75 | 77.1 | 81.8 | 79.5 | 78.5 | 79.4 | 75.2 | 68.4 | 62.7 | 56.4 | 58 | 59.1 | 59.7 | 62 | 63.2 | 63.9 | 64.6 | 65.9 | 63.3 | 60.4 | 58.9 | 58.7 | 62.2 | 65.2 | 68.5 | 71.4 | 75.3 | 74.3 | 74.3 | 76.8 | 71.9 | 65.1 | 60.5 | 54.9 | 56.4 | 57.3 | 57.7 | 59.4 | 61.3 | 62.4 | 63.2 | 64 | 61.8 | 59 | 56.8 | 57.3 | 60.2 | 62.1 | 64.8 | 67.3 | 71.5 | 71.4 | 71.9 | 73.9 | 70 | 63.3 | 58.7 | 53.4 | 54.8 | 55.8 | 55.8 | 57.6 | 59.6 | 61 | 61.9 | 62.3 | 60.1 | 57.4 | 54.6 | 55.9 | 58.2 | 60.3 | 62.1 | 64.6 | 68.2 | 69.1 | 70.1 | 71.1 | 67.5 | 61.4 | 56.9 | 10.6 | 11.6 | 13.1 | 13.8 | 13.8 | 15.2 | 14.6 | 14.5 | 16 | 15.4 | 12.5 | 10.5 | 13.3 | 15.7 | 18.2 | 20.6 | 21.2 | 22.2 | 18.8 | 18.8 | 23.9 | 22.1 | 16 | 11.5 | 8.1 | 9.1 | 10.2 | 10.6 | 10.3 | 10.4 | 8.8 | 8.5 | 11.1 | 10.7 | 8.8 | 7.7 | 9.5 | 13.1 | 15.5 | 18.3 | 18.9 | 20.9 | 18.1 | 18.2 | 21.6 | 19 | 13.1 | 8.2 | 7.1 | 8.3 | 9.6 | 10.3 | 9.8 | 10.1 | 8.7 | 8.4 | 10.4 | 10 | 8.4 | 7 | 0.324 | 0.332 | 0.341 | 0.358 | 0.365 | 0.359 | 0.367 | 0.345 | 0.348 | 0.338 | 0.322 | 0.324 | 2.562 | 2.537 | 2.504 | 2.421 | 2.426 | 2.449 | 2.432 | 2.494 | 2.47 | 2.54 | 2.568 | 2.566 | 275 | 286 | 293 | 292 | 290 | 291 | 288 | 293 | 287 | 280 | 273 | 266 | 24 | 28 | 31 | 36 | 36 | 36 | 36 | 33 | 32 | 27 | 23 | 23 | 764 | 1058 | 1494 | 1952 | 2220 | 2410 | 2246 | 2000 | 1715 | 1279 | 895 | 667 | 102 | 127 | 129 | 150 | 148 | 105 | 82 | 98 | 69 | 81 | 57 | 95 | N/A | N/A | -2.02 | N/A | N/A | N/A | N/A | N/A | 245 | 40 | N/A | N/A | -2.14 | N/A | N/A | N/A | N/A | -198 | 243 | N/A | 44
4 | USA | CA | SAN JOSE INTL | 724945 | 23293 | 37.359 | -121.924 | 51 | 14.67 | -8 | NAP | 94-19 | 3C | 12 | 36 | 38.3 | 19.6 | 14.7 | 52.8 | 24.3 | 18.5 | 53.7 | 24.8 | 54.5 | 21.7 | 54.5 | 2.4 | 150 | 0.456 | 8 | 20.8 | 91.4 | 66.1 | 87.7 | 65.2 | 83.9 | 64.2 | 68.9 | 85.6 | 67.4 | 82.9 | 66.1 | 80.7 | 10.3 | 330 | 62.9 | 86 | 74.8 | 61.3 | 81.1 | 73.2 | 60.3 | 78.2 | 71.9 | 33 | 85.5 | 31.7 | 82.5 | 30.7 | 80.8 | 78.8 | 19.7 | 17.9 | 16.3 | 32.1 | 98.9 | 3.1 | 3.4 | 29.9 | 101.3 | 28.1 | 103.3 | 26.4 | 105.3 | 24.1 | 107.7 | 29.5 | 71.5 | 2.9 | 2.6 | 27.4 | 73.4 | 25.7 | 75 | 24.1 | 76.5 | 22 | 78.4 | 60.9 | 51.6 | 53.5 | 56.6 | 58.8 | 62.9 | 67.1 | 69.5 | 69.8 | 68.9 | 64.1 | 56.6 | 51.3 | 8.27 | 4.6 | 4.8 | 4.93 | 5.37 | 5.15 | 5.02 | 4.07 | 3.86 | 4.95 | 4.75 | 4.96 | 4.71 | 106 | 36 | 18 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 39 | 2102 | 416 | 321 | 262 | 199 | 104 | 27 | 4 | 2 | 11 | 75 | 256 | 425 | 4097 | 85 | 117 | 211 | 266 | 399 | 514 | 606 | 613 | 568 | 436 | 204 | 78 | 619 | 0 | 0 | 3 | 14 | 38 | 91 | 145 | 150 | 129 | 46 | 3 | 0 | 5261 | 0 | 6 | 51 | 193 | 403 | 863 | 1103 | 1062 | 1077 | 469 | 34 | 0 | 1765 | 0 | 0 | 4 | 52 | 140 | 321 | 342 | 337 | 431 | 134 | 4 | 0 | 6.5 | 5 | 6.2 | 6.7 | 7.5 | 7.8 | 7.9 | 7.4 | 7 | 6.2 | 5.5 | 4.9 | 5.3 | 14.1 | 2.8 | 2.2 | 2.3 | 1.2 | 0.2 | 0 | 0 | 0.1 | 0.2 | 0.9 | 2.2 | 2 | 32.6 | 7.4 | 6.6 | 6.4 | 3.9 | 1.7 | 0.6 | 0.7 | 0.7 | 1 | 4.6 | 6.2 | 5 | 7.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 5.4 | 2 | 2 | 1.5 | 1.1 | 0.4 | 0.1 | 0.2 | 0.2 | 0.4 | 1 | 1.7 | 1.2 | 69.8 | 74.9 | 79.8 | 86.4 | 91.1 | 95 | 94.7 | 93.9 | 95.2 | 88.7 | 79 | 67.7 | 53.6 | 58.1 | 60.2 | 62.9 | 65.3 | 67.6 | 69.2 | 66.7 | 65.1 | 62.5 | 59.8 | 55.2 | 65.2 | 69.5 | 74.2 | 79.6 | 83.7 | 88.4 | 88.2 | 88.4 | 90.3 | 83.8 | 72.8 | 64.2 | 54.6 | 56.1 | 57.6 | 60.4 | 62.2 | 65.9 | 67.6 | 66.5 | 64.6 | 60.6 | 57.6 | 54 | 62.8 | 65.3 | 70.3 | 74.1 | 78.3 | 83.1 | 83.5 | 83.4 | 84.9 | 79.3 | 69.2 | 62.1 | 53.9 | 54.8 | 56.6 | 58.6 | 61.3 | 64.6 | 66.3 | 65.6 | 63.4 | 59.1 | 56.5 | 53.8 | 60.4 | 62.4 | 66.5 | 69.6 | 73.4 | 78.7 | 80.1 | 79.8 | 79.8 | 74.8 | 65.6 | 60 | 52.9 | 53.7 | 55.1 | 56.9 | 59.6 | 63.2 | 65.4 | 65 | 63.1 | 58.8 | 55.3 | 53 | 59.9 | 61.2 | 62.3 | 65.2 | 67.9 | 70.6 | 71 | 70.3 | 70.1 | 65.9 | 62.9 | 60.2 | 63.9 | 69.1 | 75.7 | 81.4 | 87 | 89.3 | 90.4 | 86.8 | 87.2 | 80.3 | 73 | 64.5 | 57.4 | 58.7 | 60 | 62.1 | 64.8 | 67.7 | 68.6 | 68.1 | 66.7 | 63.6 | 60.5 | 58.2 | 61.7 | 65.9 | 70.3 | 76.4 | 79.7 | 84.7 | 84.9 | 83.5 | 82.1 | 77.3 | 68.2 | 61.7 | 55.5 | 56.7 | 58.2 | 59.7 | 62.5 | 65.8 | 67.2 | 66.6 | 65.2 | 62 | 59 | 56.3 | 60 | 63.4 | 67.4 | 71.6 | 75.6 | 81.2 | 81.8 | 80.9 | 80.9 | 74.3 | 66 | 59.8 | 53.8 | 54.9 | 56.4 | 57.8 | 60.4 | 63.8 | 65.8 | 65.3 | 63.9 | 60.4 | 57.4 | 54.2 | 58.6 | 60.9 | 64.8 | 67.8 | 71.7 | 77 | 79.2 | 78.5 | 78 | 71.1 | 63.9 | 58.3 | 16 | 16.3 | 18.2 | 19 | 19.4 | 21.3 | 21.1 | 20.8 | 21.6 | 21 | 17.8 | 15.6 | 19.9 | 21.9 | 24.7 | 27.3 | 27.7 | 28.6 | 26.6 | 27.2 | 29.8 | 28.2 | 22.9 | 18.3 | 11.2 | 11.6 | 12.3 | 12.9 | 11.9 | 11.7 | 10.7 | 10.4 | 10.9 | 11.4 | 11.1 | 10.2 | 13.4 | 17.4 | 20.8 | 23.3 | 23.6 | 25.2 | 23.6 | 23.4 | 24.2 | 22.5 | 17.8 | 11 | 8.9 | 10.2 | 11.3 | 12.1 | 11.4 | 11.7 | 10.5 | 9.9 | 10 | 10 | 9.7 | 7.6 | 0.324 | 0.332 | 0.337 | 0.36 | 0.372 | 0.363 | 0.367 | 0.35 | 0.356 | 0.333 | 0.322 | 0.323 | 2.533 | 2.511 | 2.489 | 2.398 | 2.385 | 2.418 | 2.418 | 2.459 | 2.432 | 2.534 | 2.542 | 2.546 | 275 | 286 | 295 | 292 | 288 | 290 | 288 | 292 | 284 | 282 | 273 | 267 | 25 | 29 | 32 | 37 | 38 | 37 | 36 | 34 | 33 | 27 | 24 | 23 | 774 | 1073 | 1518 | 1964 | 2277 | 2496 | 2371 | 2127 | 1796 | 1327 | 915 | 685 | 102 | 125 | 134 | 161 | 141 | 101 | 72 | 82 | 67 | 80 | 54 | 95 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | -241 | 337 | 108 | N/A | N/A | -2.11 | N/A | N/A | N/A | N/A | -194 | 239 | N/A | 44
4 | USA | CA | SAN-JOSE-REID-HILLV | 724946 | 99999 | 37.33 | -121.82 | 134 | 14.62 | -8 | NAP | N/A | 3C | 12 | 35.42 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 8 | 21.06 | 91.4 | 66.02 | N/A | N/A | N/A | N/A | 68.9 | 85.82 | N/A | N/A | N/A | N/A | N/A | N/A | 62.78 | N/A | 75.56 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 7.8293 | 7.3819 | 6.9345 | 6.0397 | 5.3687 | 4.6976 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 95.18 | 95 | 94.28 | 94.28 | 90.14 | 79.52 | N/A | N/A | N/A | N/A | N/A | N/A | 67.28 | 69.62 | 67.1 | 65.48 | 62.78 | 59.36 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 21.24 | 21.06 | 21.06 | 21.6 | 20.88 | 18.18 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.363 | 0.367 | 0.35 | 0.356 | 0.333 | 0.322 | N/A | N/A | N/A | N/A | N/A | N/A | 2.418 | 2.418 | 2.459 | 2.432 | 2.534 | 2.542 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
4 | USA | CA | BUCHANAN FIELD | 724950 | 23254 | 37.992 | -122.055 | 18 | 14.69 | -8 | NAP | 99-19 | 3A | 1 | 33.1 | 35.5 | 18.7 | 14.1 | 54.8 | 22.9 | 17.3 | 54.2 | 19.6 | 55.5 | 17.2 | 53.5 | 1.9 | 160 | 0.491 | 7 | 28.6 | 97.9 | 66.9 | 94.2 | 65.8 | 90.6 | 64.9 | 69 | 92.8 | 67.5 | 89.9 | 66.2 | 87.1 | 10.1 | 300 | 60.3 | 78.3 | 73.6 | 59 | 74.6 | 71.8 | 57.9 | 71.5 | 70.5 | 33 | 92.7 | 31.8 | 89.9 | 30.7 | 87.1 | 76.5 | 19.8 | 18.1 | 16.6 | 29.8 | 104.8 | 2.1 | 3.1 | 28.3 | 107 | 27.1 | 108.8 | 26 | 110.5 | 24.4 | 112.7 | 27.7 | 71.6 | 2.3 | 2 | 26 | 73.1 | 24.7 | 74.3 | 23.4 | 75.4 | 21.7 | 76.9 | 61.4 | 49.2 | 52.3 | 56.3 | 59.3 | 64.7 | 70.3 | 72.7 | 72.4 | 70.7 | 64.3 | 55.2 | 49.2 | 10 | 4.44 | 4.59 | 5 | 5.45 | 5.45 | 5.88 | 5.15 | 4.47 | 5.28 | 5.04 | 5.23 | 4.86 | 190 | 69 | 26 | 6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 73 | 2263 | 490 | 356 | 273 | 187 | 72 | 12 | 3 | 2 | 8 | 74 | 295 | 491 | 4367 | 44 | 90 | 201 | 280 | 457 | 610 | 705 | 696 | 622 | 444 | 171 | 47 | 967 | 0 | 0 | 3 | 16 | 64 | 173 | 243 | 233 | 180 | 54 | 1 | 0 | 11188 | 0 | 7 | 74 | 297 | 918 | 2110 | 2664 | 2346 | 2012 | 725 | 35 | 0 | 5178 | 0 | 0 | 6 | 87 | 366 | 1035 | 1354 | 1116 | 976 | 235 | 3 | 0 | 7.2 | 4.5 | 5.6 | 6.6 | 7.9 | 9.4 | 10.2 | 10.4 | 9.5 | 7.4 | 5.6 | 4.5 | 4.7 | 20.1 | 4.3 | 3.6 | 2.6 | 1.4 | 0.7 | 0.2 | 0 | 0 | 0.1 | 1.1 | 2.3 | 4 | 30.5 | 10.5 | 12.9 | 8.3 | 4.6 | 3 | 1.9 | 0.1 | 0.8 | 0.6 | 4.3 | 6.8 | 10.2 | 8.7 | 0.2 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 5.3 | 2.9 | 2.6 | 2.3 | 1.1 | 0.8 | 0.4 | 0 | 0.2 | 0.1 | 1.1 | 1.7 | 2.9 | 68.2 | 74.3 | 80.5 | 87.8 | 95.3 | 101.8 | 102.5 | 100.2 | 99.7 | 91 | 78.2 | 66 | 51.9 | 56.8 | 61.1 | 63.7 | 66.1 | 68.4 | 68.5 | 67.6 | 66.3 | 62.9 | 58.8 | 53.9 | 63.6 | 69.1 | 75.8 | 82 | 88.9 | 96.1 | 96.8 | 95.2 | 95.1 | 86.2 | 73.5 | 63 | 52.9 | 55.4 | 59.3 | 61.2 | 63.7 | 66.5 | 67 | 66.3 | 64.9 | 61.2 | 57.3 | 53.2 | 60.9 | 65.1 | 71.7 | 76.6 | 83.7 | 91 | 92.2 | 90.7 | 90.6 | 81.9 | 69.3 | 60.5 | 52.2 | 53.8 | 57.1 | 59 | 61.6 | 64.9 | 66.2 | 65.2 | 64 | 59.4 | 55.6 | 53 | 58.1 | 61.9 | 67.6 | 71.7 | 78.7 | 85.9 | 88 | 86.3 | 85.6 | 77.6 | 65.7 | 58.3 | 51.3 | 53 | 55.4 | 57.1 | 60 | 63 | 65.1 | 64.4 | 62.7 | 58.6 | 54.7 | 52 | 58 | 60.3 | 63.4 | 65.7 | 68.7 | 70.8 | 71.9 | 69.7 | 69.5 | 65.9 | 62.3 | 59.5 | 61.8 | 68.1 | 76 | 83.1 | 90.7 | 97.3 | 98.4 | 93.6 | 95.4 | 83.9 | 72.9 | 62.7 | 55.9 | 58.1 | 60.7 | 62.5 | 65.4 | 68 | 68.8 | 68 | 67.1 | 63.7 | 60.2 | 57.4 | 60 | 64.8 | 72.9 | 79 | 86.4 | 92 | 92.5 | 90.4 | 88.6 | 80.3 | 68.6 | 60 | 54.1 | 56.2 | 58.6 | 60.2 | 62.9 | 66 | 67.2 | 66.4 | 65.4 | 62.1 | 58.6 | 55.4 | 57.8 | 62.7 | 68.7 | 74.5 | 80.5 | 88.1 | 89.3 | 87.2 | 85.2 | 76.8 | 65.9 | 58.3 | 52.4 | 54.3 | 56.6 | 57.9 | 60.8 | 64.1 | 65.6 | 65.1 | 63.9 | 60.3 | 56.9 | 53.4 | 56.4 | 60.4 | 65.2 | 69.8 | 76.5 | 83.8 | 86.3 | 84.3 | 82.7 | 72.9 | 63.6 | 56.4 | 16.5 | 17.9 | 19.6 | 21.1 | 23.5 | 26.8 | 28.6 | 27.5 | 27.1 | 24.2 | 19.8 | 16.3 | 21.8 | 24.6 | 27.2 | 30.6 | 33.3 | 36.1 | 36 | 35.2 | 36.2 | 32.2 | 25.5 | 19.7 | 12.7 | 13.4 | 13.5 | 14 | 12.9 | 12.3 | 11.9 | 11.4 | 11.9 | 12.3 | 12.3 | 11.5 | 15 | 19 | 23.3 | 27.6 | 30.3 | 33.3 | 34.3 | 31.7 | 31.3 | 26.8 | 20.1 | 11.8 | 10.2 | 11.4 | 12.6 | 13.4 | 12.8 | 12.3 | 12.1 | 11.1 | 11.1 | 11.3 | 11.1 | 8.5 | 0.323 | 0.326 | 0.34 | 0.359 | 0.364 | 0.361 | 0.366 | 0.35 | 0.348 | 0.333 | 0.325 | 0.326 | 2.536 | 2.529 | 2.475 | 2.394 | 2.407 | 2.421 | 2.406 | 2.444 | 2.446 | 2.525 | 2.53 | 2.529 | 273 | 288 | 293 | 292 | 291 | 290 | 288 | 291 | 286 | 281 | 270 | 263 | 24 | 28 | 32 | 37 | 37 | 37 | 37 | 35 | 33 | 27 | 24 | 23 | 736 | 1045 | 1481 | 1945 | 2293 | 2532 | 2454 | 2192 | 1821 | 1316 | 883 | 649 | 114 | 130 | 142 | 161 | 141 | 104 | 74 | 76 | 64 | 85 | 58 | 100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.67 | N/A | -2.07 | N/A | N/A | N/A | N/A | -207 | 239 | N/A | 47
4 | USA | CA | NAPA COUNTY AP | 724955 | 93227 | 38.21 | -122.285 | 14 | 14.69 | -8 | NAP | 98-19 | 3C | 12 | 29.6 | 32.1 | 17.5 | 13.3 | 51.7 | 22.2 | 16.7 | 49.2 | 25 | 55.9 | 21.7 | 55.2 | 2.1 | 0 | 0.54 | 8 | 24 | 91.1 | 65.9 | 86.4 | 64.9 | 82.4 | 64 | 68.4 | 86.1 | 66.8 | 82.9 | 65.4 | 79.7 | 10 | 200 | 61.5 | 81.6 | 74.3 | 60.4 | 78.5 | 72.7 | 59.2 | 75.2 | 71 | 32.6 | 86.2 | 31.2 | 82.9 | 30.2 | 79.9 | 75.9 | 21.3 | 19.1 | 17.5 | 23.8 | 99.7 | 2.4 | 3.6 | 22 | 102.2 | 20.6 | 104.3 | 19.3 | 106.3 | 17.6 | 108.9 | 22.5 | 71.5 | 2.5 | 1.5 | 20.7 | 72.6 | 19.3 | 73.4 | 17.8 | 74.3 | 16 | 75.3 | 57.3 | 47.5 | 49.9 | 52.8 | 55.2 | 59.8 | 64.5 | 65.9 | 66.1 | 65.1 | 60.1 | 52.6 | 47.3 | 8.36 | 4.5 | 4.64 | 4.77 | 5.02 | 4.65 | 4.7 | 3.79 | 3.62 | 4.74 | 4.67 | 5.21 | 5.15 | 338 | 103 | 54 | 25 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 115 | 3076 | 543 | 423 | 380 | 296 | 176 | 62 | 30 | 26 | 54 | 165 | 371 | 550 | 2994 | 25 | 51 | 111 | 166 | 303 | 436 | 493 | 500 | 454 | 314 | 110 | 31 | 254 | 0 | 0 | 1 | 2 | 13 | 48 | 59 | 60 | 58 | 13 | 0 | 0 | 4025 | 1 | 4 | 34 | 128 | 332 | 758 | 666 | 713 | 926 | 436 | 26 | 1 | 1438 | 0 | 0 | 3 | 29 | 117 | 292 | 220 | 240 | 398 | 137 | 2 | 0 | 7.5 | 6.3 | 6.4 | 6.9 | 8.1 | 9.1 | 9.8 | 10 | 9.1 | 7.3 | 5.8 | 5.3 | 6.2 | 26.4 | 5.4 | 4.6 | 3.7 | 1.5 | 0.7 | 0.2 | 0 | 0.1 | 0.3 | 1.5 | 3.7 | 4.8 | 51.3 | 13.8 | 15.3 | 12 | 5.7 | 3.7 | 2 | 1.1 | 1.3 | 2.3 | 10.4 | 10.5 | 15.5 | 10.5 | 0.4 | 0.2 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 8.7 | 3.6 | 3.7 | 2.9 | 1.5 | 1 | 0.4 | 0.2 | 0.3 | 0.5 | 1.8 | 2.7 | 3.6 | 67.1 | 72.2 | 78.2 | 83.9 | 90.1 | 95.1 | 93 | 94 | 96.3 | 89.9 | 77.3 | 65 | 50.8 | 58.1 | 62.1 | 63.8 | 65.5 | 68.1 | 68.3 | 66.9 | 65.4 | 61.7 | 59.7 | 49.6 | 62.4 | 67.2 | 72.7 | 77.5 | 82.6 | 88 | 85.6 | 86.2 | 90.5 | 83.8 | 72.4 | 61.8 | 52.1 | 55.5 | 59.1 | 61.3 | 63.1 | 65.6 | 67 | 66.5 | 64.7 | 60.1 | 57 | 52.6 | 59.1 | 63.3 | 68 | 71.9 | 76.6 | 82.1 | 80.8 | 81.4 | 84.4 | 78.9 | 67.6 | 59.3 | 51.9 | 53.4 | 56.5 | 58.8 | 61.2 | 64.1 | 65.4 | 65.3 | 63.6 | 58.7 | 55.5 | 53.1 | 56.4 | 60.1 | 64 | 67.1 | 72 | 77.4 | 76.8 | 77.2 | 78.6 | 73.9 | 63.7 | 57.1 | 51.4 | 52.8 | 55 | 57 | 59.8 | 62.6 | 63.9 | 64 | 62.9 | 58.1 | 54.6 | 51.9 | 57.3 | 60.1 | 64 | 66.3 | 68.7 | 70.2 | 70.2 | 69.6 | 69.1 | 65.9 | 62.9 | 59 | 60.4 | 67.4 | 75.5 | 80.4 | 86.3 | 91.2 | 89.3 | 87.8 | 87.3 | 80.9 | 73.5 | 60.8 | 55.3 | 57.8 | 60.5 | 63.1 | 64.6 | 67.3 | 67.6 | 67.4 | 66.8 | 63.5 | 60.1 | 57 | 58.4 | 64.1 | 70.2 | 75.8 | 79 | 84.5 | 84.2 | 83.8 | 84.3 | 76.4 | 67.3 | 58.9 | 53.8 | 55.9 | 58.2 | 60.2 | 62.4 | 65.1 | 65.8 | 65.8 | 65.3 | 61.8 | 58.3 | 55.2 | 56.4 | 61 | 65.4 | 69.7 | 74.5 | 79.6 | 79.9 | 80 | 80.6 | 73.3 | 63.9 | 57.1 | 52.4 | 54.1 | 56.1 | 57.8 | 60.3 | 63.2 | 64.2 | 64.3 | 63.7 | 60 | 56.5 | 53.1 | 55.3 | 58.5 | 62.1 | 65.3 | 70.8 | 76.1 | 76.4 | 76.6 | 77.3 | 70.3 | 61.8 | 55.4 | 18.1 | 20 | 21.8 | 23.3 | 24.2 | 25.3 | 23.3 | 24 | 27.9 | 27.5 | 22.7 | 18.8 | 23.8 | 27.3 | 29.8 | 32.8 | 34.2 | 35 | 31.1 | 32.7 | 39.1 | 37.4 | 29.8 | 21.7 | 15.2 | 16.9 | 18.1 | 18.9 | 17.6 | 16 | 14.5 | 15.2 | 16.8 | 17.5 | 16.5 | 13.9 | 16 | 21.4 | 25.7 | 28.6 | 29.6 | 30.6 | 28.7 | 29.5 | 33.2 | 29.4 | 22 | 12.7 | 11.6 | 14.2 | 16.7 | 17.6 | 16.5 | 14.7 | 13.7 | 14 | 15.3 | 15.4 | 14.1 | 9.9 | 0.32 | 0.321 | 0.334 | 0.356 | 0.36 | 0.357 | 0.361 | 0.345 | 0.343 | 0.321 | 0.318 | 0.321 | 2.548 | 2.548 | 2.501 | 2.411 | 2.43 | 2.444 | 2.429 | 2.468 | 2.477 | 2.576 | 2.56 | 2.546 | 274 | 290 | 295 | 292 | 292 | 292 | 289 | 292 | 288 | 285 | 273 | 265 | 24 | 27 | 31 | 36 | 36 | 36 | 36 | 34 | 32 | 26 | 23 | 23 | 729 | 1034 | 1464 | 1932 | 2287 | 2528 | 2461 | 2192 | 1819 | 1304 | 874 | 639 | 116 | 134 | 146 | 161 | 141 | 108 | 75 | 75 | 63 | 89 | 61 | 102 | 0.74 | N/A | -3.01 | N/A | N/A | N/A | N/A | N/A | 254 | N/A | 0.67 | N/A | -2.07 | N/A | N/A | N/A | N/A | -207 | 239 | N/A | 47
4 | USA | CA | SONOMA COUNTY AP | 724957 | 23213 | 38.504 | -122.81 | 114 | 14.64 | -8 | NAP | 98-19 | 3C | 12 | 29.3 | 31.5 | 18.9 | 14.3 | 57.3 | 24.3 | 18.5 | 51 | 21.1 | 55.2 | 18.2 | 54.3 | 1.6 | 300 | 0.486 | 7 | 29.9 | 94.9 | 66.5 | 91 | 65.7 | 87.3 | 64.5 | 69 | 89.9 | 67.4 | 87.3 | 65.9 | 84.3 | 8.6 | 180 | 61 | 80.3 | 74.7 | 59.3 | 75.6 | 72.6 | 58 | 72.2 | 71 | 33.1 | 90.5 | 31.7 | 87.5 | 30.6 | 84.4 | 86.7 | 17.1 | 15 | 12.6 | 25.3 | 101.7 | 2.3 | 3.3 | 23.6 | 104 | 22.3 | 105.9 | 21 | 107.7 | 19.4 | 110.1 | 24.4 | 72.9 | 2.5 | 3.6 | 22.6 | 75.5 | 21.1 | 77.6 | 19.8 | 79.6 | 18 | 82.2 | 58.1 | 47.8 | 50.3 | 53.3 | 56 | 60.8 | 65.8 | 67.4 | 67.6 | 66.2 | 61.1 | 53 | 47.5 | 8.86 | 4.41 | 4.86 | 5.16 | 5.49 | 5.02 | 5.18 | 4.09 | 3.86 | 4.92 | 5.08 | 5.27 | 5.04 | 319 | 97 | 50 | 25 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 110 | 2901 | 535 | 412 | 364 | 274 | 150 | 48 | 17 | 15 | 39 | 144 | 360 | 543 | 3279 | 27 | 58 | 126 | 190 | 336 | 475 | 541 | 545 | 487 | 343 | 119 | 32 | 386 | 0 | 0 | 1 | 5 | 20 | 73 | 93 | 95 | 76 | 22 | 1 | 0 | 7287 | 3 | 11 | 69 | 214 | 572 | 1421 | 1464 | 1447 | 1401 | 640 | 44 | 1 | 3069 | 0 | 1 | 11 | 60 | 203 | 633 | 621 | 639 | 659 | 237 | 5 | 0 | 4.6 | 3.3 | 4.5 | 5 | 5.5 | 5.8 | 5.7 | 5.4 | 4.9 | 4.3 | 3.9 | 3.3 | 3.6 | 45.4 | 9.8 | 8.4 | 5.4 | 3 | 1.9 | 0.4 | 0 | 0.1 | 0.1 | 2.2 | 4.2 | 10.2 | 71.9 | 30 | 25.3 | 18.8 | 9.3 | 6.9 | 1.4 | 0.1 | 1.2 | 0.4 | 6 | 11.1 | 23.1 | 24.8 | 0.9 | 0.4 | 0.2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 2.4 | 13.6 | 6.9 | 5.7 | 5.3 | 2.3 | 2.1 | 0.4 | 0 | 0.3 | 0.1 | 1.5 | 3.1 | 6.5 | 69.2 | 75.5 | 81.1 | 87.1 | 92.1 | 98.2 | 98.7 | 97.6 | 98.3 | 93 | 79.2 | 67.8 | 52.5 | 58.9 | 61.8 | 63.8 | 65.9 | 68.2 | 70.1 | 67.8 | 66.7 | 62.5 | 60.6 | 52.4 | 64 | 69.3 | 74.9 | 80.3 | 85.6 | 92.4 | 91.6 | 92.2 | 93.5 | 86.4 | 73.8 | 62.9 | 52.5 | 56.2 | 58.8 | 61.5 | 62.9 | 66.4 | 67.4 | 66.6 | 65.2 | 60.9 | 57.5 | 52.1 | 60.1 | 64.7 | 70.2 | 74.4 | 80.5 | 87.5 | 86.8 | 87.2 | 88.2 | 81.3 | 68.7 | 59.8 | 51.9 | 53.1 | 56.1 | 58.7 | 61.6 | 64.9 | 66.2 | 65.7 | 63.9 | 59.1 | 55.7 | 53.1 | 56.9 | 60.5 | 65.4 | 69.2 | 75.3 | 82.2 | 82.2 | 82.2 | 82.2 | 75.9 | 64 | 57.3 | 51.4 | 51.8 | 54.1 | 56.2 | 59.2 | 63.2 | 64.8 | 64.6 | 62.7 | 58.1 | 54.3 | 52.2 | 58 | 60.3 | 63.6 | 66.3 | 68.4 | 71.1 | 71.3 | 70.5 | 69.8 | 66 | 63.3 | 59.2 | 62.1 | 71.3 | 78.1 | 82.3 | 87.5 | 93.7 | 94.5 | 92.5 | 91.4 | 82.5 | 75.6 | 61.4 | 55.7 | 57.8 | 60.2 | 62.5 | 65.1 | 68.2 | 68.4 | 67.9 | 67.1 | 63.5 | 60.3 | 57.3 | 59.4 | 65.8 | 72.6 | 77.6 | 82.5 | 89.1 | 89.1 | 88.5 | 88.1 | 80.9 | 68.5 | 59.2 | 54.2 | 55.5 | 57.8 | 59.8 | 62.5 | 65.9 | 66.6 | 66.2 | 65.2 | 61.6 | 58.2 | 55.3 | 57.1 | 61.4 | 67.1 | 72.4 | 77.7 | 84.7 | 85.2 | 85.1 | 84.2 | 75.1 | 64.4 | 57.5 | 52.6 | 53.7 | 55.4 | 57.2 | 60.1 | 63.8 | 65 | 64.7 | 63.5 | 59.7 | 56.3 | 53.5 | 55.6 | 58.2 | 62.1 | 67.3 | 73.5 | 80.6 | 81.9 | 81.6 | 80.8 | 71.7 | 61.7 | 55.6 | 19.7 | 20.6 | 22.4 | 24.1 | 26.7 | 29.7 | 29.9 | 30 | 31.6 | 29.2 | 23.3 | 19.3 | 27.2 | 29.9 | 32.3 | 34.2 | 36.9 | 39.5 | 38.9 | 40 | 42.9 | 40.2 | 31.6 | 24.7 | 16.8 | 17.3 | 17.6 | 17.6 | 17.5 | 17 | 17 | 16.8 | 17.5 | 17.2 | 17 | 15.6 | 18.4 | 23.8 | 28.4 | 30.8 | 33.2 | 36 | 35.4 | 35.3 | 36.5 | 32.5 | 24 | 14.3 | 12.9 | 14.9 | 16.5 | 16.8 | 17 | 17 | 16.2 | 15.6 | 16.1 | 15.4 | 14.4 | 10.6 | 0.319 | 0.323 | 0.33 | 0.349 | 0.35 | 0.349 | 0.352 | 0.335 | 0.334 | 0.32 | 0.315 | 0.32 | 2.556 | 2.545 | 2.528 | 2.437 | 2.468 | 2.477 | 2.468 | 2.515 | 2.509 | 2.591 | 2.578 | 2.553 | 274 | 288 | 296 | 295 | 295 | 294 | 292 | 295 | 291 | 285 | 274 | 265 | 24 | 27 | 30 | 35 | 35 | 35 | 35 | 32 | 30 | 25 | 23 | 22 | 717 | 1014 | 1438 | 1908 | 2268 | 2505 | 2405 | 2123 | 1777 | 1273 | 854 | 619 | 116 | 139 | 145 | 155 | 142 | 115 | 91 | 80 | 74 | 93 | 65 | 103 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 212 | N/A | N/A | N/A | -2.14 | N/A | N/A | N/A | N/A | -187 | 248 | N/A | 39
4 | USA | CA | BLUE CANYON | 725845 | 23225 | 39.277 | -120.71 | 5276 | 12.1 | -8 | NAP | 94-19 | 4C | 2 | 21.1 | 23.6 | -6.9 | 4.6 | 42.8 | -1.6 | 6.1 | 42.6 | 25.6 | 34.5 | 22 | 35.8 | 5.7 | 60 | 0.447 | 7 | 12.9 | 83.8 | 58.7 | 81.3 | 57.8 | 79.2 | 56.4 | 62.5 | 78.3 | 60.5 | 76.8 | 59 | 75.3 | 6.4 | 270 | 56.1 | 81.6 | 70.8 | 53.6 | 74.3 | 70 | 51.3 | 68.3 | 69.1 | 30.7 | 78.3 | 29.2 | 76.9 | 27.9 | 75.2 | 80.1 | 18.8 | 16.2 | 13.1 | 17 | 87.7 | 3.2 | 2.3 | 14.7 | 89.3 | 12.8 | 90.6 | 11 | 91.9 | 8.7 | 93.6 | 14.6 | 65.5 | 3.2 | 3.6 | 12.3 | 68.1 | 10.4 | 70.2 | 8.7 | 72.2 | 6.4 | 74.9 | 51.9 | 40.5 | 38.6 | 41.5 | 44.5 | 52.8 | 62 | 70.2 | 69.4 | 64.2 | 54.5 | 44.8 | 38.9 | 14.37 | 8.91 | 8.97 | 8.93 | 9.72 | 9.83 | 8.92 | 5.77 | 5.64 | 8.53 | 9.15 | 9.38 | 8.29 | 1907 | 315 | 334 | 292 | 224 | 89 | 16 | 0 | 0 | 9 | 63 | 211 | 354 | 5301 | 760 | 738 | 729 | 616 | 390 | 155 | 21 | 24 | 114 | 339 | 607 | 808 | 2606 | 20 | 16 | 28 | 58 | 176 | 375 | 626 | 603 | 436 | 201 | 55 | 12 | 522 | 0 | 0 | 0 | 0 | 12 | 64 | 182 | 161 | 91 | 12 | 0 | 0 | 2362 | 0 | 0 | 0 | 0 | 36 | 294 | 911 | 740 | 352 | 29 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 1 | 44 | 147 | 110 | 43 | 1 | 0 | 0 | 5.5 | 5.7 | 6.2 | 6.3 | 6 | 5.4 | 5.2 | 4.5 | 4.6 | 5.1 | 5.3 | 5.4 | 6.3 | 70.4 | 12.2 | 10.3 | 9.4 | 5.2 | 2.1 | 0.8 | 0.1 | 0.6 | 1.3 | 4.3 | 10.7 | 11.5 | 121.7 | 33.9 | 37.7 | 22.2 | 14.2 | 5.3 | 2.7 | 1 | 3.7 | 7 | 22.3 | 28.3 | 41.6 | 23.5 | 0.7 | 0.8 | 1.7 | 0.7 | 0.1 | 0 | 0 | 0 | 0 | 0 | 1 | 0.4 | 20.7 | 8.2 | 8.2 | 5.6 | 3.8 | 1.5 | 0.8 | 0.3 | 1 | 1.9 | 4.6 | 7 | 9.1 | 62.7 | 62.7 | 65.5 | 70.4 | 78.5 | 85.2 | 86.9 | 86.2 | 85 | 78.1 | 68.7 | 61.6 | 42.3 | 44.1 | 46.1 | 50.4 | 55.9 | 61.2 | 60.1 | 58.5 | 54.6 | 52.2 | 48.4 | 42.3 | 58.5 | 58.6 | 61.3 | 66.4 | 73.6 | 80.4 | 83.9 | 83 | 80.4 | 72.8 | 64.7 | 57.1 | 40.7 | 42.5 | 45 | 48.5 | 54.2 | 58.1 | 59.9 | 57.7 | 54.8 | 50.4 | 46.6 | 40.2 | 55.6 | 55.2 | 57.9 | 63 | 70.4 | 77.2 | 81.2 | 80.7 | 78 | 69.7 | 61 | 53.8 | 39.7 | 40.7 | 43.4 | 46.9 | 52.3 | 56.7 | 58.9 | 56.7 | 54 | 49.1 | 44.5 | 38.2 | 52.7 | 52 | 54.3 | 59.2 | 66.9 | 74.6 | 79 | 78.4 | 75.5 | 66.5 | 57.9 | 50.7 | 38.5 | 38.9 | 41.6 | 45 | 50.4 | 55.1 | 57.5 | 55.6 | 53.3 | 47.6 | 42.9 | 37.4 | 46.7 | 47.2 | 49.4 | 53.3 | 59.4 | 63.9 | 65.1 | 62.8 | 68.6 | 55.1 | 51 | 46.2 | 52.6 | 56.8 | 60.7 | 64.7 | 72.3 | 80 | 81.8 | 80.5 | 70.8 | 70 | 64.4 | 51.8 | 44.1 | 44.5 | 46.9 | 50.5 | 56.2 | 60.9 | 62.6 | 60.3 | 60 | 52.9 | 48.3 | 43.8 | 51.3 | 53.8 | 57.5 | 62.9 | 69.9 | 76.8 | 79.4 | 77.8 | 72 | 67.8 | 60.8 | 49.1 | 42.3 | 42.5 | 44.9 | 48.4 | 54.1 | 58.6 | 60.9 | 58.8 | 57.1 | 51.3 | 46.3 | 42 | 50.4 | 51.5 | 54.8 | 60 | 67.5 | 74.1 | 77.8 | 76.4 | 72.5 | 65.9 | 57.5 | 47.7 | 40.8 | 40.6 | 43.1 | 46.3 | 51.9 | 56.4 | 59.4 | 57.3 | 55 | 49.6 | 44.6 | 40.3 | 49.5 | 49.2 | 51.9 | 56.9 | 65.2 | 71.9 | 76.1 | 74.9 | 71.9 | 63.7 | 54.5 | 47.2 | 10.1 | 10 | 11.2 | 12.6 | 13 | 13.4 | 12.9 | 13.4 | 13.6 | 12.5 | 10.4 | 9.7 | 12.7 | 12.6 | 14 | 15.6 | 15 | 14.1 | 13.2 | 13.5 | 14 | 13.6 | 12.1 | 12.6 | 8.7 | 9 | 10.5 | 11 | 10.6 | 10.6 | 9 | 8.2 | 8.3 | 8.4 | 8.5 | 8.6 | 11 | 11.2 | 13 | 14.7 | 14.7 | 13.8 | 12.6 | 12.9 | 13.6 | 12.9 | 11.5 | 10 | 8.4 | 9 | 10.1 | 11 | 10.8 | 11 | 9.2 | 8.5 | 9.3 | 8.7 | 8.6 | 8.4 | 0.276 | 0.275 | 0.296 | 0.306 | 0.312 | 0.305 | 0.307 | 0.294 | 0.299 | 0.285 | 0.268 | 0.282 | 2.528 | 2.557 | 2.5 | 2.486 | 2.497 | 2.538 | 2.541 | 2.566 | 2.563 | 2.602 | 2.612 | 2.506 | 289 | 305 | 307 | 308 | 306 | 307 | 305 | 308 | 302 | 298 | 292 | 277 | 23 | 26 | 31 | 33 | 34 | 32 | 32 | 30 | 29 | 25 | 21 | 22 | 722 | 992 | 1400 | 1850 | 2255 | 2623 | 2617 | 2355 | 1892 | 1323 | 841 | 615 | 110 | 141 | 170 | 189 | 189 | 139 | 111 | 92 | 80 | 101 | 70 | 106 | 1.48 | N/A | N/A | N/A | N/A | N/A | -212 | -324 | 198 | 97 | 0.79 | N/A | -1.98 | N/A | N/A | N/A | -58 | -175 | 236 | 95 | 26
4 | USA | CA | TRUCKEE-TAHOE | 725846 | 93201 | 39.32 | -120.139 | 5900 | 11.82 | -8 | NAP | 94-19 | 6A | 1 | 0.5 | 6.7 | -2.8 | 5.9 | 4 | 1.3 | 7.3 | 9.8 | 28.7 | 38.3 | 26.2 | 39.2 | 0.3 | 170 | N/A | 7 | 40.8 | 88.2 | 58.3 | 84.5 | 56.8 | 82.3 | 56 | 61.6 | 80.2 | 59.9 | 79 | 58.5 | 78.2 | 9.9 | 230 | 55.4 | 81.6 | 65.9 | 53.5 | 76.1 | 65.5 | 49.9 | 66.3 | 64.6 | 30.6 | 80 | 29.1 | 79.1 | 28 | 78.4 | 69.1 | 22.2 | 18.7 | 16.6 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 44 | 28.5 | 30.3 | 35.7 | 39.8 | 48.4 | 55.1 | 62.5 | 61.5 | 54.2 | 45.2 | 36.2 | 29.8 | 13.62 | 8.23 | 7.06 | 6.89 | 7 | 6.81 | 6.04 | 5.12 | 4.22 | 5.43 | 6.93 | 8.03 | 8.4 | 3349 | 667 | 551 | 445 | 307 | 114 | 26 | 0 | 0 | 22 | 177 | 414 | 626 | 7709 | 1132 | 971 | 910 | 755 | 514 | 299 | 110 | 124 | 325 | 614 | 864 | 1091 | 1163 | 0 | 0 | 0 | 2 | 65 | 177 | 387 | 356 | 148 | 28 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 15 | 1 | 0 | 0 | 0 | 4252 | 0 | 0 | 0 | 0 | 104 | 493 | 1733 | 1417 | 448 | 57 | 0 | 0 | 1227 | 0 | 0 | 0 | 0 | 10 | 79 | 597 | 452 | 82 | 7 | 0 | 0 | 4.7 | 3.9 | 4.2 | 5.3 | 5.8 | 5.7 | 4.8 | 4.9 | 4.8 | 4.4 | 4.2 | 4 | 4 | 29 | 5.5 | 4.5 | 4 | 2 | 1.4 | 0.6 | 0.3 | 0.4 | 0.5 | 1.5 | 2.8 | 5.8 | 54.6 | 12.1 | 9.4 | 14.3 | 5.7 | 4 | 1.5 | 0.8 | 1.4 | 3.3 | 4.6 | 6.1 | 16.9 | 18.7 | 0.9 | 0.7 | 0.9 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1.3 | 8.7 | 3.4 | 2.6 | 3.3 | 1.5 | 1.1 | 0.5 | 0.2 | 0.4 | 0.7 | 1.3 | 1.7 | 4.4 | 52.1 | 56.9 | 66 | 72.2 | 81.5 | 85.3 | 91.4 | 90.4 | 84.9 | 80.5 | 66.5 | 54.7 | 39.9 | 41.7 | 46.8 | 49 | 56.4 | 57.9 | 59.5 | 58.5 | 55.4 | 52.6 | 47.7 | 41.1 | 47.8 | 50.7 | 61.2 | 67.6 | 77.2 | 82 | 89.8 | 88 | 82.1 | 74 | 61.3 | 50 | 39.8 | 39.4 | 44.7 | 47.7 | 54 | 56.3 | 59.3 | 56.9 | 53.7 | 50.1 | 44.6 | 40.6 | 45 | 45.9 | 55.5 | 63.1 | 72.7 | 80.5 | 86.3 | 84.3 | 79.5 | 70.5 | 55.4 | 46.3 | 36.8 | 36.9 | 41.9 | 45.8 | 52.4 | 55.4 | 58.3 | 56.1 | 53.8 | 48.9 | 42.4 | 39.1 | 41.1 | 42.8 | 51.8 | 57.2 | 68.5 | 76.7 | 82.5 | 82 | 75.4 | 65.7 | 51.7 | 43.3 | 35.4 | 35.9 | 40.4 | 42.8 | 50.5 | 53.7 | 56.9 | 55.7 | 52.2 | 47.4 | 40.8 | 37.6 | 46.2 | 43.4 | 48.3 | 51.2 | 58.8 | 61.8 | 64.5 | 62.5 | 61.4 | 54.4 | 49.1 | 46.2 | 48 | 52.5 | 62.6 | 67.4 | 75.5 | 79.3 | 82.1 | 80.5 | 71.8 | 73.8 | 63.6 | 50 | 40.1 | 40.7 | 45.5 | 48.8 | 55.8 | 59 | 62.3 | 60.3 | 58.1 | 52 | 46.4 | 43 | 45.5 | 48.8 | 59.5 | 64.2 | 73.8 | 77.7 | 81.8 | 79.3 | 75 | 71.3 | 58.7 | 47 | 37.8 | 38.4 | 43.1 | 46.4 | 53.6 | 56.7 | 60.5 | 58.9 | 55.6 | 49.8 | 43.9 | 40.4 | 41.7 | 44.1 | 54.7 | 60.8 | 71.3 | 76.2 | 80.8 | 78.5 | 73.6 | 68.4 | 53.6 | 45.1 | 36.4 | 36.5 | 40.7 | 44.2 | 51.3 | 54.9 | 59.1 | 57.1 | 53.5 | 47.4 | 41.5 | 38.1 | 40.1 | 41 | 50.3 | 56.6 | 67.1 | 73.7 | 79.5 | 77.4 | 73.8 | 63.9 | 50 | 42.2 | 21.7 | 23 | 25 | 26.2 | 31.3 | 36.9 | 40.8 | 40.3 | 39.5 | 34.8 | 26.9 | 22.6 | 27.2 | 29.7 | 33.9 | 38.9 | 40.3 | 43.3 | 44.1 | 44.8 | 46.2 | 44.8 | 37 | 27.7 | 18.5 | 19.6 | 19 | 20.5 | 18.9 | 19.9 | 17.2 | 18.7 | 21.7 | 23.1 | 21.9 | 18.3 | 21.2 | 25 | 32.4 | 35.9 | 38.9 | 41.2 | 39.9 | 38.8 | 40.3 | 42.4 | 33 | 22.6 | 15.2 | 17 | 18.7 | 19.4 | 18.7 | 19.7 | 16.5 | 17.5 | 20.2 | 22.6 | 20.3 | 15.9 | 0.27 | 0.283 | 0.296 | 0.308 | 0.318 | 0.312 | 0.317 | 0.308 | 0.299 | 0.284 | 0.267 | 0.267 | 2.491 | 2.478 | 2.462 | 2.451 | 2.455 | 2.494 | 2.5 | 2.506 | 2.545 | 2.58 | 2.58 | 2.509 | 291 | 301 | 306 | 307 | 304 | 305 | 302 | 304 | 302 | 298 | 292 | 284 | 24 | 28 | 32 | 35 | 35 | 34 | 33 | 32 | 29 | 25 | 22 | 22 | 740 | 1013 | 1434 | 1883 | 2256 | 2620 | 2586 | 2337 | 1895 | 1335 | 861 | 629 | 103 | 130 | 147 | 171 | 192 | 147 | 123 | 99 | 79 | 97 | 64 | 97 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.59 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 157 | 74 | 20
4 | USA | CA | LAKE TAHOE | 725847 | 93230 | 38.898 | -119.995 | 6314 | 11.64 | -8 | NAP | 00-19 | 6A | 1 | 3.4 | 9.1 | -3.7 | 5.7 | 17.2 | 0.7 | 7.2 | 21.4 | 25.7 | 37.4 | 22.4 | 37.1 | 2.8 | 190 | 0.607 | 7 | 35.4 | 84.5 | 56.9 | 82.2 | 55.8 | 80 | 55 | 60.1 | 78.3 | 58.5 | 77.2 | 57 | 75.8 | 7.8 | 30 | 53.1 | 76.1 | 66.2 | 50.6 | 69.2 | 65.8 | 48.2 | 63.3 | 64.9 | 29.2 | 77.9 | 28 | 77.1 | 26.9 | 75.8 | 65.5 | 21.1 | 18.3 | 16 | -6.2 | 88.8 | 5 | 2 | -9.8 | 90.2 | -12.8 | 91.4 | -15.6 | 92.6 | -19.2 | 94 | -6.9 | 63 | 4.8 | 1.7 | -10.4 | 64.3 | -13.3 | 65.3 | -16 | 66.2 | -19.5 | 67.5 | 44.6 | 30.5 | 31.2 | 35.8 | 40.3 | 47.8 | 56 | 62.7 | 60.8 | 54.8 | 45.7 | 37.2 | 31 | 13.04 | 7.27 | 7.6 | 7.14 | 6.71 | 6.32 | 5.83 | 4.23 | 3.89 | 5.8 | 5.99 | 7.21 | 7.46 | 3149 | 605 | 527 | 440 | 292 | 116 | 17 | 0 | 0 | 25 | 155 | 384 | 588 | 7490 | 1070 | 946 | 904 | 740 | 533 | 274 | 94 | 137 | 308 | 597 | 834 | 1053 | 1167 | 0 | 0 | 0 | 2 | 48 | 196 | 395 | 335 | 168 | 22 | 1 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 3 | 24 | 7 | 1 | 0 | 0 | 0 | 2653 | 0 | 0 | 0 | 0 | 23 | 335 | 1144 | 858 | 283 | 10 | 0 | 0 | 465 | 0 | 0 | 0 | 0 | 2 | 53 | 250 | 139 | 21 | 0 | 0 | 0 | 5.3 | 4.6 | 5.5 | 6.2 | 6.3 | 5.6 | 5.6 | 4.7 | 4.7 | 4.7 | 4.7 | 5.1 | 5.6 | 22.8 | 3.6 | 3.5 | 3.3 | 1.4 | 1.2 | 0.7 | 0.4 | 0.5 | 0.6 | 1.5 | 2.5 | 3.6 | 37.4 | 10.9 | 8.1 | 11.1 | 3.3 | 3.9 | 2.5 | 1.3 | 1.7 | 2.6 | 5.7 | 6.1 | 10.1 | 12.1 | 0.2 | 0.7 | 0.6 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.2 | 5.7 | 2.5 | 2 | 2.4 | 0.8 | 0.9 | 0.7 | 0.4 | 0.4 | 0.6 | 1.3 | 1.3 | 2.6 | 55.7 | 57.5 | 63.1 | 68.9 | 77.2 | 85.3 | 88.2 | 86.3 | 82.4 | 75.4 | 63.9 | 55 | 40.3 | 40.8 | 45.1 | 48.2 | 52.6 | 57.8 | 58.6 | 56 | 53.8 | 51.8 | 47.2 | 39.4 | 50.2 | 53.2 | 58.3 | 64.7 | 72.7 | 81.1 | 85.3 | 83.5 | 79.8 | 69.8 | 59.9 | 50.5 | 38 | 38.9 | 42.4 | 46.2 | 50.6 | 55.3 | 57.9 | 55.7 | 53.1 | 49 | 43.9 | 38.1 | 46.7 | 49 | 54.6 | 61.2 | 69.3 | 77.9 | 82.9 | 81.4 | 77.5 | 66.5 | 56 | 47.6 | 36.8 | 37.4 | 40.7 | 44.3 | 49.2 | 53.5 | 56.9 | 55 | 52.4 | 47.1 | 41.8 | 36.8 | 43.5 | 44.8 | 50.4 | 56.8 | 65.4 | 74.8 | 80.5 | 79.2 | 74.8 | 63.2 | 52 | 44.6 | 35.4 | 35.3 | 38.8 | 42.5 | 47.7 | 52.3 | 56.2 | 54.6 | 52 | 45.9 | 39.6 | 36.4 | 42.4 | 43.2 | 46.2 | 50.4 | 54.6 | 60.1 | 63 | 60.3 | 57.9 | 53.4 | 48.6 | 43.8 | 50.7 | 53.9 | 60.2 | 65.4 | 70.8 | 80.4 | 78.9 | 77.6 | 74.3 | 69.7 | 60.4 | 50.1 | 40.3 | 40.5 | 43.5 | 47.5 | 52.4 | 57.5 | 61.1 | 58.5 | 55.7 | 50.9 | 45.6 | 40.9 | 47.4 | 49.7 | 56.1 | 61.7 | 69.4 | 75.9 | 78.5 | 77.3 | 74.3 | 66.1 | 57.1 | 46.8 | 37.9 | 38.4 | 41.5 | 45.3 | 50.4 | 55.5 | 59.5 | 57.2 | 54 | 48.8 | 43 | 38.7 | 44.8 | 46.8 | 52.9 | 59.1 | 66.5 | 73.8 | 78.4 | 76.6 | 74.1 | 63.4 | 53.5 | 45 | 36 | 36.2 | 39.4 | 43.2 | 48.6 | 53.5 | 58.1 | 55.9 | 52.4 | 46.6 | 40.9 | 36.7 | 42.2 | 43.6 | 49 | 55.5 | 63.5 | 71.5 | 76.8 | 75.9 | 72.9 | 60.7 | 50.5 | 43.2 | 23.4 | 22.6 | 22.9 | 23.9 | 27.6 | 32.9 | 35.4 | 36.3 | 35.4 | 30.5 | 25.5 | 22.4 | 28.1 | 29.4 | 30.9 | 34.6 | 36.4 | 38.8 | 37.9 | 39.5 | 40.8 | 37.8 | 33 | 27 | 18.1 | 17.9 | 17.2 | 18.2 | 17.4 | 17 | 15.7 | 17.3 | 19 | 20.2 | 19.7 | 17.4 | 25.2 | 25.7 | 28.7 | 32.4 | 34.8 | 36.6 | 34 | 35.8 | 37.9 | 35.1 | 30.5 | 22.8 | 17.3 | 16.3 | 16.6 | 17.7 | 17.3 | 16.6 | 14.6 | 16.4 | 18 | 19.5 | 19.3 | 16.1 | 0.248 | 0.264 | 0.273 | 0.286 | 0.296 | 0.296 | 0.3 | 0.292 | 0.282 | 0.27 | 0.252 | 0.247 | 2.54 | 2.524 | 2.524 | 2.523 | 2.533 | 2.557 | 2.577 | 2.575 | 2.612 | 2.637 | 2.632 | 2.557 | 303 | 310 | 316 | 315 | 311 | 310 | 308 | 309 | 309 | 305 | 300 | 295 | 23 | 27 | 30 | 32 | 33 | 32 | 31 | 30 | 27 | 24 | 21 | 21 | 750 | 1024 | 1435 | 1886 | 2262 | 2622 | 2568 | 2333 | 1907 | 1358 | 886 | 648 | 98 | 128 | 146 | 168 | 187 | 153 | 128 | 99 | 80 | 98 | 62 | 94 | 1.17 | N/A | N/A | N/A | N/A | N/A | -304 | -461 | N/A | N/A | 0.67 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 173 | 77 | 25
4 | USA | CA | HAYWARD | 725850 | 93228 | 37.654 | -122.115 | 43 | 14.67 | -8 | NAP | 98-19 | 3C | 1 | 37 | 39.1 | 18.4 | 13.9 | 53 | 23.7 | 18 | 50.6 | 20.9 | 52.9 | 18.8 | 53.8 | 3.3 | 60 | 0.474 | 9 | 17.4 | 87.4 | 65 | 82.7 | 64 | 78.8 | 63.1 | 67.5 | 82.1 | 65.9 | 79.1 | 64.5 | 76.1 | 10.6 | 290 | 62.3 | 84.1 | 71.1 | 61 | 80.2 | 69.4 | 59.8 | 76.7 | 68.5 | 31.8 | 82 | 30.6 | 79.1 | 29.5 | 76.2 | 81.5 | 19.4 | 17.6 | 16.1 | 33.3 | 96.4 | 2 | 4.6 | 31.9 | 99.7 | 30.8 | 102.4 | 29.7 | 105.1 | 28.2 | 108.4 | 30.2 | 70.7 | 2.3 | 3.2 | 28.6 | 73 | 27.3 | 74.9 | 26 | 76.7 | 24.3 | 79 | 59.3 | 51 | 53 | 55.8 | 57.5 | 60.6 | 63.9 | 65.9 | 66.4 | 66.7 | 63 | 56.1 | 51.1 | 7.28 | 4.22 | 4.33 | 4.78 | 4.84 | 4.63 | 5.01 | 4 | 3.68 | 5.12 | 4.59 | 4.51 | 4.56 | 110 | 39 | 18 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 41 | 2414 | 435 | 337 | 289 | 234 | 156 | 78 | 32 | 23 | 32 | 96 | 270 | 432 | 3492 | 69 | 101 | 185 | 226 | 329 | 416 | 494 | 508 | 501 | 402 | 188 | 73 | 319 | 0 | 0 | 3 | 8 | 20 | 45 | 60 | 66 | 83 | 33 | 1 | 0 | 2168 | 1 | 4 | 26 | 91 | 195 | 368 | 345 | 316 | 576 | 235 | 11 | 0 | 693 | 0 | 0 | 3 | 21 | 64 | 133 | 101 | 96 | 218 | 56 | 1 | 0 | 6.9 | 5.1 | 6.3 | 7.1 | 8.3 | 8.7 | 8.4 | 8.2 | 7.6 | 6.6 | 5.6 | 5 | 5.5 | 19.6 | 3.9 | 3.6 | 2.7 | 1.3 | 0.7 | 0.2 | 0 | 0 | 0.1 | 1 | 2.2 | 4 | 33.8 | 9.4 | 12.7 | 7.6 | 4.1 | 2.6 | 1.6 | 0.1 | 0.8 | 0.4 | 3.7 | 6.6 | 9.7 | 7.8 | 0.3 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 5.6 | 2.6 | 2.5 | 2.2 | 1 | 0.7 | 0.4 | 0 | 0.2 | 0.1 | 1 | 1.6 | 2.7 | 67.9 | 72.3 | 77.4 | 82.8 | 87.3 | 91.1 | 89 | 89.7 | 92.6 | 86.1 | 74.9 | 66.8 | 51.9 | 56.4 | 60.1 | 62.6 | 63.3 | 66.3 | 67.6 | 66.4 | 65.9 | 61.2 | 58.5 | 55 | 63.3 | 66.6 | 71.9 | 75.6 | 79.5 | 83.3 | 81.9 | 81.5 | 86.6 | 80.5 | 70.1 | 63.1 | 52.8 | 54.9 | 57.8 | 59 | 61.7 | 64.5 | 65.8 | 65.7 | 64.5 | 61.2 | 56.9 | 54.7 | 60.6 | 63.4 | 67.6 | 70 | 72.9 | 77.5 | 77.2 | 76.6 | 80.6 | 75.7 | 66.6 | 60.9 | 53.1 | 54.3 | 56.2 | 57.6 | 59.8 | 63 | 64.4 | 64.3 | 63.6 | 59.8 | 56.2 | 54 | 58.3 | 60.7 | 64.1 | 65.4 | 68.2 | 72.6 | 73.6 | 73.4 | 75.6 | 71.9 | 63.9 | 58.9 | 52.1 | 52.9 | 54.8 | 55.4 | 58.4 | 61.4 | 62.7 | 62.9 | 62.7 | 59.5 | 55.8 | 52.9 | 58.1 | 59.5 | 62 | 64.7 | 66.5 | 68.5 | 69.1 | 69 | 68.6 | 66.5 | 62.5 | 60.2 | 61.2 | 65.3 | 73.4 | 79.5 | 82.5 | 86.1 | 85.1 | 83.5 | 84.3 | 76.9 | 69.2 | 63.8 | 56.1 | 57.4 | 59.5 | 60.9 | 63.2 | 65.9 | 66.4 | 66.3 | 66.6 | 64.1 | 60.4 | 58 | 59.7 | 63.8 | 68.5 | 73.3 | 75.8 | 80.7 | 80.3 | 78.8 | 80.2 | 73.9 | 66.3 | 60.8 | 54.7 | 55.9 | 57.7 | 58.6 | 60.6 | 63.8 | 64.6 | 64.8 | 65 | 62.4 | 59 | 56.2 | 58.4 | 61.4 | 65 | 67.8 | 71.1 | 76.4 | 76.2 | 75.6 | 77.6 | 71.4 | 64.3 | 59.3 | 53.2 | 54.4 | 56.2 | 56.5 | 58.8 | 61.7 | 63.1 | 63.4 | 63.6 | 60.9 | 57.3 | 54.2 | 57.1 | 59.2 | 62.6 | 64 | 67.4 | 72.3 | 72.9 | 72.7 | 74.1 | 69.2 | 62.4 | 57.5 | 13.9 | 14.4 | 15.1 | 15.2 | 14.8 | 16 | 15.9 | 15.2 | 17.4 | 17.1 | 15.2 | 13.9 | 17.3 | 19.5 | 20.9 | 24.1 | 24.9 | 25.8 | 23 | 21.7 | 27.3 | 24.7 | 19.3 | 15.6 | 10.2 | 11 | 11.4 | 12.4 | 12 | 11.8 | 10.3 | 10 | 12.5 | 12.5 | 10.6 | 9.1 | 12.2 | 15.4 | 17.5 | 21.1 | 21.3 | 23.1 | 21.3 | 20.1 | 22.9 | 19.8 | 15 | 10.3 | 8.3 | 9.6 | 10.2 | 11.5 | 11 | 11 | 9.7 | 9.5 | 10.9 | 10.9 | 9.8 | 7.3 | 0.324 | 0.331 | 0.342 | 0.36 | 0.367 | 0.361 | 0.368 | 0.349 | 0.35 | 0.338 | 0.325 | 0.326 | 2.543 | 2.524 | 2.48 | 2.399 | 2.405 | 2.426 | 2.411 | 2.459 | 2.445 | 2.52 | 2.541 | 2.544 | 274 | 287 | 293 | 292 | 290 | 290 | 287 | 291 | 285 | 279 | 271 | 265 | 24 | 28 | 32 | 37 | 37 | 36 | 37 | 34 | 33 | 28 | 24 | 23 | 757 | 1059 | 1499 | 1955 | 2263 | 2480 | 2356 | 2105 | 1775 | 1307 | 898 | 667 | 106 | 127 | 134 | 157 | 143 | 102 | 75 | 85 | 66 | 81 | 56 | 96 | N/A | N/A | -3.65 | N/A | -1.13 | -1.64 | N/A | -313 | 374 | N/A | N/A | N/A | -2.11 | N/A | N/A | N/A | N/A | -198 | 243 | N/A | 44
4 | USA | CA | UKIAH | 725905 | 23275 | 39.126 | -123.201 | 601 | 14.38 | -8 | NAP | 94-19 | 3A | 12 | 28.5 | 30.6 | 21.1 | 16.2 | 49.2 | 24.8 | 19.3 | 46.4 | 18.1 | 51.6 | 16.1 | 50.9 | 0.3 | 310 | 0.463 | 7 | 35.6 | 100.4 | 67.4 | 97.4 | 66.6 | 93.9 | 65.6 | 70.2 | 95.2 | 68.5 | 92.8 | 67.1 | 90.7 | 7.9 | 120 | 60.8 | 81.2 | 79.5 | 58.7 | 75.4 | 77.2 | 57.1 | 71.1 | 75.1 | 34.3 | 95.3 | 32.9 | 93 | 31.7 | 90.7 | 76.8 | 15.9 | 13.4 | 12.1 | 24.8 | 106.7 | 3.1 | 2.6 | 22.6 | 108.6 | 20.7 | 110.1 | 19 | 111.5 | 16.7 | 113.4 | 23.7 | 73.2 | 3.1 | 1.9 | 21.5 | 74.6 | 19.7 | 75.8 | 18 | 76.9 | 15.7 | 78.3 | 59.5 | 47.5 | 49.3 | 52.7 | 55.8 | 62.3 | 69 | 74.8 | 73.6 | 69.6 | 61.1 | 51.8 | 46.3 | 11.36 | 4.7 | 5.27 | 5.89 | 6.4 | 6.26 | 6.38 | 5.12 | 4.54 | 5.62 | 5.57 | 5.58 | 5.07 | 410 | 104 | 70 | 38 | 16 | 1 | 0 | 0 | 0 | 0 | 1 | 44 | 136 | 2950 | 542 | 439 | 381 | 284 | 130 | 30 | 1 | 1 | 20 | 148 | 395 | 579 | 3893 | 27 | 51 | 123 | 189 | 381 | 569 | 767 | 732 | 588 | 344 | 99 | 23 | 957 | 0 | 0 | 1 | 7 | 45 | 149 | 303 | 268 | 158 | 26 | 0 | 0 | 14783 | 0 | 7 | 97 | 311 | 961 | 2335 | 4218 | 3703 | 2408 | 711 | 32 | 0 | 7839 | 0 | 0 | 15 | 96 | 404 | 1194 | 2456 | 2102 | 1299 | 271 | 2 | 0 | 3.7 | 2.6 | 3.4 | 3.9 | 4.5 | 4.8 | 5.1 | 4.6 | 4 | 3.4 | 2.7 | 2.3 | 2.6 | 42 | 8.3 | 6.8 | 5.6 | 2.6 | 1 | 0.3 | 0 | 0.2 | 0.5 | 2 | 5.9 | 8 | 82.4 | 25 | 22.3 | 18.7 | 9.8 | 6.4 | 2.2 | 0.9 | 1.5 | 3.2 | 8.2 | 17.4 | 22.4 | 15 | 0.5 | 0.4 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 12.8 | 5.6 | 5 | 4.3 | 2.2 | 1.4 | 0.5 | 0.2 | 0.4 | 0.8 | 1.9 | 4.3 | 6 | 69.9 | 74.5 | 82 | 88.2 | 95.5 | 102.4 | 105.5 | 104.3 | 101.5 | 93.4 | 78.9 | 65.1 | 53.3 | 56.7 | 59.6 | 61.4 | 65.6 | 69.1 | 69.5 | 67.7 | 65.2 | 62.4 | 58.6 | 52.3 | 63.8 | 69.2 | 76.2 | 82.4 | 89.7 | 97.1 | 100.4 | 99.3 | 97.1 | 87 | 72.5 | 61 | 51.8 | 54.4 | 56.9 | 60.1 | 63.3 | 67.3 | 68.1 | 66.8 | 64.8 | 60.5 | 56.3 | 52.3 | 59.4 | 64 | 71.5 | 76.9 | 84.3 | 91.7 | 97.1 | 95.4 | 92.8 | 82 | 66.5 | 57.9 | 51.2 | 51.9 | 55.3 | 58.2 | 61.6 | 65.1 | 67.5 | 65.5 | 63.9 | 59.1 | 54 | 52 | 55.9 | 59.2 | 65.8 | 70.8 | 79.2 | 87.2 | 93 | 91.6 | 88.4 | 76.9 | 62 | 55.5 | 50.8 | 51 | 52.9 | 55.3 | 59.6 | 63.5 | 66.5 | 65.1 | 62.9 | 57.5 | 53 | 50.9 | 57.4 | 59.1 | 61.5 | 63.9 | 67.9 | 72.2 | 72.9 | 70.6 | 69.5 | 65.2 | 61.3 | 57.8 | 62.1 | 69.4 | 78.9 | 83.7 | 91.1 | 97.6 | 98.7 | 97.4 | 95.6 | 84.9 | 74 | 60.3 | 54.8 | 56.3 | 58.7 | 60.7 | 65.2 | 69 | 70.7 | 68.6 | 67.1 | 62.8 | 58.4 | 55.8 | 58.5 | 64.7 | 73.7 | 79.4 | 86.5 | 92.9 | 95.7 | 94 | 91.2 | 81.2 | 67.4 | 58.1 | 53.3 | 54.1 | 56.2 | 58.8 | 62.7 | 66.6 | 69 | 67.4 | 65.2 | 60.8 | 56.3 | 53.8 | 56.9 | 60.7 | 67.7 | 75.3 | 82 | 88.6 | 93.3 | 92.1 | 89.1 | 77.8 | 63.2 | 56.1 | 51.4 | 52.1 | 54 | 56.3 | 60.2 | 64.4 | 67.4 | 66 | 63.4 | 58.9 | 54.4 | 51.7 | 55.4 | 57.8 | 63 | 69.3 | 76.9 | 84.7 | 90.9 | 89.6 | 85.8 | 73.4 | 60.1 | 54.5 | 18.7 | 20 | 22.7 | 24.7 | 27.9 | 31.2 | 35.6 | 36.4 | 35.4 | 30.7 | 21.6 | 18.3 | 27.4 | 30.8 | 34.8 | 36.9 | 38.9 | 39.8 | 40.9 | 41.7 | 43.3 | 41 | 31.5 | 23.9 | 16.5 | 17 | 17.2 | 17.1 | 16.2 | 15.2 | 15 | 15.1 | 16.4 | 17.3 | 16.6 | 15.1 | 18.6 | 24.4 | 29.6 | 33.5 | 35.3 | 37 | 38 | 38.5 | 39 | 34.9 | 24.3 | 14.5 | 12.4 | 14.3 | 15.6 | 16.2 | 15.9 | 15.4 | 15.5 | 15.4 | 15.9 | 15.9 | 13.7 | 10.4 | 0.316 | 0.319 | 0.324 | 0.346 | 0.339 | 0.343 | 0.341 | 0.332 | 0.328 | 0.32 | 0.312 | 0.317 | 2.559 | 2.55 | 2.548 | 2.445 | 2.505 | 2.501 | 2.508 | 2.525 | 2.525 | 2.588 | 2.582 | 2.552 | 274 | 289 | 298 | 295 | 298 | 295 | 295 | 296 | 292 | 285 | 273 | 264 | 23 | 27 | 30 | 35 | 34 | 34 | 33 | 32 | 30 | 25 | 23 | 22 | 692 | 980 | 1393 | 1864 | 2245 | 2501 | 2422 | 2133 | 1765 | 1250 | 816 | 589 | 112 | 138 | 145 | 160 | 141 | 120 | 87 | 81 | 75 | 95 | 73 | 104 | 0.7 | N/A | -1.94 | N/A | -0.68 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | -2.43 | N/A | N/A | N/A | N/A | N/A | 243 | 70 | 36
4 | USA | CA | RED BLUFF | 725910 | 24216 | 40.152 | -122.254 | 353 | 14.51 | -8 | NAP | 95-19 | 3A | 12 | 30.6 | 33.3 | 12.1 | 10.3 | 56.4 | 16.5 | 12.8 | 56.6 | 34.5 | 52.7 | 30 | 50.7 | 4.9 | 320 | 0.486 | 7 | 30.7 | 105.1 | 68.3 | 101.7 | 67.3 | 98.9 | 66.7 | 72.5 | 95 | 70.8 | 93.2 | 69.3 | 91.6 | 8.6 | 150 | 65.2 | 94.3 | 81.6 | 63.2 | 88 | 80.4 | 61.2 | 81.8 | 78.9 | 36.2 | 95.6 | 34.8 | 93 | 33.5 | 91.9 | 79.3 | 26 | 22.1 | 18.7 | 25.6 | 111.2 | 2.9 | 2.4 | 23.5 | 113 | 21.7 | 114.4 | 20.1 | 115.8 | 18 | 117.5 | 23.8 | 75.8 | 3.3 | 2 | 21.4 | 77.2 | 19.5 | 78.4 | 17.6 | 79.5 | 15.2 | 81 | 63.5 | 47.6 | 50.7 | 55 | 59.7 | 68 | 77 | 82.3 | 80.1 | 75 | 64.9 | 53.7 | 47.2 | 13.83 | 5.28 | 5.6 | 6.23 | 7.15 | 7.59 | 7.41 | 5.28 | 4.89 | 6.41 | 6.39 | 6.19 | 5.34 | 336 | 109 | 53 | 21 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 116 | 2483 | 539 | 400 | 314 | 191 | 55 | 6 | 0 | 0 | 5 | 81 | 341 | 551 | 5268 | 35 | 73 | 177 | 296 | 559 | 809 | 1000 | 934 | 751 | 461 | 143 | 30 | 1941 | 0 | 0 | 5 | 32 | 149 | 365 | 535 | 469 | 306 | 77 | 3 | 0 | 26682 | 5 | 14 | 125 | 530 | 2082 | 4996 | 7642 | 6292 | 3882 | 1049 | 65 | 0 | 15219 | 0 | 0 | 19 | 174 | 976 | 2883 | 4787 | 3813 | 2169 | 389 | 9 | 0 | 7.7 | 7.1 | 8.8 | 8.7 | 8.5 | 8.3 | 8.4 | 6.8 | 6.4 | 6.9 | 7.4 | 7 | 7.8 | 22.6 | 4.1 | 3.6 | 3 | 1.4 | 0.8 | 0.4 | 0.1 | 0.2 | 0.5 | 1.3 | 3.3 | 3.7 | 49 | 10.2 | 8.6 | 9.2 | 4.9 | 3.3 | 1.6 | 0.7 | 1.6 | 5 | 5.2 | 8.4 | 10.3 | 7.2 | 0.2 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 7.6 | 2.5 | 2.8 | 1.9 | 1.3 | 0.9 | 0.5 | 0.2 | 0.4 | 0.9 | 1.4 | 2.4 | 2.5 | 73.5 | 76.4 | 82.6 | 90.1 | 99.4 | 108.4 | 109.9 | 108 | 104.4 | 94.4 | 80.9 | 69.1 | 52 | 56 | 58.5 | 62.3 | 66.4 | 68.5 | 69.6 | 69.9 | 65.7 | 62.7 | 57.7 | 50.7 | 66.8 | 70.7 | 77.4 | 85.1 | 94.3 | 102.8 | 105.3 | 103.1 | 99.4 | 88.4 | 74.9 | 63.3 | 49.8 | 53.2 | 57.1 | 60.2 | 64.5 | 67.1 | 69 | 67.4 | 65 | 60.4 | 56.1 | 49.3 | 61.4 | 65.6 | 73 | 80.6 | 90.1 | 98.5 | 102 | 99.7 | 96.1 | 84.3 | 70.2 | 59.4 | 49.4 | 51 | 55.6 | 59 | 63.1 | 66.1 | 68 | 67.2 | 64 | 59.1 | 54.4 | 49.4 | 56.8 | 61.4 | 68.3 | 75.3 | 85.4 | 94.3 | 98.9 | 96.7 | 92.4 | 80 | 65.2 | 56.5 | 48.5 | 50.3 | 53.7 | 56.8 | 61.3 | 64.8 | 67.7 | 66 | 63.3 | 57.6 | 52.6 | 49.4 | 56.5 | 58.5 | 61.7 | 65.5 | 70 | 74.4 | 74.5 | 75.5 | 71.3 | 65.3 | 61.3 | 57.4 | 61.2 | 67.1 | 74.6 | 82.2 | 90.7 | 95.9 | 97.1 | 98.8 | 91.7 | 85.7 | 73.9 | 60 | 53.7 | 56.3 | 59.3 | 62.5 | 67.3 | 71 | 72.7 | 71.6 | 68.2 | 63.1 | 58.8 | 55 | 58.3 | 64.6 | 72.2 | 79.6 | 88.3 | 92.5 | 95.9 | 93.5 | 89.6 | 82.7 | 68.5 | 57.3 | 52.2 | 54.2 | 57.4 | 60.4 | 65.1 | 68.8 | 71.1 | 69.7 | 66.4 | 61.4 | 56.8 | 53.1 | 57 | 61.6 | 68.6 | 76.2 | 85.4 | 90.5 | 94.2 | 91.4 | 88.9 | 78.4 | 65 | 55.7 | 50.7 | 52.3 | 55.4 | 58.4 | 63 | 67.1 | 69.7 | 68.1 | 64.8 | 59.6 | 55 | 51.1 | 55.8 | 59.1 | 65.6 | 72 | 81.7 | 89.4 | 92.9 | 90.2 | 87.8 | 75.1 | 62.3 | 54.4 | 17.1 | 18.4 | 21 | 23.2 | 25.7 | 27.6 | 30.7 | 31.1 | 30.2 | 26 | 20.1 | 16.5 | 27.8 | 27.7 | 29.6 | 31.8 | 33.2 | 33.1 | 34.6 | 35 | 35.3 | 33 | 28.8 | 23.9 | 14.8 | 14.1 | 14.3 | 13.6 | 12.3 | 11.2 | 11.1 | 11.9 | 12.5 | 13.5 | 13.8 | 13.6 | 17.9 | 20.4 | 25.4 | 29.1 | 30.7 | 30.3 | 31.1 | 31.1 | 31 | 28 | 22.3 | 12.9 | 11 | 11.5 | 13.4 | 13.5 | 12 | 11.4 | 10.9 | 11.4 | 11.6 | 12.3 | 11.6 | 9.1 | 0.314 | 0.316 | 0.336 | 0.351 | 0.341 | 0.349 | 0.354 | 0.337 | 0.339 | 0.329 | 0.31 | 0.314 | 2.528 | 2.53 | 2.478 | 2.428 | 2.497 | 2.478 | 2.452 | 2.494 | 2.48 | 2.522 | 2.553 | 2.527 | 271 | 288 | 292 | 293 | 297 | 293 | 290 | 294 | 287 | 279 | 271 | 262 | 23 | 27 | 31 | 35 | 34 | 34 | 35 | 33 | 31 | 27 | 23 | 22 | 658 | 949 | 1346 | 1833 | 2258 | 2572 | 2608 | 2320 | 1855 | 1262 | 774 | 557 | 121 | 135 | 169 | 184 | 161 | 140 | 82 | 80 | 75 | 108 | 81 | 111 | 1.06 | N/A | -2.29 | N/A | N/A | N/A | -74 | -257 | 364 | 202 | 0.67 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 209 | 49 | 23
4 | USA | CA | REDDING | 725920 | 24257 | 40.518 | -122.299 | 497 | 14.43 | -8 | NAP | 94-19 | 3A | 12 | 29.4 | 31.8 | 11.1 | 9.9 | 55.2 | 15.5 | 12.3 | 55.7 | 34.1 | 51.7 | 28.7 | 52.8 | 1.2 | 30 | 0.459 | 7 | 31 | 105.4 | 68 | 102.4 | 67.1 | 99.4 | 66 | 71.4 | 96.5 | 69.9 | 94.5 | 68.5 | 92.7 | 7.8 | 160 | 63.5 | 89.4 | 79.4 | 61.4 | 82.8 | 78.3 | 59.5 | 77.3 | 77 | 35.4 | 97.3 | 34.1 | 94.1 | 32.9 | 93 | 76.8 | 25.4 | 20 | 16.8 | 24.5 | 111.2 | 3.2 | 2.7 | 22.1 | 113.1 | 20.2 | 114.6 | 18.4 | 116.1 | 16.1 | 118 | 22.9 | 74.1 | 3.1 | 1.6 | 20.7 | 75.2 | 18.8 | 76.2 | 17.1 | 77.1 | 14.8 | 78.3 | 63.2 | 47.4 | 50.1 | 54.4 | 59.1 | 67.7 | 76.8 | 83 | 80.6 | 74.9 | 64.2 | 52.7 | 46.6 | 14.26 | 5.59 | 6.04 | 6.55 | 7.4 | 7.8 | 7.83 | 5.32 | 4.92 | 6.36 | 6.66 | 6.42 | 5.56 | 399 | 116 | 67 | 29 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 135 | 2619 | 545 | 419 | 334 | 207 | 63 | 8 | 0 | 0 | 6 | 96 | 370 | 571 | 5218 | 37 | 68 | 165 | 282 | 550 | 804 | 1023 | 948 | 747 | 439 | 126 | 29 | 1961 | 0 | 1 | 6 | 30 | 147 | 362 | 558 | 483 | 302 | 70 | 2 | 0 | 27663 | 6 | 17 | 124 | 505 | 1980 | 4967 | 8084 | 6758 | 4079 | 1074 | 68 | 1 | 15939 | 0 | 1 | 19 | 161 | 904 | 2852 | 5123 | 4161 | 2298 | 409 | 11 | 0 | 5.8 | 5.2 | 6.6 | 6.6 | 6.5 | 6.5 | 6.7 | 5.6 | 5.1 | 5.2 | 5.5 | 4.6 | 5.4 | 37.9 | 7 | 5.7 | 5.2 | 2.5 | 1.6 | 0.7 | 0.1 | 0.4 | 0.9 | 2 | 5.2 | 6.6 | 73.1 | 27 | 15.8 | 16.4 | 9.2 | 7.7 | 2.6 | 3.3 | 5.5 | 7.4 | 8.8 | 16.2 | 17.7 | 20.1 | 0.3 | 0.2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 11.1 | 5.3 | 4.1 | 3.7 | 2 | 1.9 | 0.7 | 0.5 | 0.9 | 1.5 | 1.9 | 3.9 | 4.6 | 74.2 | 76.8 | 82.7 | 89.7 | 98.7 | 108.1 | 110.3 | 108.4 | 104.3 | 95.2 | 81.1 | 69.3 | 52.2 | 55.9 | 58.2 | 61 | 65.2 | 68.5 | 69.5 | 69.1 | 65.4 | 62.4 | 57.7 | 50.4 | 67.9 | 71.1 | 77.5 | 84.8 | 93.7 | 102.6 | 106 | 103.9 | 99.9 | 88.8 | 75 | 63.9 | 50.1 | 52.9 | 56.9 | 59.8 | 64.4 | 67.2 | 68.7 | 67.2 | 64.1 | 60.8 | 56.1 | 48.9 | 62.2 | 66.3 | 73 | 80.2 | 89.6 | 98.4 | 102.9 | 100.5 | 96.5 | 84.5 | 70.2 | 59.8 | 48.9 | 51.1 | 55 | 58.6 | 62.6 | 65.7 | 67.9 | 66.2 | 63.6 | 58.9 | 54.2 | 48.7 | 57.8 | 61.6 | 68.3 | 75 | 85 | 94.3 | 99.7 | 97.5 | 93 | 80.1 | 65.1 | 56.4 | 48 | 49.7 | 53 | 56.6 | 61 | 64.4 | 66.9 | 65.3 | 63 | 57.5 | 52 | 48.7 | 56.3 | 58.3 | 60.9 | 64.9 | 69.2 | 72.7 | 73.6 | 72.6 | 71.1 | 64.9 | 61.2 | 57.1 | 62.2 | 68 | 75.3 | 82.4 | 89 | 95.9 | 99 | 100.5 | 91 | 87 | 74.6 | 59.4 | 53.7 | 56.3 | 58.8 | 62.1 | 66.5 | 70 | 71.8 | 70.3 | 67.8 | 62.9 | 58.6 | 54.5 | 59.2 | 64.9 | 72.4 | 79.4 | 87.6 | 93.6 | 98.1 | 95.3 | 91.1 | 83.4 | 69.4 | 57.2 | 52 | 54 | 56.9 | 59.9 | 64.6 | 68.1 | 70.4 | 68.6 | 65.9 | 61.1 | 56.5 | 52.6 | 57.4 | 62 | 68.7 | 76.1 | 85.1 | 92.2 | 96.1 | 93.2 | 89.6 | 79.3 | 65.3 | 55.6 | 50.6 | 51.9 | 54.8 | 57.9 | 62.7 | 66.3 | 69 | 67.2 | 64.2 | 59.3 | 54.7 | 50.5 | 56.3 | 58.8 | 65.3 | 72.1 | 81.4 | 89.6 | 93.9 | 91.4 | 88.4 | 75.3 | 62 | 54.6 | 17.7 | 18.6 | 20.7 | 22.9 | 25.3 | 27.6 | 31 | 32.2 | 31.1 | 26.7 | 20.8 | 16.7 | 29.7 | 28.5 | 29.5 | 31.5 | 32.6 | 32.5 | 34.7 | 35.9 | 37 | 34.6 | 30.6 | 25.2 | 15.6 | 14.5 | 13.8 | 13 | 10.8 | 9.6 | 9.5 | 10.3 | 11.8 | 13.4 | 14.9 | 14.3 | 19.7 | 21.8 | 25.4 | 28.7 | 29.8 | 30.8 | 31.9 | 32.5 | 32.4 | 30 | 24.3 | 13.9 | 11.8 | 12.2 | 12.9 | 12.7 | 10.8 | 9.9 | 9.4 | 10 | 11.1 | 12.4 | 12.8 | 9.6 | 0.313 | 0.319 | 0.329 | 0.347 | 0.351 | 0.35 | 0.354 | 0.341 | 0.339 | 0.329 | 0.309 | 0.314 | 2.535 | 2.524 | 2.508 | 2.443 | 2.471 | 2.488 | 2.473 | 2.5 | 2.494 | 2.533 | 2.566 | 2.528 | 271 | 286 | 294 | 294 | 294 | 292 | 291 | 292 | 286 | 278 | 271 | 260 | 23 | 27 | 30 | 35 | 35 | 34 | 34 | 32 | 30 | 26 | 22 | 22 | 642 | 927 | 1313 | 1803 | 2233 | 2555 | 2599 | 2309 | 1840 | 1242 | 751 | 539 | 122 | 134 | 174 | 186 | 165 | 145 | 83 | 82 | 76 | 113 | 86 | 113 | 0.92 | N/A | -2.66 | N/A | N/A | N/A | -67 | -167 | 299 | 184 | N/A | N/A | N/A | 0.76 | N/A | N/A | N/A | N/A | 184 | 47 | 16
4 | USA | CA | SALINAS | 725930 | 23233 | 36.664 | -121.608 | 74 | 14.66 | -8 | NAP | 94-19 | 3C | 12 | 34.3 | 36.7 | 21.6 | 16.3 | 51.9 | 25.6 | 19.7 | 48.7 | 26.9 | 55.9 | 24.6 | 55.1 | 5.1 | 120 | 0.525 | 9 | 18.1 | 83.6 | 61.9 | 79 | 61 | 75.3 | 60.6 | 65 | 77.8 | 63.6 | 74.8 | 62.4 | 72.5 | 9.3 | 300 | 60.6 | 79.3 | 67.5 | 59.1 | 75.1 | 66.4 | 58.1 | 72.2 | 65.5 | 29.8 | 77.8 | 28.9 | 74.9 | 28 | 72.6 | 80.6 | 20.9 | 18.6 | 17 | 30.1 | 94.5 | 2.7 | 4.4 | 28.1 | 97.7 | 26.5 | 100.3 | 25 | 102.8 | 23 | 106 | 28.2 | 69.3 | 2.8 | 3.2 | 26.2 | 71.6 | 24.5 | 73.4 | 23 | 75.2 | 21 | 77.5 | 58.1 | 52.3 | 53.1 | 55.3 | 56.6 | 59 | 61.4 | 62.6 | 63.7 | 63.9 | 61.3 | 56.2 | 51.4 | 6.14 | 5.09 | 5.06 | 4.71 | 4.64 | 3.69 | 3.44 | 2.77 | 2.98 | 4.04 | 4.89 | 5.33 | 4.86 | 117 | 34 | 21 | 9 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 41 | 2641 | 393 | 334 | 304 | 257 | 193 | 120 | 85 | 62 | 66 | 139 | 268 | 420 | 3075 | 106 | 108 | 172 | 202 | 280 | 341 | 392 | 424 | 418 | 350 | 196 | 86 | 122 | 0 | 1 | 2 | 5 | 7 | 11 | 12 | 21 | 34 | 24 | 5 | 0 | 1131 | 12 | 21 | 40 | 86 | 94 | 117 | 57 | 101 | 267 | 264 | 68 | 4 | 331 | 1 | 1 | 7 | 29 | 30 | 38 | 9 | 23 | 85 | 92 | 16 | 0 | 7.8 | 7.4 | 7.7 | 7.5 | 8.1 | 9 | 9.3 | 8.6 | 8 | 7.2 | 6.7 | 6.6 | 7.4 | 12.4 | 2.4 | 2.2 | 2 | 1 | 0.2 | 0.1 | 0 | 0 | 0.2 | 0.5 | 1.7 | 2 | 23.7 | 7.9 | 10 | 6 | 5.7 | 1.9 | 0.6 | 0.6 | 0.7 | 1.2 | 1.9 | 4.8 | 5.1 | 6.4 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5 | 2 | 2.2 | 1.5 | 1.1 | 0.4 | 0.1 | 0.1 | 0.1 | 0.4 | 0.6 | 1.4 | 1.3 | 75.1 | 77.5 | 79 | 84 | 84 | 85 | 79.8 | 82.5 | 89.6 | 89.5 | 81.8 | 72 | 55.1 | 58.6 | 59.6 | 61.8 | 62.8 | 63.3 | 64.4 | 64.6 | 64.3 | 62.8 | 59.4 | 52.9 | 69.2 | 70.7 | 72.4 | 74.2 | 74.9 | 76.3 | 74.7 | 76 | 81.2 | 81.2 | 73.9 | 66.4 | 54.5 | 56.7 | 57.4 | 58.5 | 60.2 | 61.6 | 62.5 | 63.2 | 62.8 | 59.8 | 57.1 | 54 | 64.3 | 65.4 | 67.8 | 69 | 69.9 | 71.8 | 71.8 | 72.9 | 75.7 | 75 | 68.9 | 63.1 | 54.3 | 54.7 | 56.1 | 56.8 | 58.4 | 60.1 | 61.6 | 62.3 | 62 | 58.6 | 56 | 53.6 | 60.8 | 61.8 | 64 | 65 | 66.3 | 68.8 | 69.3 | 70.4 | 72.1 | 70.4 | 65 | 60.1 | 53.5 | 53.5 | 54.8 | 55.2 | 56.9 | 59 | 60.4 | 61.1 | 61.1 | 58 | 55.3 | 52.8 | 60.3 | 62.2 | 62 | 63.4 | 65 | 65.7 | 65.4 | 66.1 | 67.1 | 65.2 | 62.4 | 60.6 | 65.2 | 71.2 | 75.6 | 77.3 | 79.1 | 81.4 | 78 | 78.6 | 81.7 | 78.6 | 73.5 | 65 | 57.7 | 58.9 | 59.3 | 60.2 | 61.4 | 62.5 | 63.2 | 64.1 | 64.5 | 62.7 | 60.1 | 58.2 | 62.9 | 66.3 | 68.4 | 70.9 | 72.1 | 74.1 | 73.3 | 74.6 | 76.6 | 74.6 | 69.1 | 62 | 55.9 | 56.7 | 57.4 | 58.1 | 59.3 | 60.8 | 61.9 | 62.7 | 63 | 61.1 | 58.5 | 56.1 | 61.4 | 63.7 | 64.7 | 67.2 | 68.3 | 70.2 | 71 | 71.9 | 73.4 | 71.3 | 66 | 59.8 | 54.2 | 54.7 | 55.7 | 56.1 | 57.5 | 59.4 | 60.6 | 61.6 | 61.7 | 59.5 | 56.9 | 54.2 | 59.6 | 60.5 | 62.5 | 63.9 | 65.3 | 67.7 | 68.3 | 70 | 71.1 | 67.8 | 63.3 | 58.3 | 18.7 | 18.3 | 19.4 | 18.5 | 15.8 | 15.5 | 14.3 | 15.2 | 18.1 | 21.6 | 20.7 | 18.7 | 24.5 | 25.3 | 26.3 | 26.8 | 24.3 | 22.6 | 18.6 | 19.6 | 26.7 | 30.7 | 26.7 | 23.1 | 13.6 | 13.5 | 13.5 | 13.6 | 11.7 | 10.8 | 8.7 | 8.9 | 12 | 14 | 13.5 | 13.3 | 18.4 | 20.8 | 21.9 | 23.7 | 21 | 20 | 17.4 | 18.5 | 22.1 | 24.8 | 21.6 | 15.3 | 11.3 | 11.8 | 12 | 12.7 | 10.7 | 9.9 | 8.3 | 8.6 | 10.3 | 12.1 | 11.8 | 10.1 | 0.318 | 0.323 | 0.325 | 0.349 | 0.36 | 0.347 | 0.354 | 0.339 | 0.345 | 0.329 | 0.311 | 0.312 | 2.544 | 2.538 | 2.533 | 2.446 | 2.43 | 2.476 | 2.476 | 2.507 | 2.486 | 2.554 | 2.571 | 2.575 | 279 | 291 | 300 | 296 | 292 | 295 | 292 | 295 | 289 | 285 | 279 | 274 | 25 | 28 | 31 | 35 | 36 | 35 | 35 | 33 | 32 | 27 | 24 | 23 | 836 | 1112 | 1565 | 1981 | 2309 | 2527 | 2399 | 2170 | 1839 | 1369 | 965 | 737 | 91 | 122 | 129 | 167 | 123 | 88 | 60 | 65 | 56 | 77 | 50 | 91 | 0.74 | N/A | -2.43 | N/A | N/A | N/A | N/A | -317 | 301 | N/A | 0.74 | N/A | -2.16 | N/A | N/A | N/A | N/A | -229 | 270 | 67 | 40
4 | USA | CA | WOODLEY ISLAND | 725940 | 24213 | 40.8097 | -124.16 | 20 | 14.69 | -8 | NAP | 94-19 | 4C | 12 | 33.1 | 35.4 | 26.9 | 20.9 | 41.8 | 30 | 24 | 40.5 | 26.1 | 57.3 | 22.4 | 53.9 | 3.2 | 90 | 0.539 | 8 | 8.6 | 68.9 | 59.1 | 66.4 | 58.9 | 64.5 | 58.2 | 61.6 | 66.2 | 60.3 | 64.5 | 59.3 | 63.2 | 9.4 | 340 | 59.6 | 76.3 | 63.2 | 58.4 | 73.1 | 62 | 57.4 | 70.3 | 61 | 27.4 | 66.5 | 26.6 | 64.8 | 25.9 | 63.3 | 67.6 | 20.4 | 18.2 | 16.3 | 29.4 | 78.5 | 1.6 | 4.9 | 28.3 | 82 | 27.3 | 84.8 | 26.4 | 87.5 | 25.3 | 91.1 | 28.5 | 63.8 | 1.6 | 1.8 | 27.3 | 65.1 | 26.4 | 66.2 | 25.4 | 67.2 | 24.2 | 68.5 | 51.8 | 47.8 | 47.7 | 48.5 | 49.7 | 52.1 | 54.9 | 56.7 | 57.3 | 55.9 | 53.5 | 49.9 | 47.4 | 5.43 | 5.11 | 4.76 | 4.13 | 3.8 | 3.38 | 2.7 | 2.6 | 2.9 | 3.88 | 4.25 | 4.75 | 5.42 | 534 | 103 | 94 | 78 | 49 | 16 | 1 | 0 | 0 | 1 | 14 | 59 | 119 | 4818 | 533 | 485 | 511 | 458 | 400 | 303 | 258 | 240 | 275 | 356 | 452 | 547 | 1193 | 35 | 29 | 32 | 41 | 81 | 148 | 207 | 226 | 177 | 123 | 57 | 37 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 1 | 1 | 2 | 1 | 2 | 11 | 5 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 6 | 5.6 | 6.1 | 6.9 | 7.1 | 6.9 | 6.8 | 5.8 | 5.2 | 4.9 | 4.9 | 5.1 | 6.1 | 39.1 | 6.4 | 5.2 | 5.4 | 3.2 | 1.7 | 0.6 | 0.2 | 0.4 | 0.7 | 2.4 | 6.1 | 7.1 | 67.2 | 13.9 | 13.9 | 11.2 | 11.3 | 6.1 | 3.1 | 1.1 | 3.4 | 3.3 | 6.8 | 16.6 | 23.3 | 21.7 | 0.7 | 0.6 | 1.2 | 0.4 | 0.1 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0.5 | 10.1 | 3.3 | 2.8 | 2.7 | 2.3 | 1.2 | 0.6 | 0.2 | 0.7 | 0.8 | 1.8 | 3.8 | 4.7 | 64 | 65.2 | 64.4 | 67.2 | 69 | 67.6 | 68 | 69.8 | 73.7 | 72.4 | 66.5 | 63.1 | 54.2 | 54.9 | 53.5 | 55.1 | 59.2 | 58.6 | 60.2 | 61.1 | 61.1 | 57.8 | 55.7 | 54.9 | 60.5 | 60.8 | 60 | 61.3 | 62.7 | 63.4 | 65 | 66.9 | 67.9 | 66.8 | 62.2 | 60.4 | 53.5 | 54 | 53.1 | 54.5 | 57 | 57.2 | 59.3 | 60.4 | 60.2 | 57.6 | 55.8 | 54.4 | 58.2 | 58 | 57.5 | 58 | 59.7 | 61.6 | 63.2 | 65 | 65.3 | 63.5 | 59.8 | 58.2 | 53 | 52.4 | 52 | 52.9 | 55.1 | 56.5 | 58.3 | 59.6 | 59 | 57.2 | 55.1 | 53.6 | 56.1 | 55.5 | 55.5 | 56.1 | 58 | 60.2 | 61.8 | 63 | 63.1 | 61.3 | 58 | 56.3 | 52.1 | 51 | 51.2 | 51.6 | 53.9 | 55.6 | 57.6 | 58.5 | 58 | 56 | 54 | 52.5 | 57.6 | 58 | 56.6 | 58.2 | 61.2 | 60.7 | 62 | 62.8 | 63.3 | 62.2 | 59.4 | 58.2 | 59.9 | 61.5 | 60.3 | 63.6 | 66.5 | 65.5 | 65.9 | 67.1 | 70.1 | 66.2 | 62.1 | 60.4 | 55.7 | 55.7 | 54.7 | 55.3 | 57.8 | 58.8 | 60.1 | 61.3 | 61.3 | 59.9 | 57.8 | 56.5 | 58.5 | 59.4 | 57.8 | 59.3 | 61.6 | 62 | 63.8 | 65.8 | 66 | 64.1 | 60.4 | 58.7 | 54.2 | 53.5 | 53.2 | 53.7 | 55.8 | 57.3 | 58.9 | 60 | 59.9 | 58.5 | 56.3 | 54.9 | 57 | 56.3 | 56.2 | 56.9 | 59.1 | 60.5 | 62.4 | 64.1 | 64.1 | 62.2 | 58.8 | 57.4 | 52.6 | 51.8 | 51.8 | 52.4 | 54.4 | 56.2 | 57.8 | 58.9 | 58.7 | 56.8 | 54.7 | 53 | 55.4 | 54.7 | 54.7 | 55.6 | 57.3 | 59.3 | 61.1 | 62.5 | 62.4 | 60.3 | 57.2 | 55.5 | 10.9 | 11.2 | 10.9 | 10.6 | 9.4 | 9.7 | 8.3 | 8.6 | 11.4 | 12.2 | 11.3 | 11.1 | 13.1 | 14.5 | 13.6 | 14.2 | 12.6 | 12.5 | 11.1 | 12.8 | 16.9 | 16.9 | 13.5 | 11.6 | 8.3 | 8.8 | 8.3 | 8.7 | 7.9 | 7.6 | 6.4 | 7.4 | 9.3 | 9.6 | 8.4 | 7.6 | 9.3 | 10.6 | 10.9 | 12 | 11 | 10.7 | 10.2 | 11.5 | 14 | 13 | 9.9 | 7.8 | 7.3 | 7.6 | 7.7 | 8.1 | 7.5 | 7 | 6.1 | 7 | 8.3 | 8.8 | 7.3 | 6.7 | 0.327 | 0.334 | 0.337 | 0.36 | 0.365 | 0.355 | 0.368 | 0.355 | 0.346 | 0.34 | 0.321 | 0.331 | 2.535 | 2.521 | 2.531 | 2.428 | 2.453 | 2.492 | 2.461 | 2.501 | 2.503 | 2.55 | 2.582 | 2.521 | 265 | 280 | 291 | 290 | 289 | 291 | 286 | 287 | 284 | 274 | 265 | 252 | 23 | 27 | 30 | 35 | 35 | 34 | 35 | 32 | 30 | 26 | 22 | 22 | 597 | 857 | 1241 | 1701 | 2077 | 2313 | 2271 | 1963 | 1621 | 1107 | 683 | 493 | 93 | 121 | 126 | 152 | 133 | 133 | 112 | 99 | 84 | 93 | 74 | 91 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.92 | N/A | N/A | N/A | N/A | 212 | 9 | 12
4 | USA | CA | CALIFORNIA REDWOOD COAST | 725945 | 24283 | 40.978 | -124.109 | 200 | 14.59 | -8 | NAP | 94-19 | 4C | 12 | 31.4 | 33.6 | 26 | 20.1 | 41.5 | 29.1 | 23.3 | 38.9 | 24.6 | 54.4 | 21.2 | 53.3 | 3.5 | 90 | 0.555 | 8 | 11.4 | 70.9 | 59.4 | 67.9 | 59.3 | 65.7 | 58.4 | 62.4 | 67.1 | 61.1 | 65.6 | 60 | 63.9 | 9.7 | 340 | 60.7 | 80 | 63.7 | 59.2 | 75.6 | 62.3 | 58.1 | 72.7 | 61.3 | 28.1 | 67.6 | 27.1 | 65.5 | 26.4 | 64 | 68.9 | 20.2 | 18.3 | 16.4 | 27.9 | 81.9 | 2.1 | 5 | 26.4 | 85.5 | 25.2 | 88.5 | 24 | 91.3 | 22.5 | 95 | 27.2 | 65.1 | 2.2 | 1.8 | 25.6 | 66.4 | 24.3 | 67.4 | 23 | 68.4 | 21.4 | 69.7 | 52.1 | 48.2 | 48 | 48.6 | 49.7 | 52.4 | 55.1 | 57 | 57.4 | 56.3 | 53.7 | 50.5 | 47.7 | 5.53 | 5.29 | 5 | 4.2 | 3.93 | 3.64 | 2.89 | 2.65 | 2.73 | 3.83 | 4.52 | 5.06 | 5.46 | 515 | 98 | 90 | 78 | 51 | 15 | 1 | 0 | 0 | 1 | 14 | 55 | 112 | 4725 | 521 | 477 | 510 | 460 | 390 | 298 | 249 | 235 | 261 | 351 | 436 | 537 | 1268 | 42 | 33 | 33 | 41 | 90 | 153 | 216 | 231 | 191 | 129 | 69 | 40 | 3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 62 | 0 | 0 | 0 | 3 | 10 | 4 | 3 | 3 | 19 | 19 | 1 | 0 | 13 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 1 | 4 | 5 | 0 | 0 | 6.1 | 6.1 | 6.5 | 6.9 | 6.9 | 6.8 | 6.8 | 5.8 | 5.2 | 4.9 | 5 | 5.5 | 6.4 | 46.4 | 7.9 | 5.7 | 6.5 | 4 | 1.9 | 0.9 | 0.2 | 0.2 | 0.7 | 2.7 | 5.7 | 10.2 | 74.1 | 16.3 | 15.1 | 14.1 | 12.4 | 5.1 | 3.5 | 0.9 | 0.7 | 3.9 | 11.5 | 16 | 24.2 | 21.7 | 1.9 | 0.7 | 2.1 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 1.1 | 11.9 | 4.2 | 3.3 | 3.5 | 2.5 | 1.5 | 0.9 | 0.2 | 0.2 | 0.9 | 2.5 | 3.3 | 5.6 | 66.1 | 66.4 | 65.6 | 69.7 | 72.8 | 70.4 | 70.2 | 71.3 | 76.5 | 75.1 | 69 | 65 | 54 | 55.1 | 54.5 | 56.4 | 60.3 | 60.2 | 60.7 | 61.2 | 61.8 | 58 | 56.8 | 54.1 | 61.6 | 61.7 | 61.1 | 62.2 | 63.8 | 64.9 | 66.1 | 67.8 | 69.5 | 68.4 | 63.6 | 61.4 | 53.6 | 53.3 | 53.4 | 55.3 | 58.4 | 57.9 | 59.9 | 61 | 60.4 | 57.7 | 56.2 | 54.1 | 58.8 | 58.5 | 58.2 | 58.6 | 60.8 | 62.9 | 63.9 | 65.5 | 66.3 | 64.4 | 61 | 58.8 | 53.2 | 52.9 | 52.9 | 53.4 | 55.9 | 57.4 | 58.8 | 60 | 59.4 | 56.8 | 55.1 | 53.6 | 56.6 | 55.9 | 56 | 56.5 | 58.7 | 61 | 62.4 | 63.3 | 63.9 | 61.8 | 58.5 | 56.6 | 52.4 | 51.4 | 51.6 | 52.2 | 54.5 | 56.3 | 58.1 | 59 | 58.4 | 56.2 | 54.4 | 52.6 | 58.4 | 58.6 | 57.8 | 59.1 | 63.8 | 61.5 | 62.8 | 63.8 | 64.1 | 62.5 | 60.4 | 58.5 | 60.8 | 62.8 | 61.1 | 64.7 | 67.6 | 67.5 | 66.4 | 67.6 | 71.2 | 67.9 | 63.9 | 60.9 | 56.3 | 56.1 | 55.3 | 56.1 | 58.9 | 59.5 | 60.9 | 62 | 62 | 60.3 | 58.5 | 56.8 | 59.1 | 59.3 | 58.9 | 60.4 | 63.3 | 63.4 | 64.8 | 66.1 | 67.4 | 64.9 | 61.4 | 59.2 | 54.6 | 54 | 53.7 | 54.4 | 56.7 | 58.2 | 59.5 | 60.5 | 60.4 | 58.7 | 56.8 | 54.9 | 57.4 | 56.9 | 56.7 | 57.5 | 60.1 | 61.7 | 63 | 64.2 | 64.9 | 62.9 | 59.5 | 57.5 | 53.1 | 52.1 | 52.3 | 53 | 55 | 57 | 58.4 | 59.3 | 59.1 | 57 | 55 | 53.3 | 55.7 | 55 | 55.2 | 55.8 | 58 | 60.2 | 61.7 | 62.7 | 63 | 60.8 | 57.6 | 55.8 | 14.3 | 14.2 | 13.9 | 13.4 | 12.2 | 12.5 | 10.5 | 11.4 | 14.6 | 16.3 | 14.6 | 14.4 | 16.9 | 17.6 | 16.8 | 16.7 | 16.3 | 15.9 | 13.4 | 16 | 19.6 | 21.2 | 16.5 | 16.4 | 10.7 | 10.9 | 11 | 10.9 | 10.5 | 10 | 8.1 | 9.7 | 11.3 | 12.2 | 10.3 | 10.9 | 13 | 14.2 | 14.4 | 14.7 | 14.4 | 13.8 | 12.3 | 13.9 | 16.9 | 17.8 | 13.3 | 11.8 | 9.4 | 9.8 | 10.4 | 10.2 | 9.8 | 9.1 | 7.7 | 8.8 | 10.4 | 11.4 | 9.3 | 9.3 | 0.323 | 0.328 | 0.333 | 0.355 | 0.361 | 0.352 | 0.364 | 0.353 | 0.342 | 0.336 | 0.317 | 0.325 | 2.544 | 2.535 | 2.544 | 2.442 | 2.467 | 2.502 | 2.473 | 2.51 | 2.514 | 2.562 | 2.59 | 2.536 | 266 | 282 | 292 | 291 | 290 | 292 | 287 | 288 | 285 | 275 | 266 | 254 | 23 | 27 | 29 | 35 | 35 | 34 | 34 | 32 | 30 | 26 | 22 | 22 | 591 | 852 | 1234 | 1693 | 2079 | 2318 | 2290 | 1978 | 1624 | 1104 | 676 | 489 | 93 | 122 | 128 | 155 | 133 | 135 | 111 | 102 | 86 | 96 | 75 | 91 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.95 | N/A | N/A | N/A | N/A | 202 | 25 | 15
4 | USA | CA | CRESCENT CITY DEL NORTE | 725946 | 24286 | 41.78 | -124.237 | 57 | 14.67 | -8 | NAP | 94-19 | 4C | 12 | 35 | 36.7 | 23.8 | 18 | 43.4 | 27.9 | 21.9 | 43.6 | 34.3 | 52.5 | 31.3 | 52.7 | 4.6 | 90 | 0.596 | 8 | 9.4 | 67.7 | 59.2 | 65.5 | 58.8 | 63.7 | 57.8 | 61.4 | 65.3 | 60.1 | 63.8 | 59.1 | 62.6 | 8.5 | 190 | 59.4 | 75.9 | 62.5 | 58.3 | 72.8 | 61.4 | 57.2 | 70 | 60.4 | 27.2 | 65.3 | 26.4 | 63.9 | 25.7 | 62.6 | 68.5 | 27.6 | 24.5 | 20.8 | 31.4 | 77.6 | 2.2 | 4.1 | 29.8 | 80.6 | 28.5 | 83 | 27.3 | 85.3 | 25.7 | 88.3 | 29.2 | 63.8 | 2.4 | 2 | 27.5 | 65.3 | 26.1 | 66.4 | 24.7 | 67.6 | 22.9 | 69 | 52.2 | 48.5 | 48.3 | 48.7 | 49.9 | 52.5 | 54.7 | 56.7 | 57.6 | 56.5 | 53.9 | 50.9 | 48 | 4.98 | 4.43 | 4.34 | 3.61 | 3.29 | 3 | 2.58 | 2.41 | 2.63 | 3.24 | 3.96 | 4.09 | 4.54 | 413 | 80 | 77 | 68 | 40 | 8 | 1 | 0 | 0 | 0 | 8 | 37 | 94 | 4674 | 510 | 469 | 505 | 454 | 387 | 310 | 256 | 230 | 257 | 345 | 423 | 528 | 1213 | 35 | 28 | 27 | 35 | 86 | 140 | 209 | 235 | 194 | 129 | 64 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 1 | 1 | 2 | 0 | 0 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4 | 9.1 | 9.5 | 9.8 | 9.3 | 8.6 | 8.6 | 6.9 | 6.4 | 6.9 | 7.5 | 8.3 | 9.5 | 75 | 11.8 | 9.4 | 9.3 | 6.9 | 3.8 | 1.7 | 0.4 | 0.6 | 1.1 | 4.7 | 10.3 | 15 | 115.6 | 23.5 | 21.4 | 19.1 | 15.9 | 8.4 | 5.7 | 1.7 | 2.1 | 5.4 | 9.8 | 25.2 | 35 | 45.2 | 3.7 | 2.7 | 3.8 | 1.7 | 0 | 0.1 | 0 | 0 | 0 | 0.4 | 3.1 | 4.5 | 18 | 5.7 | 5 | 4.3 | 3.8 | 2.2 | 1.5 | 0.4 | 0.6 | 1.3 | 2.8 | 5.2 | 7.5 | 63.5 | 63.8 | 62.5 | 66 | 68.1 | 65.8 | 67.1 | 68.6 | 70.4 | 73 | 64.6 | 62.1 | 51.3 | 52.3 | 52.3 | 55.2 | 57.9 | 59.7 | 60.4 | 61.5 | 60.4 | 57.2 | 55.1 | 52.5 | 59 | 59 | 58.2 | 59 | 61.5 | 62.9 | 64.4 | 66.2 | 66.2 | 65.7 | 61.1 | 58.7 | 51.4 | 52.1 | 52.2 | 53.1 | 56.1 | 57.3 | 59 | 60.5 | 59.8 | 56.1 | 54.1 | 53 | 56.7 | 56.5 | 56.2 | 56.8 | 59.2 | 61.2 | 63.1 | 64.3 | 64.1 | 62.6 | 58.9 | 56.7 | 51.5 | 51.4 | 51.5 | 51.9 | 54.9 | 56.4 | 58.2 | 59.3 | 58.5 | 55.8 | 53.8 | 52.4 | 55 | 54.6 | 54.6 | 55.2 | 57.3 | 59.7 | 61.5 | 62.9 | 62.7 | 60.5 | 57.1 | 54.9 | 51.2 | 50.6 | 50.7 | 51.1 | 53.4 | 55.4 | 57.2 | 58.4 | 57.6 | 55.5 | 53.1 | 51.4 | 55.9 | 56.1 | 55.4 | 57 | 59.8 | 60.5 | 62.2 | 62.6 | 62.6 | 60.6 | 58.6 | 57.3 | 58.6 | 59.9 | 58.7 | 63.4 | 65 | 64.4 | 65.4 | 66.3 | 66.8 | 65.3 | 61.1 | 58.5 | 54.2 | 54.1 | 53.8 | 54.3 | 57.1 | 58.4 | 60.1 | 61.3 | 60.8 | 59 | 56.8 | 55.4 | 56.2 | 56.9 | 55.9 | 57.1 | 60.9 | 61.4 | 63.4 | 65 | 64.6 | 62.8 | 59 | 57.3 | 53.2 | 52.7 | 52.7 | 53.1 | 55.4 | 57.2 | 58.9 | 60 | 59.5 | 57.6 | 55.3 | 53.8 | 55.2 | 55.3 | 54.9 | 55.5 | 58.8 | 60.2 | 62.2 | 63.7 | 63 | 61.1 | 57.4 | 55.3 | 51.9 | 51.3 | 51.4 | 51.9 | 54.2 | 56.1 | 57.8 | 58.8 | 58.4 | 56.2 | 54.1 | 52.3 | 54.5 | 53.6 | 54 | 54.5 | 56.8 | 59.1 | 61 | 62.3 | 61.7 | 59.5 | 56.2 | 54.2 | 11.1 | 10.9 | 10.8 | 10.4 | 9.8 | 10.1 | 8.9 | 9.4 | 11.2 | 12 | 11.3 | 11 | 13.2 | 13.3 | 12.2 | 12.2 | 11.9 | 11.5 | 10.8 | 12 | 14.1 | 16 | 13.4 | 12.1 | 8.6 | 8.5 | 8.7 | 8.4 | 8 | 7.7 | 6.9 | 7.6 | 8.8 | 9.7 | 8.9 | 7.9 | 9.5 | 10.3 | 10 | 10.5 | 10.6 | 10.5 | 10 | 11.5 | 12.8 | 13.3 | 10 | 8.1 | 7.2 | 7.2 | 7.6 | 7.8 | 7.5 | 7.3 | 6.5 | 7.4 | 8.4 | 8.9 | 7.7 | 6.6 | 0.321 | 0.321 | 0.327 | 0.352 | 0.357 | 0.348 | 0.353 | 0.349 | 0.341 | 0.33 | 0.315 | 0.319 | 2.56 | 2.571 | 2.576 | 2.462 | 2.491 | 2.524 | 2.516 | 2.54 | 2.534 | 2.589 | 2.604 | 2.569 | 265 | 284 | 294 | 292 | 291 | 293 | 290 | 289 | 285 | 276 | 266 | 255 | 22 | 25 | 28 | 34 | 34 | 33 | 33 | 31 | 29 | 24 | 21 | 21 | 554 | 812 | 1186 | 1645 | 2049 | 2269 | 2276 | 1937 | 1571 | 1041 | 627 | 456 | 85 | 115 | 124 | 148 | 123 | 136 | 111 | 114 | 91 | 95 | 73 | 83 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 4 | 16
4 | USA | CA | SISKIYOU COUNTY AP | 725955 | 24259 | 41.781 | -122.468 | 2651 | 13.34 | -8 | NAP | 94-19 | 4A | 12 | 16.5 | 19.5 | 8.1 | 9.2 | 25.1 | 12.3 | 11.3 | 28 | 34.6 | 45.8 | 31.5 | 45.6 | 1.9 | 30 | 0.561 | 7 | 35.3 | 97.2 | 63.7 | 93.9 | 62.5 | 90.9 | 61.5 | 66 | 91.2 | 64.4 | 89.3 | 63 | 87.5 | 7.5 | 0 | 56.6 | 75.3 | 72.1 | 54.4 | 69.4 | 72.2 | 52.5 | 64.6 | 71.4 | 32 | 91.6 | 30.7 | 89.4 | 29.6 | 87.6 | 74.5 | 26.6 | 21.7 | 18.3 | 8.7 | 103.4 | 7.6 | 3 | 3.3 | 105.5 | -1.2 | 107.3 | -5.4 | 109 | -10.9 | 111.1 | 7.9 | 68.9 | 7.3 | 2 | 2.6 | 70.4 | -1.7 | 71.5 | -5.8 | 72.6 | -11.1 | 74.1 | 52.4 | 36.4 | 39.5 | 43.8 | 48.6 | 56.4 | 64.3 | 73.6 | 71.7 | 64.2 | 52.2 | 41.7 | 35.3 | 14.52 | 6.07 | 5.71 | 5.76 | 6.68 | 7.11 | 7.3 | 5.39 | 4.81 | 6.47 | 6.46 | 6.63 | 7.09 | 1817 | 421 | 294 | 204 | 106 | 21 | 2 | 0 | 0 | 2 | 49 | 262 | 456 | 5245 | 885 | 713 | 658 | 491 | 279 | 99 | 6 | 6 | 91 | 397 | 700 | 920 | 2693 | 1 | 1 | 12 | 65 | 219 | 430 | 733 | 674 | 428 | 118 | 11 | 1 | 647 | 0 | 0 | 0 | 0 | 12 | 77 | 274 | 216 | 67 | 1 | 0 | 0 | 11191 | 0 | 0 | 1 | 67 | 456 | 1541 | 4062 | 3379 | 1552 | 133 | 0 | 0 | 5482 | 0 | 0 | 0 | 8 | 140 | 668 | 2216 | 1744 | 679 | 27 | 0 | 0 | 6.1 | 5 | 6.2 | 6.9 | 6.8 | 6.8 | 7.5 | 6.6 | 6.1 | 5.4 | 5.1 | 4.8 | 5.3 | 19.1 | 3.1 | 2 | 2 | 1.5 | 1.4 | 0.8 | 0.4 | 0.3 | 0.4 | 1.3 | 2.4 | 3.3 | 30.8 | 6.2 | 5 | 8.1 | 3.5 | 3.7 | 2.4 | 1.7 | 1.4 | 1.1 | 4.8 | 7.8 | 8.9 | 10.9 | 0.7 | 0.9 | 0.5 | 0.6 | 0.4 | 0 | 0 | 0 | 0 | 0.2 | 0.4 | 0.6 | 5.2 | 1.8 | 1.1 | 1.6 | 0.7 | 0.9 | 0.7 | 0.4 | 0.3 | 0.3 | 1.1 | 1.6 | 2.4 | 56.9 | 63.5 | 71.6 | 80.8 | 89.7 | 97 | 102.1 | 100.2 | 94.5 | 83.7 | 67.9 | 55.8 | 46.6 | 49.6 | 51.9 | 56.8 | 60.5 | 63.6 | 66 | 64.2 | 60.7 | 57.8 | 52.1 | 48.1 | 53 | 58.4 | 66.3 | 75 | 83.8 | 91.5 | 98.4 | 96.3 | 90.9 | 77.8 | 62.1 | 52.2 | 45.2 | 46.4 | 50 | 54.9 | 59 | 61.7 | 64.5 | 63 | 59.8 | 55.1 | 49.9 | 45.7 | 49.7 | 54.3 | 62 | 70 | 79.2 | 87.8 | 95.1 | 92.9 | 88 | 72.8 | 57.4 | 49.4 | 43.3 | 44.8 | 48.2 | 52.4 | 57.1 | 60.2 | 63.5 | 61.8 | 59.1 | 53.2 | 47.6 | 43.7 | 46.5 | 50.8 | 57.1 | 64.3 | 74.2 | 83.4 | 91.4 | 90 | 83.8 | 68.3 | 53.9 | 46.5 | 41.5 | 42.8 | 45.8 | 49.9 | 55.2 | 58.9 | 62.7 | 61 | 58 | 51.3 | 45.8 | 41.7 | 48.9 | 51 | 54.3 | 58.8 | 63.1 | 66.2 | 68.8 | 66.9 | 64 | 59.2 | 54.4 | 49.5 | 53.8 | 60.5 | 67.5 | 76.6 | 84.6 | 91.1 | 95.1 | 93.6 | 89.9 | 78.2 | 64.6 | 54.3 | 46.1 | 48.1 | 51.4 | 55.6 | 60.3 | 63.5 | 66.9 | 64.9 | 61.6 | 57.2 | 51.3 | 46.4 | 51.1 | 56.6 | 63.5 | 72.6 | 80.2 | 87.6 | 92 | 90.8 | 86 | 75.3 | 59.8 | 50.8 | 44 | 45.7 | 49.2 | 53.1 | 58.4 | 61.3 | 65.2 | 63.5 | 59.9 | 54.6 | 48.9 | 44.4 | 48.7 | 52.9 | 59.5 | 68.1 | 76.4 | 84.2 | 90.1 | 89.2 | 84.4 | 70 | 56.1 | 48.5 | 42 | 43.6 | 46.9 | 50.5 | 56.2 | 59.6 | 63.8 | 62 | 58.5 | 52.3 | 46.4 | 42.2 | 46.4 | 50.2 | 56.2 | 62.9 | 72.2 | 80.8 | 88.4 | 86.8 | 81.8 | 65.6 | 52.9 | 46.1 | 17.5 | 21.5 | 24.2 | 26.5 | 28.8 | 32.3 | 35.3 | 35.9 | 35.6 | 30.1 | 21.3 | 16.9 | 22.1 | 27.9 | 34.2 | 37.6 | 38.3 | 39 | 39 | 39.9 | 42.1 | 38.5 | 27.8 | 18 | 15.2 | 17.5 | 19.7 | 19.8 | 17.4 | 15.2 | 14.4 | 15.5 | 18.8 | 20.3 | 17.6 | 12.4 | 18.9 | 25.3 | 30.1 | 35.3 | 35.4 | 36.7 | 36.4 | 37.1 | 39.5 | 34.3 | 24.5 | 15.7 | 13.4 | 16.4 | 17.7 | 19.3 | 16.4 | 14.8 | 13.7 | 14.7 | 18.3 | 18.6 | 15.8 | 11.2 | 0.291 | 0.295 | 0.301 | 0.319 | 0.326 | 0.319 | 0.324 | 0.32 | 0.302 | 0.301 | 0.286 | 0.295 | 2.531 | 2.545 | 2.554 | 2.494 | 2.513 | 2.566 | 2.563 | 2.555 | 2.592 | 2.592 | 2.598 | 2.516 | 276 | 293 | 303 | 302 | 301 | 302 | 299 | 298 | 298 | 287 | 277 | 264 | 23 | 26 | 29 | 33 | 33 | 31 | 31 | 30 | 27 | 24 | 21 | 21 | 594 | 879 | 1245 | 1706 | 2139 | 2485 | 2552 | 2254 | 1777 | 1167 | 678 | 486 | 93 | 111 | 131 | 167 | 169 | 141 | 93 | 95 | 85 | 111 | 80 | 95 | 0.86 | N/A | N/A | 1.13 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.94 | N/A | N/A | N/A | N/A | 176 | 32 | 16
4 | USA | CA | MOUNT SHASTA | 725957 | 24215 | 41.333 | -122.333 | 3535 | 12.91 | -8 | NAP | 94-19 | 5C | 12 | 18.2 | 21.7 | 6.7 | 8.9 | 29.1 | 11.5 | 11.3 | 30.3 | 13.4 | 38.6 | 12.2 | 38 | 1.7 | 50 | 0.493 | 7 | 33 | 91.9 | 64.2 | 89.4 | 63.1 | 86.4 | 61.7 | 67.7 | 86.1 | 65.6 | 84.8 | 63.8 | 82.9 | 2.1 | 290 | 61 | 91.5 | 78.2 | 57.3 | 79.9 | 76 | 55.1 | 73.7 | 74 | 33.9 | 86 | 32.1 | 84.7 | 30.7 | 82.8 | 77.7 | 11.9 | 10.5 | 9.1 | 10.7 | 97.2 | 5.1 | 2.7 | 7.1 | 99.1 | 4.1 | 100.7 | 1.2 | 102.2 | -2.5 | 104.2 | 9.5 | 70.7 | 4.9 | 3 | 6 | 72.9 | 3.1 | 74.7 | 0.3 | 76.4 | -3.3 | 78.6 | 50.8 | 36.7 | 38.4 | 42.4 | 46.9 | 55.1 | 62.4 | 69.4 | 67.6 | 61.7 | 51.2 | 41.5 | 35.6 | 13.34 | 5.83 | 5.89 | 6.54 | 7.27 | 7.43 | 7.02 | 5.05 | 4.74 | 6.34 | 6.47 | 6.41 | 5.91 | 1948 | 414 | 326 | 249 | 144 | 36 | 5 | 0 | 0 | 3 | 63 | 262 | 446 | 5529 | 879 | 745 | 702 | 542 | 316 | 128 | 17 | 26 | 131 | 428 | 704 | 911 | 2246 | 0 | 1 | 13 | 52 | 193 | 375 | 602 | 547 | 354 | 101 | 8 | 0 | 350 | 0 | 0 | 0 | 0 | 7 | 48 | 154 | 108 | 32 | 1 | 0 | 0 | 7196 | 0 | 0 | 1 | 43 | 314 | 964 | 2641 | 2165 | 987 | 81 | 0 | 0 | 2761 | 0 | 0 | 0 | 3 | 76 | 311 | 1156 | 879 | 323 | 13 | 0 | 0 | 3.1 | 3.2 | 3.3 | 3.6 | 3.9 | 3.6 | 3.6 | 2.4 | 2.2 | 2.6 | 2.9 | 2.9 | 3.3 | 40.6 | 7 | 6 | 5.3 | 2.9 | 1.9 | 1 | 0.3 | 0.4 | 0.7 | 2.2 | 5.6 | 7 | 75.2 | 27.5 | 21.8 | 18.9 | 9.1 | 9.3 | 3.8 | 1.7 | 2.6 | 3.9 | 9.7 | 17.2 | 25.9 | 14.2 | 0.2 | 0.2 | 0.4 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 13 | 5.3 | 4.9 | 4.3 | 2.2 | 2 | 1 | 0.4 | 0.6 | 0.9 | 2.2 | 4.2 | 5.8 | 58.9 | 64.3 | 71 | 79.2 | 87 | 92 | 96.8 | 95.2 | 91.1 | 81.4 | 67.6 | 54.9 | 44.6 | 48.2 | 51.6 | 55.4 | 60.2 | 64.6 | 66.4 | 64.3 | 61.7 | 58.7 | 51.9 | 44.5 | 54 | 58.7 | 65.8 | 73.5 | 81.7 | 87.3 | 92.8 | 90.9 | 87.3 | 75.3 | 62.7 | 50.6 | 42.7 | 45.9 | 49.1 | 53.6 | 59.6 | 62.9 | 65.1 | 63.6 | 59.8 | 55.4 | 49.7 | 42.9 | 49.6 | 53.6 | 61.4 | 68.8 | 77.3 | 83.5 | 90 | 88.2 | 83.8 | 71.8 | 57.2 | 47.8 | 41.8 | 43.1 | 46.8 | 51.3 | 56.6 | 61.3 | 63.8 | 62.3 | 59 | 53.5 | 46.6 | 42.3 | 46 | 49 | 56 | 63.3 | 72.7 | 80 | 86.8 | 85.2 | 80.5 | 66.6 | 53.1 | 45.2 | 40.7 | 41.6 | 44.8 | 49.3 | 54.9 | 59.9 | 63 | 60.9 | 58.4 | 51.4 | 44.6 | 41 | 48.3 | 50.1 | 53.8 | 57.7 | 64.1 | 68.8 | 71.1 | 69.5 | 66 | 59.8 | 54.2 | 48 | 53 | 61 | 67.8 | 74.5 | 81.4 | 85.7 | 89.2 | 86.4 | 85.1 | 76.2 | 64 | 51 | 45.3 | 47.4 | 50.5 | 54.7 | 60.6 | 65.5 | 68.3 | 66.3 | 62.6 | 57.2 | 51 | 45.5 | 50.3 | 55.5 | 62.5 | 70.9 | 78.5 | 83.7 | 86.6 | 85.6 | 81.5 | 73 | 59.6 | 48.3 | 43.3 | 44.8 | 48.2 | 52.2 | 58.3 | 62.9 | 66.2 | 64.2 | 60.4 | 54.7 | 48.3 | 43.7 | 48.2 | 51.5 | 58.9 | 66.5 | 75 | 80.6 | 85.5 | 83.8 | 79.8 | 68.9 | 55.3 | 46.8 | 41.2 | 42.4 | 45.8 | 49.7 | 55.7 | 60.7 | 64.3 | 62.4 | 58.7 | 52.3 | 46 | 41.2 | 45.6 | 48.3 | 54.6 | 61.5 | 70.7 | 77.9 | 83.7 | 82.3 | 78.3 | 64.7 | 51.2 | 44.6 | 15.3 | 17.1 | 19.9 | 22.8 | 25.9 | 28.3 | 33 | 34 | 32.1 | 26 | 18.5 | 14.5 | 23.1 | 27 | 31 | 34.7 | 35 | 34.5 | 37 | 37.5 | 38.7 | 35.1 | 27.2 | 20.2 | 14.5 | 16.2 | 17.2 | 18 | 16.5 | 15.9 | 15.9 | 16.2 | 17.5 | 18.2 | 16.8 | 13.5 | 17.7 | 22.5 | 27.4 | 31.6 | 32.2 | 32.3 | 33.8 | 34.6 | 35.1 | 31.1 | 23.9 | 15.2 | 12 | 14.4 | 16 | 17.2 | 16 | 16.8 | 16.3 | 16.6 | 17.1 | 16.9 | 15.4 | 11.3 | 0.279 | 0.284 | 0.289 | 0.305 | 0.315 | 0.308 | 0.31 | 0.306 | 0.293 | 0.291 | 0.276 | 0.281 | 2.553 | 2.563 | 2.579 | 2.529 | 2.536 | 2.59 | 2.596 | 2.59 | 2.611 | 2.618 | 2.623 | 2.55 | 283 | 298 | 308 | 307 | 304 | 305 | 304 | 303 | 302 | 292 | 284 | 272 | 22 | 25 | 28 | 32 | 32 | 31 | 30 | 30 | 27 | 24 | 20 | 21 | 620 | 909 | 1281 | 1753 | 2179 | 2521 | 2569 | 2279 | 1808 | 1204 | 712 | 513 | 101 | 114 | 142 | 174 | 167 | 140 | 92 | 91 | 81 | 112 | 82 | 101 | 0.74 | N/A | N/A | 2.18 | N/A | N/A | N/A | N/A | 230 | 86 | N/A | N/A | N/A | 0.94 | N/A | N/A | N/A | N/A | 169 | 27 | 15
4 | USA | CA | ALTURAS | 725958 | 94299 | 41.483 | -120.567 | 4375 | 12.52 | -8 | NAP | 98-19 | 5C | 12 | 3.5 | 10.1 | -1.1 | 6.1 | 11.4 | 4.6 | 8.2 | 19.1 | 25.8 | 41.6 | 22 | 39.3 | 0.9 | 20 | 0.601 | 7 | 41 | 94.4 | 60 | 91.4 | 59.1 | 88.9 | 58.1 | 62.5 | 87.5 | 60.8 | 85.7 | 59.5 | 84.4 | 9.3 | 270 | 54.1 | 73.2 | 66.7 | 51.4 | 66.1 | 66.4 | 48.4 | 59.2 | 64.6 | 30.1 | 87.4 | 28.8 | 85.7 | 27.8 | 84.3 | 69.4 | 22.1 | 19 | 16.9 | -5.6 | 99.5 | 8.2 | 2.6 | -11.5 | 101.4 | -16.3 | 102.9 | -20.8 | 104.3 | -26.8 | 106.2 | -5.9 | 65.4 | 8 | 2.2 | -11.7 | 67 | -16.4 | 68.2 | -20.9 | 69.4 | -26.7 | 71 | 47.7 | 31.8 | 34.2 | 39.2 | 44 | 52.3 | 60.6 | 68.4 | 66 | 58.4 | 47.4 | 37.8 | 30.8 | 14.56 | 8.49 | 7.01 | 6.45 | 6.8 | 6.97 | 6.73 | 5.05 | 4.74 | 6.6 | 6.59 | 7.87 | 8.19 | 2709 | 565 | 442 | 336 | 201 | 57 | 7 | 0 | 0 | 12 | 126 | 368 | 595 | 6575 | 1030 | 862 | 799 | 631 | 396 | 158 | 23 | 43 | 211 | 547 | 815 | 1060 | 1854 | 0 | 0 | 2 | 20 | 127 | 326 | 571 | 497 | 263 | 45 | 3 | 0 | 245 | 0 | 0 | 0 | 0 | 1 | 28 | 129 | 75 | 12 | 0 | 0 | 0 | 9060 | 0 | 0 | 1 | 24 | 288 | 1288 | 3494 | 2689 | 1179 | 97 | 0 | 0 | 4060 | 0 | 0 | 0 | 1 | 66 | 484 | 1797 | 1254 | 438 | 20 | 0 | 0 | 5.3 | 4.3 | 5.3 | 6.4 | 6.7 | 6.5 | 6.3 | 5.7 | 5.1 | 4.5 | 4.4 | 4.4 | 4.6 | 14.1 | 1.6 | 1.3 | 1.6 | 1.6 | 1.7 | 0.9 | 0.2 | 0.3 | 0.4 | 1 | 1.6 | 1.9 | 23.5 | 3.9 | 3.1 | 4.2 | 3.9 | 5.6 | 2.4 | 0.8 | 1.2 | 1.4 | 3.1 | 4.2 | 5.3 | 8.3 | 0.1 | 0.4 | 0.6 | 0.4 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0.2 | 0.5 | 4.4 | 1.1 | 0.7 | 0.9 | 0.8 | 1.4 | 0.7 | 0.2 | 0.4 | 0.4 | 0.8 | 0.9 | 1.5 | 57.7 | 61.3 | 70.4 | 77.3 | 86.9 | 94.5 | 99.3 | 96.7 | 92.5 | 83.3 | 69.5 | 54 | 43.1 | 45.5 | 48.7 | 52.3 | 57.9 | 60.6 | 63 | 61 | 58.8 | 54.5 | 49.6 | 42.8 | 53.1 | 55.4 | 64.2 | 72.3 | 81.4 | 89.6 | 95.4 | 93 | 88.3 | 75.5 | 63.7 | 49.9 | 41.9 | 42.1 | 46.3 | 50.3 | 55.9 | 59 | 60.3 | 59.6 | 56.4 | 51.6 | 47.5 | 41 | 48.4 | 51.1 | 59.9 | 67.3 | 77 | 85.6 | 92.7 | 90.3 | 85.2 | 72.4 | 57.4 | 46.5 | 40.2 | 41.3 | 44.3 | 48.1 | 53.5 | 56.8 | 59.5 | 58.5 | 55.5 | 50 | 44.4 | 40.2 | 44.8 | 46.7 | 54.4 | 62.3 | 72.3 | 81.8 | 90.1 | 87.6 | 81.7 | 67.2 | 52.4 | 43.5 | 38.7 | 39 | 42.4 | 45.9 | 51.7 | 55.9 | 58.9 | 57.4 | 54.8 | 48.2 | 42.6 | 38.5 | 47.1 | 47.4 | 50.2 | 54.3 | 59.9 | 62.9 | 65.4 | 64.9 | 62 | 55.6 | 51.3 | 45.6 | 54.6 | 57.9 | 66.3 | 72.6 | 81.8 | 88.4 | 92.5 | 91.4 | 81.7 | 75.4 | 65.6 | 49.9 | 43.5 | 44.3 | 47.6 | 51.4 | 57 | 60.1 | 63.2 | 61.6 | 59.2 | 53.1 | 48.4 | 43.2 | 50 | 52.9 | 61.1 | 69.5 | 77.9 | 85 | 89.1 | 86.2 | 81.6 | 72 | 60.7 | 47.7 | 41 | 41.8 | 45.5 | 49.1 | 54.9 | 58.4 | 61.4 | 59.9 | 57 | 51.2 | 46 | 41.2 | 47.1 | 49.1 | 57.7 | 64.9 | 73.4 | 82 | 86.9 | 84.7 | 81 | 69.3 | 56.2 | 45.3 | 38.9 | 39.6 | 43.3 | 46.8 | 52.7 | 56.7 | 59.9 | 58.5 | 55.2 | 49.2 | 43.6 | 38.8 | 44.2 | 46.5 | 53.4 | 60.2 | 69.3 | 78.8 | 85.7 | 83.4 | 79.7 | 64.9 | 51.3 | 43.1 | 22.3 | 22.2 | 25.1 | 27.1 | 30.1 | 35.5 | 41 | 41.3 | 40.3 | 34.6 | 25.8 | 20.7 | 29.6 | 30.1 | 37.8 | 40.8 | 41 | 43.4 | 44.5 | 45.7 | 47.6 | 45.6 | 36.8 | 25.9 | 19.4 | 18.6 | 21 | 20.7 | 18.2 | 16.8 | 16.5 | 18.7 | 21.6 | 23.9 | 22.1 | 17.9 | 24.2 | 25.5 | 33.1 | 37.1 | 36.9 | 40.4 | 41 | 41.3 | 43.6 | 40.2 | 32.4 | 19.3 | 16.4 | 16.3 | 19 | 19.2 | 16.7 | 16.3 | 15.8 | 17.7 | 20.4 | 21.8 | 19.7 | 13.8 | 0.279 | 0.289 | 0.3 | 0.307 | 0.314 | 0.308 | 0.312 | 0.31 | 0.298 | 0.297 | 0.28 | 0.275 | 2.507 | 2.51 | 2.505 | 2.493 | 2.513 | 2.557 | 2.545 | 2.53 | 2.56 | 2.551 | 2.563 | 2.531 | 281 | 295 | 303 | 306 | 305 | 305 | 303 | 301 | 300 | 288 | 280 | 274 | 23 | 27 | 30 | 33 | 33 | 32 | 32 | 31 | 28 | 25 | 22 | 21 | 627 | 912 | 1288 | 1723 | 2133 | 2501 | 2536 | 2243 | 1784 | 1194 | 709 | 502 | 83 | 113 | 123 | 167 | 190 | 131 | 108 | 106 | 89 | 100 | 75 | 98 | N/A | N/A | N/A | 1.06 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.08 | N/A | N/A | N/A | N/A | 164 | 76 | 7
4 | USA | CA | MADERA | 745046 | 93242 | 36.988 | -120.111 | 253 | 14.56 | -8 | NAP | 99-19 | 3B | 12 | 30 | 32.5 | 22.9 | 17.4 | 49.5 | 26.4 | 20.6 | 46.4 | 21 | 54 | 18.8 | 52.8 | 2.2 | 90 | 0.458 | 7 | 33.5 | 102 | 69.7 | 99.6 | 68.9 | 97.3 | 67.8 | 72.8 | 95.7 | 71.1 | 94.2 | 69.5 | 92.3 | 8.7 | 300 | 64.5 | 91.6 | 82.4 | 63 | 86.9 | 80.9 | 61.1 | 81.2 | 78.7 | 36.5 | 94.8 | 34.9 | 94.1 | 33.6 | 92.4 | 82.2 | 18.5 | 16.2 | 13.5 | 26.5 | 106.7 | 2.6 | 1.9 | 24.6 | 108.1 | 23.1 | 109.2 | 21.6 | 110.3 | 19.7 | 111.7 | 25.1 | 75.3 | 2.5 | 2.2 | 23.3 | 76.9 | 21.8 | 78.2 | 20.3 | 79.4 | 18.5 | 81.1 | 63.1 | 47.5 | 51.1 | 55.9 | 60.3 | 67.9 | 75 | 80 | 78.4 | 74.2 | 64.6 | 54.3 | 47.3 | 12.77 | 5.11 | 4.93 | 5.61 | 6.57 | 6.22 | 6.15 | 4.86 | 4.16 | 5.64 | 5.75 | 5.65 | 5.21 | 309 | 111 | 42 | 12 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 118 | 2383 | 544 | 389 | 284 | 170 | 40 | 4 | 0 | 0 | 4 | 77 | 322 | 549 | 5092 | 32 | 73 | 196 | 313 | 554 | 749 | 930 | 881 | 726 | 452 | 152 | 34 | 1692 | 0 | 0 | 3 | 30 | 129 | 303 | 465 | 416 | 281 | 64 | 1 | 0 | 23759 | 0 | 2 | 126 | 578 | 2057 | 4361 | 6459 | 5524 | 3645 | 957 | 50 | 0 | 13238 | 0 | 0 | 20 | 201 | 938 | 2472 | 3982 | 3304 | 1996 | 320 | 5 | 0 | 6 | 4.6 | 5.4 | 5.8 | 7.1 | 7.9 | 7.9 | 7.2 | 6.7 | 5.7 | 4.8 | 4.1 | 4.7 | 11.2 | 1.8 | 1.8 | 1.9 | 1.2 | 0.2 | 0 | 0 | 0 | 0.2 | 0.6 | 1.7 | 1.5 | 22.1 | 5.7 | 5.3 | 5.1 | 5.5 | 1.8 | 0.4 | 0.1 | 0.3 | 1.6 | 2 | 4.3 | 3.3 | 5.6 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 1.5 | 1.5 | 1.3 | 1.2 | 0.4 | 0.1 | 0 | 0.1 | 0.4 | 0.6 | 1.1 | 0.9 | 67.9 | 73.2 | 82.3 | 91.6 | 99 | 103.9 | 106 | 104.3 | 101.4 | 93.4 | 79.2 | 66.7 | 54 | 58.6 | 61.5 | 63.2 | 67.6 | 71.2 | 72.3 | 69.2 | 67.6 | 65.4 | 60.3 | 54.5 | 63.6 | 68.7 | 77.2 | 85.7 | 93.6 | 100.1 | 102.2 | 100.3 | 98.4 | 87.7 | 74.5 | 63 | 53.1 | 56.8 | 59.7 | 61.8 | 65.6 | 69.3 | 70.3 | 68.6 | 67.1 | 63.4 | 58.5 | 52.8 | 60.4 | 65.2 | 73.3 | 80.9 | 89.8 | 96.8 | 99.7 | 98.3 | 95.2 | 83.1 | 70.6 | 60 | 52.3 | 55 | 58.8 | 60.4 | 63.5 | 67.6 | 69.8 | 68 | 66.1 | 61.3 | 57 | 52.3 | 57.1 | 62.2 | 69.6 | 75.5 | 85.1 | 92.9 | 97 | 95.3 | 91.3 | 79.5 | 66.3 | 57 | 51.1 | 53.7 | 57.3 | 58.4 | 61.9 | 66.1 | 68.5 | 67 | 65.4 | 60.6 | 55.3 | 51.1 | 58.1 | 60.6 | 65.1 | 67.4 | 70.3 | 74.7 | 75.6 | 73.2 | 71.9 | 68 | 62.5 | 58.6 | 63.2 | 68.4 | 76.8 | 83.9 | 93.8 | 98.4 | 100.4 | 95.1 | 93.9 | 84.3 | 74.3 | 63.8 | 55.5 | 58.5 | 62.2 | 64.1 | 67.5 | 71.7 | 73.3 | 71.2 | 69.2 | 65.7 | 60.3 | 55.7 | 60.2 | 66.4 | 73.6 | 81.4 | 89.4 | 95 | 96.1 | 94.8 | 92 | 81.9 | 71.4 | 59.5 | 53.5 | 56.4 | 59.9 | 61.7 | 65.3 | 69.4 | 71.4 | 69.6 | 67.7 | 63.7 | 58.5 | 53.9 | 57.7 | 63.8 | 70.6 | 77.3 | 86.2 | 91.9 | 94.5 | 92.7 | 90.9 | 79.6 | 68 | 57.8 | 51.4 | 54.4 | 57.8 | 59.7 | 63.2 | 67.8 | 69.8 | 68.4 | 66.2 | 61.8 | 56.6 | 51.8 | 56.6 | 60.8 | 67.8 | 73.9 | 82.7 | 89.7 | 92.9 | 91.1 | 88.6 | 76.6 | 64.6 | 55.9 | 17.7 | 20.6 | 23.8 | 26.6 | 30 | 32.9 | 33.5 | 33.9 | 32.7 | 28 | 23.2 | 18.2 | 23.9 | 25.7 | 30.2 | 34.1 | 36.3 | 36 | 34.7 | 36.2 | 36.4 | 33.2 | 29.2 | 22.2 | 15 | 15.1 | 14.9 | 13.6 | 13 | 11.9 | 11.4 | 11.1 | 11.8 | 13.7 | 15.3 | 13.7 | 17.5 | 22.8 | 27.7 | 30.8 | 34.2 | 34.2 | 32.9 | 34.2 | 33.9 | 29 | 25.3 | 15.2 | 11.9 | 14 | 15 | 13.6 | 13 | 11.9 | 11.7 | 11.6 | 11.7 | 12.1 | 13.9 | 10.4 | 0.349 | 0.362 | 0.384 | 0.376 | 0.365 | 0.362 | 0.377 | 0.366 | 0.37 | 0.379 | 0.372 | 0.357 | 2.37 | 2.344 | 2.278 | 2.333 | 2.388 | 2.397 | 2.374 | 2.382 | 2.38 | 2.318 | 2.289 | 2.334 | 263 | 274 | 279 | 287 | 291 | 290 | 285 | 286 | 279 | 264 | 250 | 249 | 29 | 34 | 39 | 39 | 38 | 38 | 38 | 37 | 35 | 34 | 31 | 29 | 775 | 1106 | 1570 | 2001 | 2385 | 2669 | 2583 | 2359 | 1953 | 1419 | 957 | 705 | 111 | 127 | 137 | 156 | 132 | 97 | 92 | 71 | 62 | 82 | 55 | 97 | 1.69 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.9 | N/A | -2.09 | N/A | N/A | N/A | N/A | -245 | 304 | 95 | 27
4 | USA | CA | OROVILLE | 745048 | 93210 | 39.49 | -121.618 | 190 | 14.6 | -8 | NAP | 99-19 | 3A | 12 | 33.1 | 35.6 | 18.1 | 13.8 | 51.6 | 22.1 | 16.7 | 50.1 | 27.7 | 51.5 | 24.9 | 51 | 3 | 320 | 0.44 | 7 | 29.3 | 100.5 | 69.8 | 98.1 | 69.2 | 95.2 | 67.9 | 73.3 | 95 | 71.5 | 93.3 | 70.1 | 91.5 | 6.3 | 180 | 65.5 | 94.9 | 86.2 | 63.2 | 87.3 | 84.5 | 61.3 | 81.4 | 82.2 | 37 | 95.3 | 35.4 | 93.4 | 34 | 91.5 | 88.2 | 20.7 | 18.2 | 16.1 | 28.1 | 106.4 | 2.5 | 2.4 | 26.3 | 108.1 | 24.8 | 109.6 | 23.4 | 110.9 | 21.6 | 112.7 | 26.3 | 77.2 | 2.2 | 4.7 | 24.8 | 80.6 | 23.5 | 83.4 | 22.3 | 86.1 | 20.7 | 89.5 | 63.2 | 47.7 | 51.2 | 55.7 | 60.2 | 68 | 75.7 | 80.5 | 78.3 | 73.7 | 64.6 | 54 | 47.7 | 12.82 | 4.58 | 4.76 | 5.46 | 6.55 | 6.77 | 6.63 | 5.22 | 4.43 | 5.57 | 5.59 | 5.7 | 4.96 | 282 | 97 | 39 | 12 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 104 | 2388 | 535 | 387 | 292 | 174 | 44 | 6 | 0 | 0 | 5 | 75 | 332 | 538 | 5091 | 27 | 72 | 188 | 308 | 558 | 772 | 946 | 878 | 711 | 452 | 147 | 32 | 1720 | 0 | 0 | 3 | 29 | 137 | 328 | 481 | 413 | 266 | 62 | 1 | 0 | 22120 | 1 | 1 | 78 | 459 | 1772 | 4242 | 6453 | 5110 | 3184 | 799 | 19 | 2 | 11361 | 0 | 0 | 7 | 136 | 728 | 2245 | 3744 | 2738 | 1526 | 236 | 1 | 0 | 6.1 | 5.3 | 6.7 | 7.1 | 7.1 | 7.1 | 6.7 | 6 | 5.6 | 5.4 | 5.2 | 5 | 5.8 | 20.9 | 4.3 | 4 | 3 | 1.6 | 1.3 | 0.4 | 0 | 0.1 | 0.1 | 1.1 | 1.9 | 4.5 | 35.5 | 14.1 | 11.5 | 10.4 | 4.9 | 4 | 1.5 | 0.1 | 0.6 | 0.6 | 3.7 | 5 | 11.1 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 5.9 | 3.4 | 2.8 | 3.2 | 1.4 | 1.1 | 0.4 | 0 | 0.2 | 0.2 | 0.9 | 1.4 | 2.7 | 68.1 | 72.1 | 81 | 89.2 | 96.8 | 103.5 | 105.8 | 102.1 | 99.3 | 91.1 | 76.6 | 66.2 | 50.6 | 56.7 | 60.4 | 63.4 | 69.3 | 71.1 | 71.5 | 69.2 | 67.6 | 64.1 | 58.5 | 53.7 | 61.8 | 67.4 | 75.8 | 83.9 | 91.9 | 99.1 | 101.5 | 98.7 | 95.3 | 86 | 72.2 | 61.3 | 50.7 | 55.2 | 58.5 | 61.5 | 66.7 | 69.8 | 70.4 | 68.7 | 66.1 | 61.5 | 57.3 | 53 | 58.5 | 63.6 | 72.2 | 79.8 | 88.2 | 95.3 | 98.8 | 95.5 | 92.5 | 81.9 | 68 | 58.6 | 51.1 | 53.2 | 57.1 | 60.3 | 64.8 | 67.7 | 69.9 | 67.7 | 65.6 | 60.1 | 55.6 | 52.2 | 55.6 | 60.6 | 67.9 | 74.6 | 83.6 | 91.4 | 95.5 | 92.7 | 89.3 | 78.7 | 63.9 | 56.2 | 50.2 | 52.1 | 54.9 | 58.1 | 62.8 | 66.4 | 68.8 | 67.3 | 65 | 58.9 | 54.4 | 50.7 | 56.7 | 59.8 | 62.5 | 66.5 | 75.3 | 75.6 | 76.1 | 74.4 | 72.8 | 67 | 61.8 | 58.9 | 60.7 | 67.9 | 76.2 | 83 | 88.1 | 96.4 | 99.6 | 92.9 | 89.7 | 84.3 | 72.5 | 63.3 | 54.2 | 57.2 | 60.3 | 63.5 | 69.4 | 72.2 | 73.4 | 71.5 | 69.1 | 64.3 | 59.3 | 56.4 | 57.7 | 64.3 | 72.9 | 80.8 | 87.6 | 93.8 | 96.6 | 92.8 | 90.2 | 80.8 | 67.6 | 59.6 | 52.7 | 55.2 | 58.4 | 61.2 | 66.4 | 70.2 | 71.8 | 70 | 67.3 | 62.4 | 57.7 | 54 | 55.9 | 61.1 | 69.1 | 77 | 85 | 91.4 | 94.6 | 91.1 | 88.4 | 77.3 | 64.1 | 56.3 | 51.1 | 53.4 | 56.5 | 59.2 | 64 | 68.2 | 70.4 | 68.5 | 65.7 | 60.5 | 56.1 | 52.1 | 55.1 | 58.6 | 65.7 | 72.7 | 81.4 | 88.8 | 92.6 | 89.5 | 86.9 | 74 | 62.2 | 54.6 | 15 | 17 | 19.6 | 22.4 | 24.9 | 27.3 | 29.3 | 28.8 | 27.6 | 24.4 | 17.9 | 14.7 | 21 | 23.4 | 27.5 | 30.6 | 30.7 | 31.3 | 31.2 | 30.7 | 32 | 30.5 | 24.7 | 18.5 | 12.6 | 13.7 | 14 | 13.3 | 12.4 | 11.3 | 11.4 | 11.3 | 12.4 | 12.8 | 12.6 | 11.1 | 14.1 | 18.6 | 23.5 | 28.4 | 28.7 | 29.7 | 29.7 | 29 | 29.5 | 26.1 | 19 | 11.7 | 9.6 | 11.8 | 12.8 | 12.9 | 13.8 | 11.8 | 12 | 11.9 | 12.4 | 11.7 | 10.5 | 8.2 | 0.328 | 0.329 | 0.351 | 0.36 | 0.36 | 0.356 | 0.353 | 0.34 | 0.343 | 0.339 | 0.323 | 0.327 | 2.485 | 2.494 | 2.426 | 2.397 | 2.435 | 2.448 | 2.439 | 2.47 | 2.473 | 2.486 | 2.517 | 2.489 | 267 | 284 | 287 | 290 | 291 | 291 | 291 | 293 | 286 | 276 | 266 | 258 | 25 | 28 | 33 | 36 | 36 | 36 | 36 | 34 | 31 | 28 | 24 | 23 | 671 | 968 | 1380 | 1863 | 2301 | 2605 | 2623 | 2335 | 1872 | 1288 | 800 | 581 | 121 | 137 | 170 | 185 | 157 | 119 | 82 | 79 | 72 | 101 | 72 | 104 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.74 | N/A | -2 | N/A | N/A | N/A | -58 | -180 | 241 | 90 | 32
4 | USA | CA | RAMONA | 745056 | 53120 | 33.038 | -116.916 | 1393 | 13.97 | -8 | NAP | 99-19 | 3A | 12 | 28.6 | 31.3 | 2.5 | 6.6 | 62.4 | 7.7 | 8.6 | 61.4 | 23.8 | 60.5 | 20.3 | 60.9 | 1.2 | 110 | 0.46 | 8 | 30.8 | 97.3 | 67.6 | 94.2 | 67.3 | 91.3 | 66.6 | 72.3 | 90.9 | 70.8 | 88.8 | 69.4 | 86.7 | 10.8 | 280 | 66.2 | 101.6 | 79 | 64.3 | 95 | 78.6 | 63.1 | 91.1 | 77.4 | 36.7 | 91 | 35.4 | 88.9 | 34.3 | 86.7 | 88.2 | 18.1 | 15.7 | 13 | 24.4 | 104.1 | 2.6 | 3.9 | 22.6 | 106.9 | 21.1 | 109.1 | 19.7 | 111.3 | 17.8 | 114.1 | 22.6 | 75.5 | 2.3 | 4.3 | 21 | 78.6 | 19.6 | 81.1 | 18.3 | 83.5 | 16.6 | 86.6 | 61.1 | 51.5 | 51.5 | 54.2 | 56.8 | 61.8 | 67.4 | 73.3 | 74 | 71.1 | 63.9 | 56.4 | 50.6 | 10 | 6.05 | 5.75 | 5.29 | 5.46 | 4.91 | 4.77 | 4.72 | 4.71 | 5.89 | 5.67 | 5.95 | 5.56 | 200 | 54 | 45 | 20 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 61 | 2349 | 420 | 380 | 337 | 253 | 124 | 23 | 0 | 0 | 10 | 89 | 265 | 448 | 4245 | 100 | 86 | 149 | 211 | 364 | 523 | 721 | 745 | 632 | 431 | 204 | 79 | 920 | 2 | 1 | 1 | 6 | 23 | 96 | 256 | 281 | 192 | 55 | 7 | 0 | 14466 | 98 | 120 | 200 | 386 | 698 | 1694 | 3170 | 3540 | 2741 | 1340 | 418 | 61 | 6692 | 9 | 15 | 40 | 123 | 259 | 717 | 1535 | 1846 | 1423 | 602 | 118 | 5 | 4.9 | 4.8 | 5 | 4.8 | 5.1 | 5.2 | 5.2 | 5.3 | 5 | 4.7 | 4.6 | 4.7 | 4.6 | 19 | 3.8 | 4.6 | 2.8 | 1.5 | 0.4 | 0.2 | 0.1 | 0.2 | 0.2 | 0.9 | 1.2 | 3.1 | 35.5 | 20.1 | 12.8 | 14.5 | 3.6 | 2.9 | 0.9 | 0.5 | 1.5 | 1.9 | 7.9 | 3 | 12.2 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 8.2 | 4.8 | 2.9 | 3.5 | 1.1 | 0.7 | 0.3 | 0.1 | 0.3 | 0.4 | 1.7 | 1 | 2.7 | 81.1 | 82.2 | 84.5 | 90.3 | 93.2 | 99.1 | 99.9 | 100.4 | 100.3 | 96.6 | 88 | 79.7 | 56 | 55 | 58.1 | 58.4 | 62.1 | 66.2 | 70.9 | 68.5 | 69.7 | 62.1 | 57.3 | 54.7 | 76.8 | 77.9 | 79.5 | 83.2 | 87.4 | 92 | 94.6 | 96.4 | 96.6 | 91 | 83.6 | 75.1 | 53.4 | 54 | 57.8 | 57.7 | 61.4 | 66.4 | 68.9 | 69 | 67.4 | 60.9 | 56.1 | 52.1 | 72.8 | 73.1 | 74.9 | 78.3 | 81.7 | 87.9 | 91.3 | 93.1 | 92.4 | 87.3 | 79.2 | 71.1 | 52.1 | 53.3 | 56.4 | 57.3 | 62.1 | 65.6 | 68.5 | 68.1 | 67.1 | 60.3 | 54.5 | 50.9 | 68.5 | 67.5 | 70.4 | 73 | 76.8 | 83.6 | 88.5 | 90.2 | 88.7 | 82.1 | 73.8 | 66.2 | 50 | 51.1 | 55.5 | 56.7 | 60.9 | 64.5 | 68.1 | 68 | 65.6 | 59.7 | 52.7 | 49.6 | 61.1 | 60.1 | 63.9 | 64.4 | 68.5 | 70.6 | 73.7 | 74 | 73.4 | 70.2 | 61.3 | 59.5 | 74.5 | 71.4 | 77.5 | 79.1 | 84.8 | 90.3 | 92.5 | 92.6 | 93.2 | 82.6 | 70.2 | 68 | 56.8 | 57.2 | 60.7 | 61.7 | 65.7 | 68.4 | 71.9 | 71.9 | 71.4 | 66 | 59.3 | 56.8 | 67.4 | 69.6 | 73.4 | 75.8 | 81.1 | 87.2 | 89.8 | 90.9 | 90 | 80.5 | 73.3 | 66 | 54.7 | 55.2 | 58.6 | 59.5 | 63.7 | 66.8 | 70.4 | 70.4 | 69.6 | 63.8 | 57.6 | 54.6 | 64.7 | 67.4 | 70.6 | 72.9 | 78.1 | 84.9 | 87.6 | 89 | 86.3 | 79.6 | 72.8 | 63 | 53 | 53.2 | 56.3 | 57.6 | 61.4 | 65.2 | 69 | 69 | 67.7 | 61.7 | 55.9 | 52.7 | 62.5 | 63.3 | 67.7 | 71 | 74.5 | 82.5 | 85.5 | 86.9 | 83.9 | 76.1 | 69.1 | 61 | 28.6 | 26.4 | 27.2 | 27 | 25.8 | 29.4 | 29.8 | 30.8 | 31.1 | 30.2 | 30.2 | 28.3 | 36.8 | 38.8 | 38.3 | 39.8 | 38.1 | 38.2 | 33.3 | 34.6 | 36 | 41.1 | 39.6 | 37.8 | 19.1 | 19.8 | 20 | 19.3 | 18.4 | 17 | 14 | 14.7 | 15.3 | 18.5 | 18.7 | 20.1 | 29.2 | 31.1 | 32.1 | 32.4 | 31.9 | 34.3 | 29.6 | 30.6 | 31.4 | 32.1 | 32.3 | 28.5 | 17.9 | 18.3 | 19 | 17.9 | 16.7 | 16.1 | 12.7 | 13.6 | 14.8 | 17 | 18.2 | 17.6 | 0.298 | 0.306 | 0.319 | 0.329 | 0.347 | 0.349 | 0.377 | 0.38 | 0.345 | 0.352 | 0.306 | 0.309 | 2.559 | 2.553 | 2.5 | 2.482 | 2.453 | 2.452 | 2.451 | 2.421 | 2.502 | 2.441 | 2.568 | 2.558 | 294 | 303 | 305 | 304 | 298 | 295 | 286 | 285 | 292 | 281 | 289 | 284 | 26 | 29 | 32 | 35 | 36 | 36 | 36 | 36 | 32 | 31 | 25 | 24 | 1054 | 1329 | 1771 | 2147 | 2324 | 2467 | 2345 | 2226 | 1924 | 1499 | 1157 | 954 | 68 | 119 | 93 | 98 | 141 | 126 | 128 | 87 | 84 | 97 | 63 | 64 | 1.19 | N/A | N/A | 1.64 | N/A | N/A | N/A | -331 | 421 | N/A | 1.19 | N/A | -2.9 | 1.35 | N/A | N/A | N/A | -193 | 423 | 223 | 41
4 | USA | CA | WATSONVILLE | 745058 | 23277 | 36.936 | -121.789 | 160 | 14.61 | -8 | NAP | 99-19 | 3C | 12 | 34.1 | 36.4 | 22 | 16.6 | 52.5 | 25.9 | 20 | 50.1 | 18.4 | 56.2 | 15.7 | 56.8 | 2.5 | 330 | 0.455 | 9 | 20.5 | 86.2 | 62.5 | 81.1 | 62 | 77 | 61.2 | 65.4 | 79.8 | 64.1 | 77.1 | 62.8 | 74.4 | 6.4 | 210 | 60.9 | 80.3 | 66.6 | 59.3 | 75.9 | 66.2 | 58.3 | 73.1 | 65.3 | 30.2 | 80.1 | 29.2 | 77 | 28.4 | 74.4 | 72.9 | 15 | 12.4 | 10.9 | 30.1 | 96.8 | 2.6 | 4.3 | 28.3 | 99.9 | 26.8 | 102.4 | 25.3 | 104.8 | 23.4 | 107.9 | 28.2 | 68.9 | 2.5 | 1.4 | 26.4 | 70 | 24.9 | 70.8 | 23.5 | 71.6 | 21.7 | 72.7 | 57.6 | 51.3 | 52.3 | 54.2 | 55.6 | 58.4 | 61.2 | 62.6 | 63.3 | 63.8 | 61.2 | 55.5 | 50.9 | 6.43 | 4.89 | 4.97 | 4.7 | 4.67 | 3.91 | 3.58 | 3.09 | 3.48 | 4.93 | 5.18 | 5.1 | 4.61 | 148 | 45 | 29 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 45 | 2855 | 424 | 356 | 337 | 287 | 212 | 124 | 91 | 75 | 81 | 143 | 287 | 438 | 2906 | 86 | 94 | 142 | 173 | 260 | 337 | 389 | 414 | 413 | 348 | 177 | 73 | 137 | 0 | 0 | 1 | 5 | 6 | 11 | 15 | 24 | 45 | 27 | 3 | 0 | 1652 | 10 | 15 | 40 | 92 | 112 | 159 | 123 | 181 | 461 | 390 | 68 | 1 | 549 | 1 | 0 | 6 | 33 | 34 | 51 | 20 | 53 | 193 | 145 | 13 | 0 | 4.1 | 3.3 | 4 | 4.2 | 4.7 | 4.9 | 4.9 | 4.8 | 4.4 | 4.1 | 3.7 | 3.2 | 3.4 | 21.3 | 4.2 | 3.5 | 3.6 | 1.9 | 0.2 | 0.1 | 0.1 | 0.1 | 0.3 | 1.1 | 3.3 | 3.5 | 48.3 | 10.9 | 10.4 | 11 | 6.7 | 1 | 1.3 | 1.3 | 1.1 | 1.5 | 3.8 | 8 | 10.5 | 10.7 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 8.1 | 2.9 | 3 | 2.4 | 2 | 0.2 | 0.2 | 0.3 | 0.2 | 0.4 | 1.1 | 2.4 | 2.3 | 75 | 76.2 | 79.4 | 84 | 84.2 | 86.7 | 82.2 | 86.6 | 93.4 | 91.1 | 81.5 | 71.6 | 54.5 | 58.8 | 62.1 | 62.9 | 63 | 63.8 | 65.3 | 65.3 | 64.7 | 62.1 | 60.3 | 53.7 | 69.5 | 71.1 | 72.5 | 74.6 | 75.7 | 78.3 | 77.4 | 78.6 | 85.7 | 83.4 | 74.4 | 66 | 54.7 | 56.5 | 58.4 | 58.8 | 59.7 | 62.5 | 63.6 | 63.9 | 61.9 | 60.3 | 58.2 | 53.7 | 64.2 | 65.4 | 67.5 | 69.2 | 70.8 | 73.2 | 73.3 | 74.1 | 78.7 | 77.4 | 69.6 | 62.7 | 53.8 | 54.5 | 56.2 | 56.3 | 58.8 | 60.8 | 62.1 | 62.6 | 62.4 | 59 | 55.9 | 53.3 | 60.4 | 61.3 | 63.5 | 64.6 | 66.9 | 70.1 | 70.3 | 71.5 | 73.1 | 72 | 64.6 | 59.6 | 52.8 | 53.4 | 54.7 | 55.3 | 57.4 | 59.7 | 61 | 61.7 | 61.3 | 58.1 | 54.8 | 52.8 | 59.3 | 61.2 | 63.4 | 64.1 | 64.9 | 65.9 | 66.4 | 66.4 | 67.2 | 65.4 | 63.3 | 60.8 | 66 | 70.4 | 77 | 81.9 | 79.7 | 81.6 | 80.1 | 81.5 | 82.4 | 80.5 | 74.1 | 64.3 | 57.1 | 58.7 | 60.1 | 60.5 | 61.3 | 63.4 | 64.1 | 64.5 | 64.9 | 63.1 | 60.6 | 58.2 | 62.7 | 66.4 | 69.3 | 71.7 | 73.2 | 76.3 | 76 | 76.7 | 79.4 | 76.1 | 68 | 60.9 | 55.5 | 56.7 | 57.9 | 58.2 | 59.4 | 61.5 | 62.5 | 63.1 | 63.4 | 61.5 | 58.9 | 56.2 | 60.8 | 63.1 | 64.6 | 66.3 | 68.8 | 72.4 | 72.6 | 73.7 | 76.1 | 72.6 | 65.7 | 59.2 | 54 | 54.7 | 56 | 56.3 | 57.9 | 60 | 61.2 | 61.8 | 61.8 | 59.8 | 57.1 | 54.2 | 58.8 | 59.9 | 61.7 | 63.2 | 66.1 | 69.1 | 69.8 | 70.8 | 72.1 | 69 | 63.2 | 57.7 | 19.1 | 18.1 | 18.7 | 19.1 | 18.6 | 18.7 | 16.8 | 17 | 20.5 | 22.1 | 21 | 18.5 | 26.2 | 26.6 | 26.7 | 28 | 26.9 | 26.4 | 23 | 23.3 | 31.1 | 32.7 | 28.6 | 23.2 | 14.7 | 14.8 | 14.9 | 14.9 | 13.8 | 12.7 | 10.8 | 10.8 | 13.1 | 14.1 | 14.1 | 13.3 | 19.4 | 20.6 | 22 | 23.2 | 23.1 | 23.1 | 21.2 | 21.7 | 25.9 | 25.5 | 21.2 | 14.1 | 12.2 | 12.4 | 13.2 | 13.5 | 12.6 | 11.5 | 10 | 10.1 | 11.6 | 12 | 11.9 | 9.7 | 0.319 | 0.325 | 0.326 | 0.353 | 0.364 | 0.355 | 0.358 | 0.342 | 0.35 | 0.323 | 0.311 | 0.315 | 2.548 | 2.538 | 2.53 | 2.431 | 2.416 | 2.452 | 2.461 | 2.496 | 2.465 | 2.576 | 2.576 | 2.574 | 278 | 290 | 299 | 294 | 291 | 292 | 291 | 294 | 286 | 287 | 279 | 272 | 24 | 28 | 31 | 36 | 37 | 36 | 35 | 33 | 32 | 26 | 23 | 23 | 809 | 1094 | 1543 | 1969 | 2279 | 2487 | 2345 | 2114 | 1803 | 1342 | 941 | 714 | 95 | 122 | 130 | 165 | 135 | 100 | 70 | 80 | 67 | 79 | 52 | 93 | 0.65 | N/A | N/A | N/A | N/A | 1.26 | N/A | -351 | 331 | N/A | 0.67 | N/A | -2.2 | N/A | N/A | N/A | N/A | -194 | 245 | 56 | 44
4 | USA | CA | MOUNTAIN VIEW MOFFETT | 745090 | 23244 | 37.417 | -122.05 | 39 | 14.68 | -8 | NAP | 94-19 | 3C | 12 | 36.4 | 38.8 | 21.1 | 15.9 | 52.3 | 25.4 | 19.4 | 51.1 | 20.5 | 56.5 | 18.2 | 55.5 | 1.3 | 140 | 0.442 | 8 | 16.5 | 88.1 | 65.6 | 83.8 | 64.8 | 80.5 | 64.1 | 68.3 | 82.6 | 66.9 | 79.9 | 65.8 | 77.5 | 9.7 | 340 | 63.2 | 86.9 | 74.2 | 61.6 | 81.9 | 71.9 | 60.8 | 79.8 | 71.1 | 32.5 | 81.9 | 31.4 | 79.9 | 30.5 | 77.6 | 74.8 | 18.8 | 17 | 15.4 | 31.3 | 96.2 | 2.3 | 4.2 | 29.6 | 99.2 | 28.3 | 101.7 | 27 | 104.1 | 25.2 | 107.2 | 28.7 | 70.4 | 2.4 | 2 | 27 | 71.9 | 25.6 | 73.1 | 24.2 | 74.2 | 22.5 | 75.7 | 60.3 | 51.4 | 53.3 | 56.1 | 58.8 | 62 | 66 | 67.8 | 68.1 | 67.9 | 63.6 | 56.5 | 51 | 7.71 | 4.34 | 4.49 | 4.58 | 4.93 | 4.59 | 4.53 | 3.65 | 3.71 | 4.71 | 4.57 | 4.66 | 4.85 | 108 | 35 | 17 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 44 | 2185 | 422 | 328 | 277 | 197 | 119 | 35 | 10 | 8 | 17 | 82 | 257 | 433 | 3852 | 79 | 109 | 195 | 264 | 372 | 481 | 552 | 562 | 538 | 422 | 202 | 76 | 451 | 0 | 0 | 1 | 10 | 25 | 66 | 97 | 105 | 105 | 39 | 3 | 0 | 2912 | 0 | 3 | 25 | 124 | 242 | 480 | 470 | 502 | 720 | 322 | 24 | 0 | 852 | 0 | 0 | 1 | 29 | 82 | 154 | 116 | 133 | 254 | 82 | 1 | 0 | 5.5 | 3.9 | 4.9 | 5.4 | 6.2 | 6.9 | 7.2 | 7.3 | 6.7 | 5.4 | 4.5 | 3.7 | 4.3 | 13.9 | 2.8 | 2.2 | 2.3 | 1 | 0.2 | 0.1 | 0 | 0 | 0.2 | 0.8 | 2 | 2 | 31.4 | 6.8 | 7.2 | 6.4 | 4 | 1.7 | 0.5 | 0.5 | 0.6 | 1.2 | 3.5 | 5.6 | 4.4 | 6.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 5.2 | 1.9 | 2 | 1.6 | 1.1 | 0.4 | 0.1 | 0.1 | 0.2 | 0.3 | 0.9 | 1.7 | 1.2 | 69.3 | 73.3 | 77.4 | 84.4 | 88.7 | 91.3 | 89.6 | 90.4 | 92.7 | 87.7 | 77.8 | 67.2 | 53.1 | 56.6 | 59.6 | 62.9 | 64.1 | 65.5 | 69.4 | 68 | 65.5 | 62.9 | 59 | 55.6 | 64.9 | 68.2 | 72.1 | 77.2 | 80.7 | 84.2 | 83 | 83.3 | 87.3 | 81.6 | 71.6 | 63.9 | 53.4 | 55.3 | 57.3 | 59.8 | 63.1 | 65.1 | 67.1 | 66.8 | 64.8 | 61 | 58.6 | 54.8 | 62.1 | 64.4 | 68.2 | 72.3 | 74.4 | 79.1 | 78.9 | 79.1 | 81.7 | 77.2 | 67.8 | 61.9 | 53.3 | 54 | 56.2 | 58.8 | 60.7 | 64.2 | 65.5 | 65.7 | 64.1 | 59.9 | 56.4 | 54.2 | 59.4 | 61.5 | 65 | 68.1 | 70.7 | 75.1 | 75.6 | 75.7 | 77.2 | 73.1 | 64.7 | 59.7 | 52.3 | 53 | 55.3 | 56.6 | 59 | 62.5 | 64.4 | 64.5 | 63.5 | 59.6 | 55.5 | 53.4 | 59.8 | 59.9 | 62 | 64.9 | 67.5 | 69.3 | 70.5 | 70.1 | 69.5 | 66.8 | 62.9 | 60.4 | 63.9 | 66.9 | 74.2 | 79.9 | 85 | 86.6 | 85.6 | 84.7 | 84.1 | 79 | 72.2 | 63.6 | 56.7 | 57.7 | 59.8 | 62.2 | 63.9 | 66.7 | 67.8 | 68 | 67.1 | 64.6 | 61 | 58.7 | 60.5 | 64.9 | 68.6 | 74.9 | 75.9 | 80.9 | 81.1 | 81 | 80.3 | 75.1 | 68.2 | 62 | 54.9 | 56 | 58.1 | 59.9 | 61.7 | 65 | 66.2 | 66.3 | 65.7 | 62.9 | 59.3 | 56.6 | 59.3 | 62.4 | 65.5 | 69.9 | 73.1 | 77.2 | 77.7 | 77.6 | 78.6 | 72.6 | 64.9 | 59.9 | 53.3 | 54.4 | 56.4 | 58 | 59.9 | 63.3 | 64.9 | 65 | 64.3 | 61.3 | 57.6 | 54.4 | 57.6 | 60.2 | 63.3 | 66.6 | 69.8 | 74.1 | 75.1 | 75 | 75.9 | 70 | 63.1 | 58.3 | 15.2 | 15.4 | 16.6 | 17.6 | 17.1 | 18.3 | 16.6 | 16.5 | 18.9 | 18.8 | 16.8 | 15.2 | 19.5 | 20.8 | 22.1 | 24.7 | 24 | 24.4 | 21.6 | 21.7 | 26.8 | 26.1 | 21.3 | 17.3 | 11 | 11.6 | 11.8 | 12.6 | 11.7 | 11.2 | 9.8 | 9.6 | 11.1 | 11.8 | 11 | 9.9 | 14.3 | 17.1 | 18.8 | 21.7 | 21.5 | 22 | 19.8 | 19.9 | 22.2 | 20.3 | 16.7 | 11.5 | 9.2 | 10.3 | 11 | 11.8 | 11 | 10.5 | 9.4 | 9.3 | 10 | 10 | 10 | 7.9 | 0.324 | 0.333 | 0.338 | 0.359 | 0.37 | 0.362 | 0.366 | 0.348 | 0.353 | 0.335 | 0.322 | 0.324 | 2.541 | 2.516 | 2.492 | 2.407 | 2.396 | 2.426 | 2.423 | 2.47 | 2.442 | 2.533 | 2.55 | 2.55 | 275 | 286 | 294 | 292 | 289 | 290 | 288 | 292 | 285 | 281 | 273 | 266 | 24 | 28 | 32 | 36 | 38 | 36 | 36 | 34 | 33 | 27 | 24 | 23 | 771 | 1069 | 1512 | 1961 | 2257 | 2466 | 2326 | 2082 | 1768 | 1311 | 909 | 680 | 101 | 125 | 132 | 157 | 144 | 102 | 75 | 88 | 68 | 80 | 55 | 95 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | -283 | N/A | N/A | N/A | N/A | -2.11 | N/A | N/A | N/A | N/A | -194 | 239 | N/A | 43
4 | USA | CA | TRAVIS AFB | 745160 | 23202 | 38.267 | -121.933 | 62 | 14.66 | -8 | NAP | 94-19 | 3A | 1 | 30.3 | 33.2 | 17.3 | 13.2 | 53.8 | 21.2 | 16 | 52.1 | 29 | 52.2 | 25.9 | 51.8 | 3.8 | 30 | 0.641 | 8 | 30 | 99.2 | 67.5 | 95.4 | 66.6 | 91.4 | 65.6 | 70 | 93.6 | 68.4 | 90.9 | 67 | 88.4 | 10.2 | 240 | 61.5 | 81.7 | 72.3 | 60.1 | 77.8 | 71.5 | 58.9 | 74.6 | 70.9 | 33.8 | 93.7 | 32.5 | 91.1 | 31.4 | 88.1 | 81.5 | 28.8 | 26.8 | 25 | 24.7 | 105.8 | 4.3 | 2.8 | 21.6 | 107.8 | 19.2 | 109.5 | 16.8 | 111 | 13.7 | 113.1 | 23.8 | 73.3 | 4.1 | 2.7 | 20.9 | 75.2 | 18.5 | 76.8 | 16.2 | 78.3 | 13.2 | 80.2 | 60.9 | 47.7 | 50.9 | 55.3 | 58.6 | 64.1 | 70.1 | 72.8 | 73.1 | 71.5 | 64.4 | 54.3 | 47.7 | 10.7 | 4.82 | 4.5 | 4.97 | 5.9 | 5.99 | 5.93 | 4.89 | 4.77 | 5.41 | 5.3 | 5.7 | 5.28 | 284 | 101 | 39 | 11 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 107 | 2483 | 535 | 394 | 302 | 205 | 88 | 14 | 1 | 1 | 8 | 75 | 324 | 536 | 4273 | 31 | 66 | 176 | 262 | 438 | 602 | 707 | 715 | 644 | 445 | 151 | 36 | 994 | 0 | 0 | 1 | 14 | 61 | 166 | 243 | 251 | 202 | 55 | 1 | 0 | 12142 | 0 | 1 | 52 | 306 | 930 | 2191 | 2728 | 2710 | 2348 | 818 | 57 | 1 | 5832 | 0 | 0 | 3 | 84 | 380 | 1099 | 1389 | 1395 | 1197 | 280 | 5 | 0 | 12 | 7.4 | 8.6 | 9.9 | 12.1 | 15.2 | 16.7 | 18.4 | 17 | 13.5 | 10.1 | 7.3 | 7.4 | 21.7 | 4.1 | 4 | 2.8 | 1.2 | 0.8 | 0.2 | 0 | 0 | 0.1 | 1.1 | 2 | 4.3 | 35.4 | 13.3 | 12.9 | 10 | 4.2 | 3.1 | 2 | 0.4 | 0.6 | 0.6 | 5 | 6.3 | 12 | 11.2 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 6.1 | 3.5 | 2.9 | 2.7 | 1 | 0.8 | 0.5 | 0.1 | 0.1 | 0.2 | 1.2 | 1.5 | 3.3 | 68 | 72.2 | 79.4 | 87.9 | 95.4 | 102.3 | 102.8 | 102.7 | 100.3 | 93 | 80.3 | 67.9 | 52.7 | 57.6 | 60.7 | 63.7 | 66.2 | 69.4 | 68.8 | 68.7 | 66.1 | 63.4 | 59.5 | 54.1 | 63.4 | 67.7 | 74.7 | 81.8 | 89.5 | 97.1 | 97.3 | 97.5 | 96.8 | 87.4 | 74.5 | 63.1 | 54 | 56.4 | 59.5 | 61.9 | 64.7 | 68.1 | 67.7 | 67.7 | 65.4 | 62.2 | 58.4 | 53.7 | 60.2 | 63.8 | 71.2 | 77.1 | 84 | 91.3 | 92.6 | 92.8 | 92.2 | 82.2 | 70 | 60.2 | 52.5 | 54 | 58.2 | 60.1 | 62.6 | 65.9 | 67 | 66.6 | 64.2 | 60.1 | 56.3 | 52.5 | 57 | 60.8 | 67.2 | 72.2 | 78.9 | 86.3 | 88.1 | 88 | 87.6 | 78.5 | 65.8 | 57.3 | 51.3 | 52.8 | 56.2 | 58 | 60.9 | 64.4 | 65.9 | 65.8 | 63.4 | 58.8 | 55 | 51.6 | 59.9 | 61.1 | 63.8 | 67.4 | 69.1 | 72.4 | 71.6 | 71.5 | 69.6 | 66.6 | 63.3 | 60.4 | 62.3 | 66.7 | 74.1 | 82.8 | 91 | 96.9 | 98 | 97.1 | 92.5 | 84.5 | 71.1 | 62.9 | 56.3 | 58.8 | 61.4 | 64.1 | 66.3 | 69.3 | 69.2 | 69.2 | 67.5 | 64.4 | 61.1 | 57.5 | 59.7 | 64.4 | 71.5 | 77.7 | 85.9 | 92 | 93.6 | 92.5 | 89.7 | 81.3 | 70 | 59.7 | 54.3 | 56.6 | 59.4 | 61.5 | 64 | 67.2 | 67.7 | 67.6 | 66 | 62.5 | 59.2 | 55.3 | 57.5 | 61.5 | 68.3 | 74.2 | 81.5 | 89.3 | 90.3 | 89.5 | 87.3 | 76.8 | 66.4 | 57.5 | 52.4 | 54.6 | 57.4 | 59.3 | 61.8 | 65.1 | 66.2 | 66.1 | 64.5 | 61 | 57.2 | 53.3 | 55.7 | 58.8 | 64.8 | 70 | 76.5 | 84.5 | 86.8 | 86.6 | 84.4 | 73.6 | 63.5 | 55.7 | 17.2 | 18.7 | 21.3 | 23.4 | 25.3 | 28.5 | 30 | 30 | 29.6 | 26.1 | 22 | 17.9 | 23.8 | 24.9 | 28.3 | 31.8 | 34.1 | 36.9 | 36.6 | 37.4 | 37.6 | 33.8 | 29.3 | 22 | 15.2 | 14.9 | 15.9 | 15.6 | 13.8 | 13.4 | 12.7 | 12.7 | 12.7 | 14.1 | 15.2 | 13.8 | 16.6 | 20.3 | 24.6 | 27.9 | 31.3 | 34.2 | 33.8 | 33.4 | 32.3 | 28.1 | 23.2 | 13.9 | 12.5 | 13.6 | 14.6 | 14.9 | 13.9 | 13.5 | 12.8 | 12.5 | 12 | 12.5 | 13.7 | 10.7 | 0.32 | 0.322 | 0.335 | 0.355 | 0.36 | 0.359 | 0.36 | 0.346 | 0.345 | 0.329 | 0.323 | 0.326 | 2.526 | 2.524 | 2.473 | 2.398 | 2.408 | 2.417 | 2.407 | 2.437 | 2.445 | 2.52 | 2.518 | 2.511 | 274 | 289 | 294 | 293 | 292 | 291 | 289 | 292 | 286 | 282 | 270 | 262 | 24 | 28 | 32 | 37 | 37 | 37 | 37 | 35 | 33 | 27 | 24 | 23 | 715 | 1034 | 1469 | 1938 | 2320 | 2575 | 2534 | 2264 | 1859 | 1325 | 871 | 634 | 121 | 132 | 147 | 163 | 138 | 105 | 72 | 71 | 63 | 87 | 60 | 102 | N/A | -1.71 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.68 | N/A | -2.02 | N/A | N/A | N/A | N/A | -211 | 236 | N/A | 49
4 | USA | CA | CHINA LAKE | 746120 | 93104 | 35.688 | -117.693 | 2230 | 13.55 | -8 | NAP | 07-19 | 3B | 12 | 23.1 | 26.5 | -7.6 | 4 | 47.2 | -2.9 | 5.1 | 47.3 | 31.3 | 55.3 | 27.8 | 55 | 2.9 | 200 | 0.519 | 7 | 31.4 | 108.3 | 65.2 | 106 | 64.5 | 103.8 | 63.6 | 69 | 97.6 | 67.7 | 97.6 | 66.3 | 97 | 10.7 | 170 | 59.6 | 82.8 | 79.3 | 55.9 | 72.3 | 83.3 | 52.5 | 63.7 | 81.5 | 34.3 | 97.4 | 33.1 | 97.4 | 32 | 97.4 | 74.3 | 27.5 | 24.4 | 20.7 | 16.8 | 112.2 | 3.5 | 1.8 | 14.3 | 113.5 | 12.3 | 114.6 | 10.4 | 115.6 | 7.9 | 117 | 13.4 | 71.7 | 3.3 | 2.2 | 11 | 73.3 | 9.1 | 74.5 | 7.2 | 75.7 | 4.8 | 77.3 | 65.7 | 45.9 | 49.8 | 57.6 | 64.1 | 71.6 | 82 | 88.2 | 86.4 | 78.6 | 65.5 | 53.7 | 44.2 | 16.26 | 5.93 | 6.23 | 6.47 | 6.79 | 7.05 | 6.27 | 4.45 | 4.1 | 6.4 | 6.23 | 6.49 | 5.97 | 474 | 152 | 75 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 35 | 196 | 2431 | 593 | 426 | 239 | 95 | 24 | 0 | 0 | 0 | 3 | 66 | 339 | 646 | 6210 | 24 | 69 | 249 | 424 | 669 | 961 | 1184 | 1127 | 857 | 483 | 147 | 16 | 2692 | 0 | 0 | 11 | 68 | 228 | 511 | 719 | 662 | 410 | 82 | 1 | 0 | 43226 | 5 | 32 | 384 | 1248 | 3534 | 8109 | 11702 | 10434 | 6051 | 1551 | 176 | 0 | 26697 | 1 | 0 | 85 | 458 | 1838 | 5212 | 7933 | 6915 | 3639 | 597 | 19 | 0 | 7.6 | 5.3 | 7.3 | 8.8 | 9.8 | 9.3 | 8.7 | 8 | 7.9 | 7.3 | 6.9 | 5.6 | 5.8 | 4 | 0.8 | 1.1 | 0.5 | 0.1 | 0.1 | 0 | 0.1 | 0.1 | 0.2 | 0.2 | 0.3 | 0.6 | 9.4 | 5.1 | 4.4 | 2.6 | 1.4 | 0.8 | 0.2 | 0.7 | 0.6 | 2.1 | 1.2 | 1.3 | 3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 1.1 | 1.1 | 0.6 | 0.3 | 0.2 | 0 | 0.1 | 0.1 | 0.4 | 0.3 | 0.3 | 0.7 | 71.7 | 77.9 | 87.1 | 93.5 | 101.2 | 110.4 | 111.8 | 108.8 | 104.8 | 93.8 | 82.6 | 69 | 50.1 | 51.6 | 55 | 58.2 | 60.6 | 64.4 | 66.1 | 65.5 | 65.2 | 59.9 | 53.7 | 50 | 67.4 | 74.5 | 82.2 | 89 | 96.9 | 106.5 | 109.3 | 106.7 | 101.6 | 90 | 79.3 | 65.1 | 47.1 | 50.5 | 53.6 | 55.8 | 59 | 63.4 | 65.6 | 65.1 | 63.1 | 58.9 | 51.9 | 47.4 | 64 | 70.5 | 78.1 | 85.4 | 94 | 103.9 | 106.8 | 104.8 | 99.2 | 86.6 | 75.2 | 61.8 | 46.1 | 49.1 | 51.9 | 54.6 | 58 | 62.1 | 65 | 64.3 | 62.4 | 56.4 | 51.3 | 45.9 | 60.5 | 66.3 | 74.6 | 81.8 | 90.3 | 100.7 | 104.3 | 102.6 | 96.7 | 82.8 | 70.2 | 58.3 | 45 | 47.1 | 50.7 | 53.5 | 57.2 | 61.3 | 64.3 | 63.3 | 61.2 | 54.8 | 48.9 | 44.4 | 53.5 | 54.7 | 56.5 | 59.5 | 61.8 | 67.4 | 71 | 70.7 | 68.6 | 64.3 | 55.4 | 53.5 | 62.6 | 66.6 | 76.9 | 87.4 | 97.1 | 104.1 | 92.2 | 97.8 | 95 | 82.9 | 76.5 | 62.5 | 50.9 | 51.4 | 54.9 | 57.3 | 60.1 | 65.5 | 69.2 | 68.9 | 67 | 61.4 | 53.6 | 51.1 | 59.5 | 70.7 | 75.9 | 85.1 | 92.9 | 100.6 | 98 | 97.2 | 95.6 | 81.8 | 74.5 | 60.8 | 49 | 50 | 53.3 | 55.8 | 59 | 63.9 | 68.2 | 67.1 | 65.1 | 59 | 52 | 48.6 | 58.4 | 68.1 | 75.6 | 81.9 | 90.5 | 98.7 | 97.7 | 96.9 | 92.3 | 81 | 71.8 | 57.5 | 46.8 | 48.3 | 51.7 | 54.3 | 57.7 | 62.4 | 66.9 | 65.6 | 63 | 56.9 | 50.3 | 45.9 | 58.5 | 64.3 | 72.4 | 79.1 | 87.9 | 96.7 | 97.4 | 96.8 | 91.4 | 78.3 | 68.5 | 55.5 | 28 | 28.8 | 29.3 | 29.9 | 30.7 | 33.1 | 31.4 | 32.7 | 32.7 | 32.1 | 31.2 | 26.6 | 33.7 | 35.8 | 35.9 | 35.1 | 35.9 | 36.6 | 33.9 | 34.1 | 34.8 | 36.7 | 36.7 | 32 | 18.6 | 17.5 | 15.8 | 14.2 | 13 | 11.9 | 11 | 11.6 | 12.7 | 16.3 | 18.6 | 18.5 | 24.7 | 32.3 | 32.4 | 32.2 | 34.6 | 34.4 | 27.5 | 29.3 | 29.8 | 29.5 | 32.9 | 24.1 | 14.9 | 16.3 | 14.4 | 13.6 | 13 | 10.9 | 9.4 | 10.5 | 10.6 | 12.6 | 17.1 | 15 | 0.267 | 0.277 | 0.285 | 0.31 | 0.327 | 0.322 | 0.345 | 0.334 | 0.314 | 0.292 | 0.269 | 0.268 | 2.582 | 2.57 | 2.539 | 2.463 | 2.44 | 2.46 | 2.451 | 2.455 | 2.516 | 2.571 | 2.604 | 2.594 | 302 | 310 | 314 | 309 | 303 | 303 | 295 | 297 | 300 | 300 | 299 | 295 | 24 | 27 | 30 | 35 | 36 | 36 | 36 | 35 | 31 | 27 | 23 | 22 | 961 | 1277 | 1751 | 2193 | 2491 | 2713 | 2523 | 2357 | 2012 | 1506 | 1106 | 871 | 72 | 117 | 75 | 81 | 101 | 96 | 106 | 69 | 52 | 77 | 46 | 65 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.15 | N/A | -3.06 | 0.77 | N/A | N/A | N/A | -209 | 382 | 207 | 28
4 | USA | CA | LEMORE NAS | 747020 | 23110 | 36.333 | -119.95 | 232 | 14.57 | -8 | NAP | 94-19 | 3B | 12 | 28.3 | 31.1 | 17.4 | 13.3 | 41.1 | 20.7 | 15.6 | 44.3 | 24.4 | 51.6 | 20.2 | 50.6 | 4.2 | 260 | 0.484 | 7 | 34.5 | 103.7 | 70 | 101.3 | 69.1 | 98.9 | 68.4 | 73.2 | 97.4 | 71.4 | 96.1 | 69.9 | 94.6 | 8.4 | 10 | 64.3 | 91.1 | 84.8 | 62.1 | 84.1 | 83.7 | 59.8 | 77.4 | 81.9 | 36.8 | 97.1 | 35.2 | 96.2 | 33.8 | 94.7 | 82.6 | 21 | 18.2 | 16 | 25.2 | 108 | 4.2 | 2.1 | 22.1 | 109.5 | 19.7 | 110.7 | 17.3 | 111.9 | 14.3 | 113.4 | 23.3 | 75.9 | 4.4 | 2.9 | 20.2 | 78 | 17.6 | 79.6 | 15.2 | 81.3 | 12 | 83.4 | 63.8 | 48 | 51.5 | 57.2 | 61.8 | 68.4 | 75.6 | 81.1 | 80 | 75.1 | 65.1 | 54.4 | 46.8 | 13.16 | 5.26 | 5.44 | 5.73 | 6.72 | 6.79 | 6.22 | 4.46 | 4.47 | 6.12 | 5.88 | 6.07 | 5.55 | 313 | 101 | 43 | 9 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 132 | 2293 | 526 | 378 | 247 | 140 | 42 | 3 | 0 | 0 | 4 | 70 | 319 | 564 | 5356 | 40 | 86 | 232 | 355 | 571 | 767 | 965 | 930 | 752 | 467 | 158 | 33 | 1861 | 0 | 0 | 6 | 43 | 148 | 320 | 500 | 465 | 306 | 72 | 1 | 0 | 27832 | 1 | 12 | 223 | 873 | 2397 | 4966 | 7324 | 6556 | 4141 | 1239 | 100 | 0 | 15952 | 0 | 1 | 40 | 321 | 1155 | 2923 | 4627 | 4069 | 2335 | 473 | 8 | 0 | 7.1 | 5.2 | 6.1 | 7.2 | 8.9 | 9.1 | 8.8 | 7.8 | 7.3 | 7.1 | 6.4 | 5.4 | 5.5 | 6.9 | 1.3 | 1.4 | 1.3 | 0.6 | 0.3 | 0.1 | 0 | 0 | 0.2 | 0.3 | 0.9 | 0.9 | 15 | 5.4 | 4.6 | 4.8 | 2.3 | 2.2 | 0.4 | 0.2 | 0.4 | 1.2 | 1.3 | 2.7 | 3.7 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 2.6 | 1.3 | 1.3 | 1.1 | 0.6 | 0.5 | 0.1 | 0 | 0.1 | 0.4 | 0.4 | 0.7 | 0.7 | 70 | 75.6 | 84.7 | 93.4 | 99.4 | 105.8 | 106.4 | 106 | 102.5 | 95.7 | 81.2 | 69.2 | 54.1 | 58.8 | 60.8 | 64.2 | 65.6 | 70.8 | 69.8 | 71.3 | 68.9 | 65.8 | 60.9 | 58 | 64.5 | 70.4 | 79.7 | 88.2 | 95 | 102 | 103.7 | 102.5 | 99.5 | 89.6 | 77.1 | 64.1 | 54.4 | 57.5 | 60 | 62.4 | 64.3 | 68.6 | 70 | 70 | 67.8 | 63.4 | 59.1 | 55.2 | 61.4 | 66.6 | 75.8 | 83.3 | 91 | 98.3 | 101.3 | 100 | 96.6 | 85 | 72.6 | 60.5 | 53.1 | 56.1 | 58.1 | 60.7 | 62.9 | 66.9 | 69.5 | 69.3 | 67.1 | 61.7 | 58.1 | 52.9 | 58.4 | 63.2 | 72 | 78.9 | 86.8 | 94.8 | 98.6 | 97.4 | 93.1 | 81.2 | 68.1 | 57 | 52.1 | 54.8 | 57.1 | 58.8 | 61.4 | 65.7 | 69.2 | 68.1 | 66.2 | 60.4 | 55.8 | 51.1 | 59.6 | 62.3 | 64.1 | 67.3 | 68.3 | 73.2 | 75.5 | 76.6 | 74.2 | 68.2 | 63.1 | 60.7 | 64.7 | 69.6 | 78.6 | 86.8 | 93.7 | 101.2 | 99.1 | 99.4 | 95.4 | 88 | 76.9 | 66.1 | 56.4 | 59.4 | 61.5 | 64.1 | 66.1 | 70.7 | 73 | 73.1 | 71 | 66 | 61 | 57 | 61 | 67.1 | 75.3 | 84.5 | 91.6 | 97.7 | 97.5 | 97.5 | 90.8 | 85.6 | 74 | 61.7 | 54.5 | 57.4 | 59.7 | 61.8 | 64.2 | 68.6 | 71.3 | 70.9 | 68.6 | 63.9 | 59.1 | 54.6 | 59.3 | 65 | 72.7 | 80.5 | 88.1 | 94.8 | 97 | 95.4 | 92 | 81.4 | 70.4 | 58.4 | 52.6 | 55.3 | 57.8 | 59.6 | 62.2 | 66.7 | 69.9 | 69.1 | 67 | 61.5 | 56.9 | 52.3 | 57.5 | 62 | 70.1 | 76.7 | 84.4 | 91.9 | 95.2 | 93.4 | 90.7 | 77.7 | 67 | 56 | 19.6 | 21.8 | 26.3 | 29.1 | 30.4 | 33.8 | 34.5 | 34.8 | 33.2 | 30.7 | 26 | 19.3 | 25.4 | 27.5 | 33 | 35.8 | 36.5 | 37.9 | 36.5 | 36.4 | 36.8 | 36.3 | 32.1 | 24 | 17.3 | 17.2 | 17 | 17.1 | 15.1 | 14.7 | 14.1 | 14 | 15.1 | 17.5 | 19.4 | 16.3 | 19.4 | 23.4 | 28.7 | 32.4 | 33.8 | 35.7 | 34 | 34.8 | 34 | 31.3 | 28.4 | 16.8 | 13.7 | 15.6 | 15.8 | 16 | 14.5 | 14.3 | 14 | 14.6 | 14.5 | 15.2 | 17.7 | 12.3 | 0.349 | 0.363 | 0.364 | 0.362 | 0.362 | 0.356 | 0.374 | 0.355 | 0.362 | 0.383 | 0.375 | 0.347 | 2.371 | 2.34 | 2.347 | 2.374 | 2.391 | 2.406 | 2.385 | 2.414 | 2.406 | 2.304 | 2.278 | 2.385 | 264 | 275 | 286 | 292 | 292 | 292 | 286 | 290 | 283 | 263 | 250 | 257 | 30 | 34 | 37 | 38 | 38 | 37 | 38 | 36 | 35 | 35 | 32 | 28 | 794 | 1140 | 1617 | 2050 | 2428 | 2681 | 2570 | 2358 | 1968 | 1438 | 986 | 729 | 107 | 123 | 132 | 147 | 120 | 83 | 85 | 63 | 56 | 74 | 54 | 94 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.95 | N/A | -1.98 | 0.92 | N/A | N/A | N/A | -266 | 319 | 88 | 29
4 | USA | CA | ONTARIO | 747040 | 03102 | 34.056 | -117.6 | 949 | 14.2 | -8 | NAP | 94-19 | 3A | 12 | 38.7 | 41 | 3.5 | 6.8 | 66.1 | 9.6 | 9.3 | 64.3 | 33.5 | 62.4 | 28 | 62.4 | 2.8 | 40 | 0.416 | 8 | 27.5 | 100.4 | 69.2 | 97.6 | 68.3 | 94.8 | 67.4 | 73 | 93.6 | 71.4 | 91.4 | 70.1 | 89.4 | 12 | 260 | 66.3 | 100.2 | 79.8 | 64.4 | 93.8 | 77.7 | 63.5 | 90.7 | 76 | 37 | 93.5 | 35.8 | 91.7 | 34.5 | 89.4 | 82.9 | 21 | 17.4 | 15.5 | 32.7 | 107.5 | 3.5 | 3.3 | 30.2 | 109.9 | 28.1 | 111.8 | 26.1 | 113.7 | 23.5 | 116 | 28.6 | 75.6 | 2.8 | 2.3 | 26.6 | 77.3 | 25 | 78.6 | 23.4 | 79.9 | 21.4 | 81.5 | 66.5 | 56.4 | 56.4 | 60.3 | 63.2 | 67.1 | 72.6 | 78.7 | 79.7 | 76.7 | 69.2 | 61.6 | 55.4 | 10.39 | 6.04 | 6 | 6.22 | 6.62 | 6.13 | 5.73 | 4.75 | 4.97 | 6.27 | 6.41 | 6.38 | 5.43 | 38 | 11 | 9 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 13 | 1323 | 273 | 247 | 173 | 110 | 46 | 7 | 0 | 0 | 1 | 29 | 138 | 299 | 6065 | 210 | 189 | 320 | 398 | 529 | 679 | 890 | 921 | 801 | 595 | 351 | 182 | 1878 | 7 | 8 | 26 | 57 | 110 | 236 | 425 | 456 | 353 | 160 | 37 | 3 | 20211 | 129 | 167 | 413 | 755 | 1141 | 2350 | 4450 | 4938 | 3630 | 1654 | 509 | 75 | 10170 | 16 | 36 | 122 | 286 | 486 | 1126 | 2412 | 2790 | 1964 | 755 | 171 | 6 | 6 | 5.1 | 5.2 | 6 | 6.8 | 7.1 | 7 | 6.9 | 6.4 | 5.8 | 5.6 | 4.7 | 5 | 22.4 | 5 | 5.6 | 3 | 1.5 | 0.6 | 0.2 | 0.1 | 0.1 | 0.2 | 0.9 | 1.4 | 3.6 | 39.9 | 20.9 | 16.3 | 11.5 | 4.4 | 5.6 | 1.3 | 0.6 | 0.4 | 1.2 | 6.4 | 3.2 | 11.9 | 9.5 | 0.4 | 0.2 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.6 | 9.2 | 5.4 | 4.1 | 3 | 1.1 | 1.2 | 0.4 | 0.2 | 0.1 | 0.3 | 1.4 | 0.9 | 2.9 | 82.2 | 84.6 | 89.4 | 93.6 | 97 | 101.5 | 103.2 | 104.6 | 103.9 | 97.9 | 90.5 | 80.8 | 54.8 | 56.4 | 58.8 | 60.1 | 64.4 | 68.4 | 70.7 | 70.6 | 68.1 | 62.9 | 58.5 | 53.7 | 77.8 | 79.4 | 83.4 | 87.6 | 90.5 | 95.3 | 98.6 | 100.1 | 99.3 | 92.9 | 85.3 | 75.5 | 53 | 54.6 | 57.8 | 59.1 | 63 | 67.6 | 70.9 | 69.9 | 68.6 | 61.7 | 57.4 | 52.3 | 73.6 | 74.1 | 78.7 | 82.3 | 85.6 | 90.5 | 95.2 | 97.1 | 95.4 | 88.5 | 80 | 71.8 | 51.9 | 53.2 | 56.5 | 58.1 | 62.5 | 66.5 | 69.3 | 68.7 | 67.3 | 60.5 | 55.8 | 51 | 69.7 | 68.6 | 73.4 | 77.6 | 80.5 | 86.8 | 92.1 | 93.4 | 91 | 83.5 | 74.9 | 67.1 | 50.8 | 52.1 | 55.4 | 56.7 | 61.9 | 65.9 | 68.6 | 68.1 | 66 | 59.6 | 54 | 50.1 | 60 | 60.6 | 63.9 | 65.2 | 69.8 | 72.2 | 75.6 | 75.9 | 73.3 | 69.4 | 62.4 | 59.4 | 69.6 | 74.7 | 79 | 85.1 | 89.5 | 91.9 | 97 | 95.6 | 95.5 | 84 | 73.6 | 66.4 | 57.2 | 57.9 | 61 | 62.7 | 66.8 | 69.7 | 73 | 73 | 71.3 | 66.5 | 60.3 | 57.3 | 66 | 68.1 | 76.2 | 80.4 | 84.7 | 89.6 | 93.2 | 93.7 | 91.8 | 81.1 | 73.3 | 65.4 | 55.4 | 56.1 | 59.1 | 60.3 | 64.6 | 68.2 | 71.3 | 71.2 | 69.7 | 64.6 | 58.8 | 55.4 | 63.9 | 67.1 | 72.1 | 75.7 | 80.7 | 86.6 | 90.9 | 91.4 | 88.9 | 79.3 | 72.2 | 62.8 | 53.9 | 54.5 | 57.3 | 58.6 | 62.7 | 66.6 | 69.8 | 69.5 | 68.2 | 62.8 | 57.3 | 53.7 | 63.2 | 64.6 | 69.1 | 72.7 | 76.6 | 83.4 | 88.1 | 89.4 | 85.5 | 76.3 | 69.4 | 61.1 | 20.8 | 19.8 | 21.5 | 22.3 | 21.9 | 24.9 | 26.8 | 27.5 | 25.8 | 23.5 | 23 | 20.8 | 28.7 | 30.1 | 30.5 | 31.2 | 30.9 | 31.1 | 29.5 | 30.4 | 30.8 | 31.9 | 31.3 | 29.2 | 12.9 | 12.5 | 12.4 | 12 | 11.3 | 10.3 | 9.9 | 10.5 | 10.3 | 11.5 | 12.5 | 13.3 | 20.3 | 22.4 | 25.2 | 26.8 | 27.6 | 28.9 | 27.6 | 27.9 | 27.4 | 26.3 | 24.8 | 19.3 | 10.6 | 10.6 | 11.4 | 11.2 | 10.8 | 10.5 | 10 | 10.3 | 9.8 | 10.3 | 11 | 10.1 | 0.304 | 0.313 | 0.335 | 0.35 | 0.352 | 0.362 | 0.377 | 0.361 | 0.345 | 0.338 | 0.301 | 0.3 | 2.544 | 2.534 | 2.448 | 2.413 | 2.437 | 2.422 | 2.442 | 2.474 | 2.505 | 2.496 | 2.591 | 2.587 | 290 | 299 | 298 | 297 | 295 | 291 | 286 | 290 | 291 | 285 | 289 | 285 | 26 | 29 | 34 | 37 | 36 | 37 | 36 | 34 | 32 | 30 | 24 | 23 | 1022 | 1307 | 1759 | 2141 | 2348 | 2523 | 2430 | 2299 | 1957 | 1490 | 1139 | 927 | 71 | 128 | 88 | 96 | 124 | 128 | 115 | 61 | 59 | 90 | 55 | 64 | 1.1 | N/A | -5.17 | N/A | N/A | N/A | N/A | -148 | 425 | 248 | 1.13 | N/A | -3.06 | 1.3 | N/A | N/A | N/A | -202 | 401 | 202 | 51
4 | USA | CA | IMPERIAL COUNTY AP | 747185 | 03144 | 32.834 | -115.579 | -58 | 14.73 | -8 | NAP | 94-19 | 2B | 12 | 35.9 | 38.5 | 9.2 | 8.8 | 61 | 13.1 | 10.7 | 61.1 | 26.8 | 63 | 23.9 | 63.5 | 4.6 | 260 | 0.468 | 8 | 26.3 | 111.9 | 72.7 | 109.5 | 72.3 | 107.8 | 72 | 80.9 | 97.1 | 79.5 | 96.3 | 78.2 | 95.9 | 7.2 | 110 | 76.9 | 140 | 88.5 | 75 | 130.8 | 88.8 | 72.9 | 121.8 | 89.2 | 44.3 | 97 | 42.9 | 95.8 | 41.5 | 96.1 | 89.2 | 26.1 | 22.3 | 18.8 | 30.7 | 117.1 | 3.4 | 2.9 | 28.2 | 119.2 | 26.2 | 120.9 | 24.3 | 122.6 | 21.8 | 124.7 | 25.9 | 83.8 | 3 | 2.7 | 23.7 | 85.7 | 22 | 87.3 | 20.3 | 88.8 | 18.1 | 90.8 | 74.2 | 56.8 | 59.5 | 66.1 | 71.2 | 78.6 | 87.5 | 93.5 | 93.7 | 87.6 | 75.4 | 64.2 | 55.6 | 14.58 | 5.01 | 5.84 | 6.2 | 6.3 | 6.51 | 5.56 | 3.7 | 3.75 | 5.65 | 6.38 | 6.16 | 5.1 | 23 | 8 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 10 | 893 | 256 | 167 | 63 | 18 | 1 | 0 | 0 | 0 | 0 | 6 | 88 | 294 | 8869 | 220 | 270 | 500 | 635 | 888 | 1125 | 1350 | 1356 | 1128 | 787 | 427 | 183 | 4263 | 2 | 14 | 98 | 203 | 424 | 675 | 885 | 891 | 678 | 328 | 63 | 2 | 65067 | 108 | 339 | 1485 | 2737 | 5800 | 10323 | 14530 | 14580 | 10166 | 4057 | 881 | 61 | 41961 | 6 | 68 | 589 | 1324 | 3453 | 6938 | 10238 | 10257 | 6642 | 2164 | 279 | 3 | 7.1 | 5.4 | 6.6 | 7.9 | 9.5 | 9.2 | 8.6 | 7.9 | 7 | 6.5 | 6.3 | 5.5 | 5.2 | 2.4 | 0.4 | 0.3 | 0.2 | 0.1 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.2 | 0.3 | 0.3 | 4.9 | 1.5 | 1.3 | 1 | 0.6 | 0.1 | 0 | 1.1 | 0.5 | 3 | 1.9 | 1.7 | 1.6 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0.5 | 0.4 | 0.3 | 0.2 | 0 | 0 | 0.2 | 0.2 | 0.7 | 0.4 | 0.5 | 0.4 | 80.3 | 86.1 | 93.9 | 99.7 | 107.9 | 113.9 | 115.4 | 114.6 | 110.2 | 101.9 | 90.5 | 79.3 | 56.7 | 58.6 | 61.4 | 64.3 | 67.6 | 70.2 | 73.5 | 73.6 | 71.6 | 68 | 60.7 | 57.7 | 77.1 | 82 | 90.2 | 95.4 | 102.5 | 110 | 112.1 | 111.5 | 107.8 | 98.6 | 86.7 | 75.2 | 55 | 57.6 | 60.4 | 62.5 | 65.9 | 69.7 | 73.3 | 73.4 | 71.2 | 66.9 | 59.6 | 55.3 | 73.9 | 78.6 | 86.5 | 91.5 | 99.7 | 107.4 | 109.3 | 109.1 | 105.4 | 95 | 83.2 | 72.3 | 54 | 56.8 | 59.3 | 61.1 | 65.9 | 68.7 | 72.8 | 73.8 | 70.8 | 64.5 | 59.1 | 53.8 | 71.2 | 74.4 | 82.6 | 88 | 96.4 | 104.3 | 107.4 | 107 | 102.3 | 91.3 | 79.4 | 68.9 | 53.4 | 55 | 58.2 | 60.1 | 64.3 | 67.9 | 72.6 | 73.7 | 71.1 | 63.4 | 57.7 | 52.2 | 61.9 | 63.7 | 65.6 | 67.9 | 73.5 | 78.2 | 81.9 | 84 | 81.8 | 75.1 | 64.9 | 61.3 | 74.2 | 78.6 | 85.1 | 90.8 | 96.6 | 101.4 | 101.5 | 99.9 | 96.4 | 91.1 | 80.9 | 72.8 | 59 | 60.6 | 62.5 | 65 | 69.8 | 75.7 | 80 | 81.4 | 79.5 | 71.4 | 62.3 | 58.6 | 70.5 | 75.1 | 84.4 | 89.4 | 94.2 | 97.7 | 98.4 | 96.4 | 94.5 | 86.9 | 80.5 | 69.7 | 56.9 | 58.3 | 60.8 | 63.1 | 67.6 | 73.4 | 78.6 | 80 | 77.6 | 68.5 | 60.5 | 56.6 | 68.9 | 73.6 | 82.6 | 87.4 | 94.1 | 96.6 | 97.1 | 95.9 | 94 | 87.3 | 79.5 | 67.5 | 54.7 | 56.4 | 59.1 | 61.2 | 65.7 | 71.3 | 77.4 | 78.6 | 75.7 | 65.8 | 58.8 | 54.1 | 67.5 | 71.5 | 80 | 85.1 | 92.2 | 96.4 | 96.4 | 95.6 | 93.6 | 87.4 | 77.4 | 65.5 | 27 | 26.5 | 28.5 | 28.9 | 30.1 | 31.6 | 27.2 | 26.3 | 27.7 | 28.8 | 27.8 | 25.9 | 31.6 | 31.8 | 33.6 | 33.7 | 34.2 | 34.5 | 30.1 | 29.1 | 30.1 | 32.5 | 31.8 | 29.7 | 16.9 | 15.5 | 14.4 | 13.5 | 12.6 | 12.8 | 11.2 | 11.3 | 11.5 | 13.2 | 14.8 | 15.8 | 25.4 | 27 | 31 | 31.3 | 32.6 | 30.9 | 24.2 | 23.5 | 23.8 | 26.7 | 28 | 24.3 | 15.2 | 14.6 | 14.4 | 13.3 | 13 | 13 | 10.4 | 10.5 | 12.6 | 12.6 | 14.1 | 13.8 | 0.291 | 0.295 | 0.313 | 0.33 | 0.348 | 0.349 | 0.393 | 0.388 | 0.351 | 0.321 | 0.295 | 0.291 | 2.514 | 2.523 | 2.457 | 2.411 | 2.379 | 2.38 | 2.365 | 2.372 | 2.437 | 2.49 | 2.531 | 2.54 | 297 | 307 | 307 | 304 | 297 | 295 | 282 | 282 | 290 | 293 | 293 | 291 | 27 | 29 | 34 | 37 | 39 | 39 | 39 | 38 | 34 | 30 | 26 | 25 | 1110 | 1419 | 1882 | 2300 | 2564 | 2675 | 2428 | 2260 | 1991 | 1602 | 1213 | 1004 | 56 | 99 | 68 | 58 | 70 | 93 | 98 | 90 | 71 | 65 | 53 | 54 | 0.94 | N/A | -2.84 | N/A | N/A | N/A | N/A | N/A | 391 | 293 | 0.86 | N/A | -2.32 | 1.06 | N/A | N/A | N/A | -137 | 313 | 164 | 23
4 | USA | CA | DESERT RESORTS | 747187 | 03104 | 33.627 | -116.159 | -118 | 14.76 | -8 | NAP | 94-19 | 2B | 12 | 31.7 | 34.9 | 4.4 | 6.9 | 65.7 | 8.8 | 8.6 | 64.7 | 20.8 | 62 | 18.1 | 62.6 | 3 | 340 | 0.471 | 7 | 29.4 | 112.6 | 72 | 109.7 | 71.5 | 107.8 | 71 | 79.6 | 97.1 | 78.2 | 97 | 77 | 97 | 7.5 | 140 | 74.9 | 130.3 | 88.9 | 72.8 | 121.2 | 89.3 | 70.6 | 112.1 | 90.1 | 42.9 | 96.6 | 41.5 | 96.9 | 40.2 | 96.8 | 88 | 20.6 | 18.3 | 16.2 | 24.7 | 118.7 | 3.9 | 3.1 | 21.9 | 121 | 19.6 | 122.8 | 17.4 | 124.6 | 14.6 | 126.8 | 21.2 | 81.9 | 3.6 | 1.9 | 18.7 | 83.2 | 16.6 | 84.3 | 14.6 | 85.3 | 12 | 86.7 | 73.2 | 55.7 | 58.7 | 66.1 | 71.6 | 79.3 | 86.8 | 92.4 | 91.6 | 85.6 | 74 | 62.3 | 54 | 14.55 | 5.57 | 5.91 | 6.4 | 6.56 | 6.1 | 5.57 | 4.51 | 4.46 | 5.34 | 5.99 | 6.47 | 5.38 | 43 | 15 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 21 | 1038 | 292 | 188 | 66 | 17 | 1 | 0 | 0 | 0 | 0 | 8 | 124 | 342 | 8529 | 191 | 248 | 498 | 648 | 907 | 1103 | 1314 | 1291 | 1067 | 745 | 371 | 146 | 4049 | 3 | 12 | 99 | 215 | 443 | 653 | 849 | 826 | 617 | 288 | 42 | 2 | 65688 | 199 | 436 | 1728 | 3156 | 6285 | 10751 | 14676 | 14097 | 9419 | 3918 | 929 | 94 | 42681 | 28 | 115 | 741 | 1611 | 3765 | 7322 | 10477 | 9942 | 6186 | 2156 | 329 | 9 | 6.5 | 4.7 | 5.5 | 7.1 | 8.7 | 9.1 | 8.2 | 7 | 6.4 | 6.4 | 5.9 | 4.8 | 4.5 | 2.5 | 0.4 | 0.6 | 0.4 | 0 | 0.1 | 0 | 0.1 | 0.2 | 0.2 | 0.1 | 0.2 | 0.2 | 6.6 | 2.4 | 3.4 | 1.7 | 0.5 | 0.8 | 0.4 | 1.1 | 3.6 | 2.4 | 0.5 | 1.7 | 1 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 0.6 | 0.8 | 0.4 | 0.1 | 0.2 | 0.1 | 0.2 | 0.7 | 0.5 | 0.1 | 0.4 | 0.3 | 83.4 | 88.1 | 96.3 | 102.2 | 108.4 | 115.3 | 117.1 | 115.3 | 111.5 | 103.8 | 92.1 | 81 | 55.8 | 58.3 | 61.2 | 64 | 68.8 | 70.9 | 74.9 | 72.4 | 71.2 | 67 | 60.8 | 56.7 | 79.2 | 83.6 | 91.5 | 97.5 | 103.7 | 110.2 | 112.4 | 111.9 | 108 | 99.2 | 88 | 76.5 | 55 | 56.6 | 59.9 | 62.2 | 66.2 | 69.2 | 72.7 | 72.7 | 70.5 | 65.6 | 59.8 | 55.1 | 75.4 | 79.8 | 88.1 | 93.3 | 100 | 107.4 | 109.4 | 109.1 | 105.2 | 95.2 | 83.8 | 72.9 | 53.7 | 55.8 | 58.9 | 60.9 | 65.3 | 68.7 | 72 | 72.5 | 69.9 | 63.6 | 58.5 | 53.1 | 72 | 75.2 | 83.9 | 89.4 | 96.7 | 104.4 | 107.2 | 106.4 | 102.1 | 91.6 | 79.5 | 69.5 | 52.5 | 54.2 | 57.3 | 59.4 | 64.2 | 67.8 | 71.8 | 72.2 | 69.6 | 63 | 57 | 51.6 | 60.3 | 62.3 | 63.7 | 67 | 72.9 | 77 | 80.6 | 81.9 | 80.4 | 72.8 | 64.3 | 60.6 | 74.3 | 79.4 | 87.4 | 96.5 | 102.5 | 103.3 | 99 | 97.9 | 95.2 | 90.2 | 83.3 | 74.9 | 58 | 59.5 | 61.9 | 64.3 | 69.5 | 74.1 | 78.9 | 80.2 | 78 | 69.8 | 61.8 | 58 | 71 | 75.3 | 85.6 | 91.7 | 96.2 | 99.9 | 97.6 | 97.1 | 95.2 | 89.1 | 82.4 | 70.2 | 56.1 | 57.5 | 60.4 | 62.5 | 67.4 | 72.1 | 77.6 | 78.7 | 76.1 | 67.4 | 60 | 55.9 | 70 | 73.9 | 83.4 | 88.6 | 93.4 | 99.4 | 97.6 | 96.8 | 94.4 | 90 | 80.3 | 68 | 54.1 | 55.9 | 58.9 | 60.9 | 65.7 | 70.3 | 76.5 | 77.4 | 74.1 | 65.1 | 58.4 | 53.6 | 68.6 | 72 | 80.5 | 85.7 | 92.4 | 98.1 | 97.6 | 96.8 | 93.6 | 87 | 77 | 65.8 | 31 | 30.5 | 31.3 | 30.6 | 30.1 | 32.9 | 29.4 | 29.5 | 31.8 | 32.7 | 32.8 | 30.5 | 36.7 | 37.5 | 38.2 | 38.2 | 35.7 | 35.9 | 31.8 | 32.2 | 34.9 | 38.8 | 38.1 | 35.1 | 18.2 | 16.8 | 14.7 | 13.6 | 11.4 | 11.8 | 11.3 | 11.6 | 11.9 | 14.5 | 16.9 | 18.1 | 30.8 | 31 | 34 | 34.3 | 33.9 | 34.5 | 26.3 | 26 | 27.6 | 33.1 | 33.7 | 29.1 | 16.2 | 14.9 | 13.7 | 12.8 | 11.5 | 13.1 | 11.1 | 12.3 | 12.7 | 13.9 | 15.7 | 16 | 0.305 | 0.308 | 0.328 | 0.352 | 0.369 | 0.369 | 0.405 | 0.395 | 0.36 | 0.337 | 0.309 | 0.308 | 2.496 | 2.505 | 2.435 | 2.373 | 2.353 | 2.368 | 2.367 | 2.38 | 2.446 | 2.47 | 2.524 | 2.521 | 289 | 300 | 301 | 296 | 291 | 289 | 278 | 280 | 286 | 286 | 286 | 282 | 27 | 30 | 35 | 38 | 40 | 39 | 39 | 38 | 34 | 30 | 26 | 25 | 1063 | 1363 | 1836 | 2247 | 2525 | 2681 | 2443 | 2279 | 1987 | 1564 | 1176 | 962 | 65 | 113 | 81 | 70 | 88 | 97 | 108 | 95 | 72 | 75 | 51 | 57 | 1.19 | N/A | -3.04 | N/A | -0.76 | N/A | N/A | N/A | 387 | 281 | 0.97 | N/A | -2.97 | 1.06 | N/A | N/A | N/A | -149 | 346 | 187 | 38
4 | USA | CA | BLYTHE | 747188 | 23158 | 33.619 | -114.714 | 395 | 14.49 | -8 | NAP | 94-19 | 1B | 12 | 36.9 | 39.7 | -1.3 | 5.2 | 55.6 | 2.9 | 6.5 | 57.6 | 28.1 | 60.4 | 25.4 | 60.8 | 3.9 | 350 | 0.485 | 7 | 25.3 | 113 | 71.5 | 110.8 | 71 | 108.7 | 70.5 | 77.9 | 98.2 | 76.9 | 97.5 | 75.9 | 96.9 | 10.6 | 160 | 73.1 | 124.7 | 85.2 | 71.4 | 117.7 | 86.6 | 69.2 | 108.9 | 89.5 | 41.5 | 97.6 | 40.4 | 96.9 | 39.4 | 96.7 | 84.6 | 24.3 | 20.5 | 18.2 | 30.2 | 117.6 | 2.8 | 2.7 | 28.2 | 119.6 | 26.6 | 121.2 | 25 | 122.7 | 22.9 | 124.7 | 23.9 | 80.1 | 2.9 | 1.6 | 21.8 | 81.2 | 20.1 | 82.2 | 18.4 | 83 | 16.3 | 84.2 | 74.7 | 56.2 | 59.3 | 66.2 | 72.2 | 80.5 | 89.5 | 95.3 | 94.8 | 88.1 | 75.5 | 63.5 | 54.4 | 15.43 | 5.19 | 5.71 | 6.38 | 6.56 | 6.83 | 5.87 | 4.14 | 4.1 | 5.66 | 6.54 | 6.23 | 5.11 | 31 | 11 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 16 | 961 | 276 | 171 | 64 | 15 | 1 | 0 | 0 | 0 | 0 | 6 | 100 | 328 | 9048 | 202 | 264 | 503 | 665 | 945 | 1184 | 1404 | 1388 | 1143 | 790 | 406 | 154 | 4502 | 2 | 12 | 102 | 230 | 480 | 734 | 939 | 923 | 693 | 332 | 54 | 1 | 72798 | 46 | 248 | 1445 | 3239 | 7313 | 12566 | 16492 | 15961 | 10713 | 4076 | 677 | 22 | 48531 | 2 | 36 | 550 | 1603 | 4473 | 8804 | 12105 | 11595 | 7051 | 2116 | 195 | 1 | 7.7 | 6.4 | 7 | 7.5 | 9 | 8.9 | 9.2 | 9.5 | 8.5 | 7.1 | 6.7 | 6.1 | 6.4 | 3.5 | 0.5 | 0.5 | 0.4 | 0.1 | 0 | 0 | 0.2 | 0.6 | 0.4 | 0.2 | 0.2 | 0.3 | 9.2 | 2.3 | 3 | 2.2 | 1 | 0.1 | 0.1 | 1.2 | 2.1 | 2.1 | 1.9 | 0.9 | 2.2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0.6 | 0.7 | 0.6 | 0.2 | 0 | 0 | 0.3 | 0.6 | 0.6 | 0.4 | 0.2 | 0.5 | 78.3 | 84.1 | 94.1 | 100.7 | 109.1 | 115.7 | 116.6 | 114.5 | 110.3 | 102.1 | 89.5 | 76.9 | 54.1 | 56.8 | 59.8 | 62.7 | 67.9 | 69.2 | 73.2 | 72.4 | 70.3 | 66.7 | 58.8 | 55.6 | 74.9 | 80.7 | 89.7 | 96.9 | 104.7 | 111.5 | 113.3 | 112.3 | 107.6 | 97.8 | 85.5 | 72.6 | 52.8 | 55.8 | 58.5 | 61.3 | 65.7 | 68.5 | 71.8 | 72.3 | 70.4 | 65.2 | 58.2 | 53.2 | 71.9 | 77.1 | 86.2 | 93.1 | 101.3 | 108.8 | 110.8 | 109.9 | 105.3 | 94.7 | 81.6 | 69.6 | 51.9 | 54.3 | 57.4 | 60 | 63.8 | 67.6 | 71.8 | 72.1 | 70 | 63.5 | 57.2 | 51.8 | 68.6 | 73.1 | 82.5 | 89.3 | 98 | 106.4 | 108.5 | 107.8 | 102.5 | 91.2 | 77.6 | 66.3 | 50.7 | 53 | 56 | 58.3 | 62.8 | 67.1 | 71.2 | 71.9 | 69.7 | 62.3 | 55.5 | 49.7 | 59.6 | 61.4 | 62.2 | 65 | 70.5 | 75.3 | 78.9 | 79.5 | 78.7 | 73.2 | 63.8 | 59.5 | 70 | 75.7 | 85.5 | 96.1 | 104.6 | 104.4 | 100.6 | 100.1 | 95.6 | 88.8 | 78.4 | 69.9 | 57.1 | 58.9 | 60.3 | 62.6 | 67.6 | 73.2 | 77.4 | 78.1 | 77 | 69.4 | 60.5 | 57 | 66.6 | 72.2 | 82.9 | 91.8 | 100.1 | 102.8 | 99.1 | 98.7 | 94.1 | 88.5 | 78.1 | 66.6 | 55 | 56.8 | 58.9 | 61 | 65.5 | 71.2 | 76.4 | 77.2 | 75.6 | 67.2 | 58.7 | 54.7 | 65.7 | 70.2 | 81.6 | 89.5 | 96.9 | 100.8 | 98.4 | 97.9 | 93.1 | 87.3 | 77.8 | 64.7 | 52.7 | 54.9 | 57.3 | 59.4 | 63.8 | 69.1 | 75.3 | 76.2 | 74.3 | 64.6 | 56.9 | 52.3 | 64.3 | 69.2 | 79.1 | 86.5 | 94.6 | 101.3 | 97.9 | 97.4 | 92.7 | 86.1 | 75.7 | 62.6 | 24.1 | 24.8 | 27.2 | 28.1 | 28.8 | 30.2 | 25.3 | 24.6 | 26.1 | 27.3 | 26.2 | 23.3 | 28.2 | 30.1 | 32.5 | 33.5 | 32.5 | 32.4 | 28 | 27.1 | 28.6 | 30.8 | 30.8 | 26.9 | 14.9 | 14.6 | 13.7 | 14.1 | 12.8 | 11.9 | 9.7 | 9.6 | 11.1 | 13.4 | 15.3 | 14.8 | 22.1 | 24.8 | 29.5 | 31.1 | 30.1 | 28 | 21.8 | 21.8 | 22 | 25 | 27 | 22.4 | 12.3 | 12.4 | 12.5 | 13.1 | 12.2 | 11.4 | 8.1 | 8.4 | 9.6 | 11.6 | 14.4 | 12.7 | 0.279 | 0.282 | 0.298 | 0.322 | 0.335 | 0.338 | 0.383 | 0.377 | 0.341 | 0.307 | 0.285 | 0.28 | 2.572 | 2.586 | 2.511 | 2.431 | 2.415 | 2.417 | 2.399 | 2.406 | 2.477 | 2.536 | 2.576 | 2.585 | 301 | 311 | 312 | 306 | 301 | 298 | 284 | 285 | 293 | 297 | 296 | 295 | 25 | 27 | 32 | 36 | 37 | 37 | 38 | 37 | 33 | 28 | 24 | 23 | 1086 | 1404 | 1871 | 2298 | 2574 | 2684 | 2410 | 2238 | 1975 | 1574 | 1192 | 980 | 57 | 97 | 66 | 63 | 64 | 88 | 93 | 88 | 66 | 64 | 51 | 56 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.68 | N/A | -3.24 | N/A | -0.72 | N/A | N/A | N/A | 277 | 173 | 13
|  |  |  | 97 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92

## ForCSVExport
; | CEC Tilte 24 Compliance Ruleset - 2022 Standards
; | Design Day Look-up Table
; | Last Modified | 2022-08-31 | NK
;
; | Source Data:
; |  | 1 | ASHRAE Handbook --- Fundamentals 2021
; |  |  | For use with 2022 CA weather files
; |  |  | Note: Units in IP. Convert to SI for use in EnergyPlus
;
; |  | # | CA Climate Zone Lookup - https://caenergy.maps.arcgis.com/apps/webappviewer/index.html?id=5cfefd9798214bea91cc4fddaa7e643f
;
;
;
;
; | Other cell color coding |  | Columns added for CA climate zone reference
; |  |  | Data not available for stations - excluded from lookup table
; |  |  | Data populated for stations from 2022.1.0
; |  | # | CA Climate Zone Number Added for new stations
;
; | Mod History | 8/24/2022 - CB created intial table with header, Corrected header for MWBR columns and cell T5 correction
; |  | 8/29/2022 - NK Added missing headers, added Weather_FileName and CA_Climate_Zone Columns, Commented out missing stations
; |  | 8/31/2022- NK Added comments for source data and color coding. Added missing Climate zone number for new stations added for 2022 analysis
; |  | 9/25/2022 - NK Added data for Torrance and San Jose-Reid Hill stations based on 2022.1.0 ddy files
;
;
;
;
;
;
;
; |  |  | Station Information | [13 empty] | Annual Heating and Humidification Design Conditions | [15 empty] | Annual Cooling, Dehumidification, and Enthalpy Design Conditions | [31 empty] | Extreme Annual Design Conditions | [26 empty] | Temperatures, Degree-Days, and Degree-Hours | [103 empty] | Wind Speed | [12 empty] | Precipitation | [51 empty] | Monthly Design Dry Bulb and Mean Coincident Wet Bulb Temperatures | [95 empty] | Monthly Design Wet Bulb and Mean Coincident Dry Bulb Temperatures | [95 empty] | Mean Daily Temperature Range | [59 empty] | Clear-Sky Solar Irradiance | [47 empty] | All-Sky Solar Radiation | [23 empty] | Historical Trends
; |  |  | Region | Country | Prov State | Station Name | WMO | WBAN | Lat | Lon | Elev | StdP | TZ Offset | TZ Code | Period | Climate Zone | Coldest Month | Heating DB |  | Humidification DP/MCDB and HR | [5 empty] | Coldest Month WS/MCDB |  |  |  | MCWS/PCWD to 99.6% DB |  | Wind Shelter Factor | Hottest Month | Hottest Month DB Range | Cooling DB/MCWB | [5 empty] | Evaporation WB/MCDB | [5 empty] | MCWS/PCWD to 0.4% DB |  | Dehumidification DP/MCDB and HR | [8 empty] | Enthalpy/MCDB | [5 empty] | Extreme Max WB | Extreme Annual WS |  |  | Extreme Annual DB |  |  |  | n-Year Return Period Values of Extreme DB | [7 empty] | Extreme Annual WB |  |  |  | n-Year Return Period Values of Extreme WB | [7 empty] | Average Daily Temperature | [12 empty] | Standard Deviation of Average Daily Temperature | [12 empty] | Heating Degree Days 50°F (HDD50) | [12 empty] | Heating Degree Days 65°F (HDD65) | [12 empty] | Cooling Degree Days 50°F (CDD50) | [12 empty] | Cooling Degree Days 65°F (CDD65) | [12 empty] | Cooling Degree Hours 74°F (CDH74) | [12 empty] | Cooling Degree Hours 80°F (CDH80) | [12 empty] | Average Wind Speed | [12 empty] | Average Precipitation | [12 empty] | Maximum Precipitation | [12 empty] | Minimum Precipitation | [12 empty] | Standard Deviation of Precipitation | [12 empty] | 0.4% Monthly Design Dry Bulb Temperature | [11 empty] | Mean Wet Bulb Coincident with 0.4% Monthly Design Dry Bulb Temperature | [11 empty] | 2% Monthly Design Dry Bulb Temperature | [11 empty] | Mean Wet Bulb Coincident with 2% Monthly Design Dry Bulb Temperature | [11 empty] | 5% Monthly Design Dry Bulb Temperature | [11 empty] | Mean Wet Bulb Coincident with 5% Monthly Design Dry Bulb Temperature | [11 empty] | 10% Monthly Design Dry Bulb Temperature | [11 empty] | Mean Wet Bulb Coincident with 10% Monthly Design Dry Bulb Temperature | [11 empty] | 0.4% Monthly Design Wet Bulb Temperature | [11 empty] | Mean Dry Bulb Coincident with 0.4% Monthly Design Wet Bulb Temperature | [11 empty] | 2% Monthly Design Wet Bulb Temperature | [11 empty] | Mean Dry Bulb Coincident with 2% Monthly Design Wet Bulb Temperature | [11 empty] | 5% Monthly Design Wet Bulb Temperature | [11 empty] | Mean Dry Bulb Coincident with 5% Monthly Design Wet Bulb Temperature | [11 empty] | 10% Monthly Design Wet Bulb Temperature | [11 empty] | Mean Dry Bulb Coincident with 10% Monthly Design Wet Bulb Temperature | [11 empty] | Mean Daily Dry Bulb Temperature Range | [11 empty] | Mean Daily Dry Bulb Temperature Range Coincident with 5% Design Dry Bulb Temperature | [11 empty] | Mean Daily Wet Bulb Temperature Range Coincident with 5% Design Dry Bulb Temperature | [11 empty] | Mean Daily Dry Bulb Temperature Range Coincident with 5% Design Wet Bulb Temperature | [11 empty] | Mean Daily Wet Bulb Temperature Range Coincident with 5% Design Wet Bulb Temperature | [11 empty] | Clear-Sky Optical Depth for Beam Irradiance (taub) | [11 empty] | Clear-Sky Optical Depth for Diffuse Irradiance (taud) | [11 empty] | Clear-Sky Noon Beam Normal Irradiance on 21st Day | [11 empty] | Clear-Sky Noon Diffuse Horizontal Irradiance on 21st Day | [11 empty] | All-Sky Average Monthly Global Horizontal Radiation | [11 empty] | All-Sky Standard Deviation of Monthly Global Horizontal Radiation | [11 empty] | Station Only | [9 empty] | Regional
; | [19 empty] | 99.6% |  |  | 99.0% |  |  | 0.4% |  | 1% | [6 empty] | 0.4% |  | 1% |  | 2% |  | 0.4% |  | 1% |  | 2% |  |  |  | 0.4% |  |  | 1% |  |  | 2% |  |  | 0.4% |  | 1% |  | 2% | [5 empty] | Mean |  | Standard Deviation |  | n=5 years |  | n=10 years |  | n=20 years |  | n=50 years |  | Mean |  | Standard Deviation |  | n=5 years |  | n=10 years |  | n=20 years |  | n=50 years | [494 empty] | DBAvg | Heating |  | Cooling |  |  | Degree-Days |  |  |  | DBAvg | Heating |  | Cooling |  |  | Degree-Days |  |  |  | Neighbors
; | [17 empty] | 99.6% | 99.0% | DP | HR | MCDB | DP | HR | MCDB | WS | MCDB | WS | MCDB | MCWS | PCWD |  |  |  | DB | MCWB | DB | MCWB | DB | MCWB | WB | MCDB | WB | MCDB | WB | MCDB | MCWS | PCWD | DP | HR | MCDB | DP | HR | MCDB | DP | HR | MCDB | Enth | MCDB | Enth | MCDB | Enth | MCDB |  | 1% | 2.5% | 5% | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Min | Max | Annual | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Annual | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Annual | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Annual | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Annual | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Annual | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Annual | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Annual | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Annual | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Annual | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Annual | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Annual | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Annual | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec |  | 99% DB | 99% DP | 1% DB | 1% WB | 1% DP | HDD50 | HDD65 | CDD60 | CDD65 |  | 99% DB | 99% DP | 1% DB | 1% WB | 1% DP | HDD50 | HDD65 | CDD60 | CDD65
TABLE WeatherCliZnDsgnDay2022
| Weather_FileName | CA_Climate_Zone | Region | Country | Prov_State | Station_Name | WMO | WBAN | Lat | Lon | Elev | StdP | TZ_Offset | TZ_Code | Period | Climate_Zone | Coldest_Month | DB996 | DB990 | DP996 | HR_DP996 | MCDB_DP996 | DP990 | HR_DP996 | MCDB_DP990 | WS004 | MCDB_WS004 | WS010 | MCDB_WS010 | MCWS_DB996 | PCWC_DB996 | WSF | Hottest_Month | MDBR_HM | DB004 | MCWB_DB004 | DB010 | MCWB_DB010 | DB020 | MCWB_DB020 | WB004 | MCDB_WB004 | WB010 | MCDB_WB010 | WB020 | MCDB_WB020 | MCWS_DB004 | PCWD_DB004 | DP004 | HR_DP004 | MCDB_DP004 | DP010 | HR_DP010 | MCDB_DP010 | DP020 | HR_DP020 | MCDB_DP020 | Enth004 | MCDB_Enth004 | Enth010 | MCDB_Enth010 | Enth020 | MCDB_Enth020 | WBExtMax | WSExt010 | WSExt025 | WSExt_050 | DBMeanMin | DBMeanMax | DBStdDevMeanMin | DBStdDevMeanMax | DB5yrMin | DB5yrMax | DB10yrMin | DB10yrMax | DB20yrMin | DB20yrMax | DB50yrMin | DB50yrMax | WBMeanMin | WBStdDevMeanMax | WBStdDevMeanMin | WBMeanMax | WB5yrMin | WB5yrMax | WB10yrMin | WB10yrMax | WB20yrMin | WB20yrMax | WB50yrMin | WB50yrMax | DBAvg_Yr | DBAvg_Jan | DBAvg_Feb | DBAvg_Mar | DBAvg_Apr | DBAvg_May | DBAvg_Jun | DBAvg_Jul | DBAvg_Aug | DBAvg_Sep | DBAvg_Oct | DBAvg_Nov | DBAvg_Dec | DBStdDev_Yr | DBStdDev_Jan | DBStdDev_Feb | DBStdDev_Mar | DBStdDev_Apr | DBStdDev_May | DBStdDev_Jun | DBStdDev_Jul | DBStdDev_Aug | DBStdDev_Sep | DBStdDev_Oct | DBStdDev_Nov | DBStdDev_Dec | HDD50_Yr | HDD50_Jan | HDD50_Feb | HDD50_Mar | HDD50_Apr | HDD50_May | HDD50_Jun | HDD50_Jul | HDD50_Aug | HDD50_Sep | HDD50_Oct | HDD50_Nov | HDD50_Dec | HDD65_Yr | HDD65_Jan | HDD65_Feb | HDD65_Mar | HDD65_Apr | HDD65_May | HDD65_Jun | HDD65_Jul | HDD65_Aug | HDD65_Sep | HDD65_Oct | HDD65_Nov | HDD65_Dec | CDD50_Yr | CDD50_Jan | CDD50_Feb | CDD50_Mar | CDD50_Apr | CDD50_May | CDD50_Jun | CDD50_Jul | CDD50_Aug | CDD50_Sep | CDD50_Oct | CDD50_Nov | CDD50_Dec | CDD65_Yr | CDD65_Jan | CDD65_Feb | CDD65_Mar | CDD65_Apr | CDD65_May | CDD65_Jun | CDD65_Jul | CDD65_Aug | CDD65_Sep | CDD65_Oct | CDD65_Nov | CDD65_Dec | CDD74_Yr | CDD74_Jan | CDD74_Feb | CDD74_Mar | CDD74_Apr | CDD74_May | CDD74_Jun | CDD74_Jul | CDD74_Aug | CDD74_Sep | CDD74_Oct | CDD74_Nov | CDD74_Dec | CDH80_Yr | CDH80_Jan | CDH80_Feb | CDH80_Mar | CDH80_Apr | CDH80_May | CDH80_Jun | CDH80_Jul | CDH80_Aug | CDH80_Sep | CDH80_Oct | CDH80_Nov | CDH80_Dec | WSAvg_Yr | WSAvg_Jan | WSAvg_Feb | WSAvg_Mar | WSAvg_Apr | WSAvg_May | WSAvg_Jun | WSAvg_Jul | WSAvg_Aug | WSAvg_Sep | WSAvg_Oct | WSAvg_Nov | WSAvg_Dec | PrecipAvg_Yr | PrecipAvg_Jan | PrecipAvg_Feb | PrecipAvg_Mar | PrecipAvg_Apr | PrecipAvg_May | PrecipAvg_Jun | PrecipAvg_Jul | PrecipAvg_Aug | PrecipAvg_Sep | PrecipAvg_Oct | PrecipAvg_Nov | PrecipAvg_Dec | PrecipMax_Yr | PrecipMax_Jan | PrecipMax_Feb | PrecipMax_Mar | PrecipMax_Apr | PrecipMax_May | PrecipMax_Jun | PrecipMax_Jul | PrecipMax_Aug | PrecipMax_Sep | PrecipMax_Oct | PrecipMax_Nov | PrecipMax_Dec | PrecipMin_Yr | PrecipMin_Jan | PrecipMin_Feb | PrecipMin_Mar | PrecipMin_Apr | PrecipMin_May | PrecipMin_Jun | PrecipMin_Jul | PrecipMin_Aug | PrecipMin_Sep | PrecipMin_Oct | PrecipMin_Nov | PrecipMin_Dec | PrecipStdDev_Yr | PrecipStdDev_Jan | PrecipStdDev_Feb | PrecipStdDev_Mar | PrecipStdDev_Apr | PrecipStdDev_May | PrecipStdDev_Jun | PrecipStdDev_Jul | PrecipStdDev_Aug | PrecipStdDev_Sep | PrecipStdDev_Oct | PrecipStdDev_Nov | PrecipStdDev_Dec | DB004_Jan | DB004_Feb | DB004_Mar | DB004_Apr | DB004_May | DB004_Jun | DB004_Jul | DB004_Aug | DB004_Sep | DB004_Oct | DB004_Nov | DB004_Dec | MCWB_DB004_Jan | MCWB_DB004_Feb | MCWB_DB004_Mar | MCWB_DB004_Apr | MCWB_DB004_May | MCWB_DB004_Jun | MCWB_DB004_Jul | MCWB_DB004_Aug | MCWB_DB004_Sep | MCWB_DB004_Oct | MCWB_DB004_Nov | MCWB_DB004_Dec | DB020_Jan | DB020_Feb | DB020_Mar | DB020_Apr | DB020_May | DB020_Jun | DB020_Jul | DB020_Aug | DB020_Sep | DB020_Oct | DB020_Nov | DB020_Dec | MCWB_DB020_Jan | MCWB_DB020_Feb | MCWB_DB020_Mar | MCWB_DB020_Apr | MCWB_DB020_May | MCWB_DB020_Jun | MCWB_DB020_Jul | MCWB_DB020_Aug | MCWB_DB020_Sep | MCWB_DB020_Oct | MCWB_DB020_Nov | MCWB_DB020_Dec | DB050_Jan | DB050_Feb | DB050_Mar | DB050_Apr | DB050_May | DB050_Jun | DB050_Jul | DB050_Aug | DB050_Sep | DB050_Oct | DB050_Nov | DB050_Dec | MCWB_DB050_Jan | MCWB_DB050_Feb | MCWB_DB050_Mar | MCWB_DB050_Apr | MCWB_DB050_May | MCWB_DB050_Jun | MCWB_DB050_Jul | MCWB_DB050_Aug | MCWB_DB050_Sep | MCWB_DB050_Oct | MCWB_DB050_Nov | MCWB_DB050_Dec | DB100_Jan | DB100_Feb | DB100_Mar | DB100_Apr | DB100_May | DB100_Jun | DB100_Jul | DB100_Aug | DB100_Sep | DB100_Oct | DB100_Nov | DB100_Dec | MCWB_DB100_Jan | MCWB_DB100_Feb | MCWB_DB100_Mar | MCWB_DB100_Apr | MCWB_DB100_May | MCWB_DB100_Jun | MCWB_DB100_Jul | MCWB_DB100_Aug | MCWB_DB100_Sep | MCWB_DB100_Oct | MCWB_DB100_Nov | MCWB_DB100_Dec | WB004_Jan | WB004_Feb | WB004_Mar | WB004_Apr | WB004_May | WB004_Jun | WB004_Jul | WB004_Aug | WB004_Sep | WB004_Oct | WB004_Nov | WB004_Dec | MCDB_WB004_Jan | MCDB_WB004_Feb | MCDB_WB004_Mar | MCDB_WB004_Apr | MCDB_WB004_May | MCDB_WB004_Jun | MCDB_WB004_Jul | MCDB_WB004_Aug | MCDB_WB004_Sep | MCDB_WB004_Oct | MCDB_WB004_Nov | MCDB_WB004_Dec | WB020_Jan | WB020_Feb | WB020_Mar | WB020_Apr | WB020_May | WB020_Jun | WB020_Jul | WB020_Aug | WB020_Sep | WB020_Oct | WB020_Nov | WB020_Dec | MCDB_WB020_Jan | MCDB_WB020_Feb | MCDB_WB020_Mar | MCDB_WB020_Apr | MCDB_WB020_May | MCDB_WB020_Jun | MCDB_WB020_Jul | MCDB_WB020_Aug | MCDB_WB020_Sep | MCDB_WB020_Oct | MCDB_WB020_Nov | MCDB_WB020_Dec | WB050_Jan | WB050_Feb | WB050_Mar | WB050_Apr | WB050_May | WB050_Jun | WB050_Jul | WB050_Aug | WB050_Sep | WB050_Oct | WB050_Nov | WB050_Dec | MCDB_WB050_Jan | MCDB_WB050_Feb | MCDB_WB050_Mar | MCDB_WB050_Apr | MCDB_WB050_May | MCDB_WB050_Jun | MCDB_WB050_Jul | MCDB_WB050_Aug | MCDB_WB050_Sep | MCDB_WB050_Oct | MCDB_WB050_Nov | MCDB_WB050_Dec | WB100_Jan | WB100_Feb | WB100_Mar | WB100_Apr | WB100_May | WB100_Jun | WB100_Jul | WB100_Aug | WB100_Sep | WB100_Oct | WB100_Nov | WB100_Dec | MCDB_WB100_Jan | MCDB_WB100_Feb | MCDB_WB100_Mar | MCDB_WB100_Apr | MCDB_WB100_May | MCDB_WB100_Jun | MCDB_WB100_Jul | MCDB_WB100_Aug | MCDB_WB100_Sep | MCDB_WB100_Oct | MCDB_WB100_Nov | MCDB_WB100_Dec | MDBR_Jan | MDBR_Feb | MDBR_Mar | MDBR_Apr | MDBR_May | MDBR_Jun | MDBR_Jul | MDBR_Aug | MDBR_Sep | MDBR_Oct | MDBR_Nov | MDBR_Dec | MDBR_DB050_Jan | MDBR_DB050_Feb | MDBR_DB050_Mar | MDBR_DB050_Apr | MDBR_DB050_May | MDBR_DB050_Jun | MDBR_DB050_Jul | MDBR_DB050_Aug | MDBR_DB050_Sep | MDBR_DB050_Oct | MDBR_DB050_Nov | MDBR_DB050_Dec | MWBR_DB050_Jan | MWBR_DB050_Feb | MWBR_DB050_Mar | MWBR_DB050_Apr | MWBR_DB050_May | MWBR_DB050_Jun | MWBR_DB050_Jul | MWBR_DB050_Aug | MWBR_DB050_Sep | MWBR_DB050_Oct | MWBR_DB050_Nov | MWBR_DB050_Dec | MCDB_WB050_Jan | MCDB_WB050_Feb | MCDB_WB050_Mar | MCDB_WB050_Apr | MCDB_WB050_May | MCDB_WB050_Jun | MCDB_WB050_Jul | MCDB_WB050_Aug | MCDB_WB050_Sep | MCDB_WB050_Oct | MCDB_WB050_Nov | MCDB_WB050_Dec | MWBR_WB050_Jan | MWBR_WB050_Feb | MWBR_WB050_Mar | MWBR_WB050_Apr | MWBR_WB050_May | MWBR_WB050_Jun | MWBR_WB050_Jul | MWBR_WB050_Aug | MWBR_WB050_Sep | MWBR_WB050_Oct | MWBR_WB050_Nov | MWBR_WB050_Dec | Taub_Jan | Taub_Feb | Taub_Mar | Taub_Apr | Taub_May | Taub_Jun | Taub_Jul | Taub_Aug | Taub_Sep | Taub_Oct | Taub_Nov | Taub_Dec | Taud_Jan | Taud_Feb | Taud_Mar | Taud_Apr | Taud_May | Taud_Jun | Taud_Jul | Taud_Aug | Taud_Sep | Taud_Oct | Taud_Nov | Taud_Dec | DNINoon_Jan | DNINoon_Feb | DNINoon_Mar | DNINoon_Apr | DNINoon_May | DNINoon_Jun | DNINoon_Jul | DNINoon_Aug | DNINoon_Sep | DNINoon_Oct | DNINoon_Nov | DNINoon_Dec | DHINoon_Jan | DHINoon_Feb | DHINoon_Mar | DHINoon_Apr | DHINoon_May | DHINoon_Jun | DHINoon_Jul | DHINoon_Aug | DHINoon_Sep | DHINoon_Oct | DHINoon_Nov | DHINoon_Dec | GHRAvg_Jan | GHRAvg_Feb | GHRAvg_Mar | GHRAvg_Apr | GHRAvg_May | GHRAvg_Jun | GHRAvg_Jul | GHRAvg_Aug | GHRAvg_Sep | GHRAvg_Oct | GHRAvg_Nov | GHRAvg_Dec | GHRStdDev_Jan | GHRStdDev_Feb | GHRStdDev_Mar | GHRStdDev_Apr | GHRStdDev_May | GHRStdDev_Jun | GHRStdDev_Jul | GHRStdDev_Aug | GHRStdDev_Sep | GHRStdDev_Oct | GHRStdDev_Nov | GHRStdDev_Dec | StDBAvg | StHtgDB990 | StHtgDP990 | StClgDB010 | StClgWB010 | StClgDP010 | StHDD50 | StHDD65 | StCDD60 | StCDD65 | RegDBAvg | RegHtgDB990 | RegHtgDP990 | RegClgDB010 | RegClgWB010 | RegClgDP010 | RegHDD50 | RegHDD65 | RegCDD60 | RegCDD65 | Neighbors
| AUBURN_STYP20 | 11 | 4 | USA | CA | AUBURN | 720267 | 23224 | 38.955 | -121.082 | 1531 | 13.9 | -8 | NAP | 04-19 | 3A | 12 | 32 | 34.1 | 15.8 | 13 | 48.7 | 19.1 | 15.2 | 47 | 19.7 | 47.4 | 17.7 | 48.6 | 2.5 | 100 | 0.422 | 7 | 24.5 | 98.8 | 66.9 | 95 | 65.2 | 92.5 | 64.6 | 69.3 | 92.1 | 67.9 | 89.8 | 66.4 | 87.8 | 6.1 | 260 | 61.5 | 86.2 | 76.9 | 59.4 | 80 | 76.4 | 57.2 | 73.9 | 73.4 | 34.2 | 91.6 | 32.9 | 90.1 | 31.7 | 87.7 | 82 | 15.6 | 12.6 | 11 | 27.2 | 103.9 | 3.5 | 6.4 | 24.6 | 108.5 | 22.6 | 112.2 | 20.6 | 115.8 | 18 | 120.4 | 25.3 | 72.4 | 2.9 | 3.4 | 23.1 | 74.8 | 21.4 | 76.7 | 19.8 | 78.6 | 17.6 | 81.1 | 61 | 47.3 | 49 | 52.4 | 55.8 | 63.1 | 71.8 | 78.8 | 77.6 | 72.9 | 62.7 | 53.3 | 46.1 | 13.19 | 5.45 | 6.23 | 6.49 | 7.24 | 7.39 | 7.81 | 5.66 | 5.4 | 7.39 | 6.9 | 6.42 | 5.08 | 456 | 117 | 86 | 49 | 22 | 2 | 0 | 0 | 0 | 0 | 1 | 37 | 142 | 2916 | 547 | 449 | 393 | 291 | 125 | 26 | 0 | 0 | 19 | 126 | 353 | 587 | 4462 | 35 | 58 | 123 | 195 | 408 | 655 | 892 | 857 | 687 | 396 | 136 | 20 | 1447 | 0 | 0 | 2 | 15 | 67 | 231 | 427 | 392 | 256 | 55 | 2 | 0 | 16844 | 1 | 7 | 16 | 139 | 751 | 2843 | 5287 | 4567 | 2705 | 508 | 20 | 0 | 8098 | 0 | 1 | 1 | 20 | 226 | 1317 | 2813 | 2318 | 1274 | 127 | 1 | 0 | 5 | 4.2 | 5.4 | 5.7 | 5.7 | 5.5 | 5.2 | 5.3 | 5 | 4.9 | 4.3 | 4 | 4.3 | 35.4 | 6.2 | 5.2 | 5.7 | 2.7 | 0.7 | 0.3 | 0 | 0.2 | 0.7 | 2.3 | 5.9 | 5.4 | 64.9 | 17 | 17.6 | 15.3 | 7.7 | 2.8 | 1.1 | 0.9 | 1.6 | 3.7 | 13.9 | 13.5 | 14.2 | 11.8 | 0.5 | 0.3 | 1.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7 | 0 | 11.9 | 4.3 | 4.1 | 3.6 | 2.3 | 0.7 | 0.3 | 0.2 | 0.4 | 1.1 | 2.8 | 3.8 | 3.7 | 69.8 | 71.9 | 75.4 | 82.2 | 90.6 | 99.8 | 102.1 | 100.1 | 98.8 | 89.8 | 77 | 64.2 | 51.3 | 56.1 | 58.7 | 62.8 | 65.9 | 68.4 | 69.6 | 66.1 | 65.1 | 61.6 | 57.8 | 49.8 | 64 | 66.5 | 72.1 | 78.9 | 84.5 | 95.4 | 98.8 | 97.1 | 93.1 | 82.4 | 72.8 | 61.1 | 49.9 | 53.6 | 56.7 | 60.8 | 62.9 | 66.6 | 67.5 | 65 | 62.8 | 59.2 | 56 | 49.6 | 61.2 | 63.6 | 68.3 | 73.1 | 81.8 | 91 | 95.2 | 93.1 | 90.7 | 79.5 | 69.8 | 57.1 | 49.5 | 51.2 | 54.8 | 57.6 | 61.2 | 64.6 | 65.6 | 64.6 | 62.5 | 57.3 | 54.6 | 48.7 | 56.7 | 60.6 | 64 | 69.8 | 78.7 | 88.1 | 91.5 | 90.7 | 88.2 | 75.3 | 63.8 | 54.7 | 48.3 | 50 | 52.5 | 56.5 | 59.9 | 63.4 | 65.1 | 63.7 | 61.9 | 56.4 | 52.3 | 48.8 | 55.4 | 58 | 60.3 | 65.3 | 67.8 | 71.8 | 72.8 | 68.8 | 67 | 64.2 | 62.4 | 56.7 | 59.9 | 63.6 | 72.9 | 79.4 | 85.7 | 94.4 | 97.8 | 93.3 | 86.1 | 78.6 | 72.4 | 58.3 | 53.7 | 55.5 | 57.8 | 62.1 | 65.3 | 69.2 | 69.5 | 67.4 | 65.2 | 62 | 58.8 | 54.3 | 58.6 | 63.9 | 68.8 | 75.6 | 83.3 | 89.9 | 93.7 | 91.3 | 88.1 | 78.8 | 67.6 | 55.8 | 51.9 | 53.5 | 55.7 | 59.3 | 63 | 67.1 | 68.2 | 66.1 | 63.8 | 60.1 | 56.4 | 52.4 | 56.2 | 59.8 | 65.1 | 71.1 | 77.9 | 87 | 91.4 | 89.8 | 87 | 74.5 | 64.4 | 54.3 | 50.1 | 51.8 | 53.8 | 57.1 | 61 | 65.2 | 66.6 | 64.9 | 62.3 | 58.2 | 54.3 | 50.1 | 55.8 | 57.4 | 62 | 67.4 | 75.3 | 83.4 | 88.7 | 87.8 | 84.8 | 71 | 61.2 | 54.1 | 15.5 | 16.1 | 16.6 | 18.4 | 21 | 24.1 | 24.5 | 24.3 | 23.2 | 20.4 | 17.1 | 15.1 | 22 | 22.3 | 21.8 | 22.8 | 24.6 | 26.9 | 25.7 | 25 | 24.9 | 24 | 22.9 | 19 | 13.1 | 14 | 13.3 | 13.4 | 12 | 11 | 10.1 | 10.4 | 11.2 | 11.3 | 12.3 | 11.6 | 17.4 | 18.6 | 19.3 | 20.9 | 23 | 24.8 | 24.2 | 24 | 23.7 | 20.5 | 19.3 | 12.3 | 11.8 | 12.5 | 12.3 | 12.9 | 11.7 | 10.8 | 9.9 | 10.3 | 10.9 | 10.5 | 11.7 | 9.2 | 0.309 | 0.31 | 0.338 | 0.342 | 0.357 | 0.349 | 0.348 | 0.332 | 0.341 | 0.332 | 0.31 | 0.323 | 2.514 | 2.525 | 2.433 | 2.424 | 2.404 | 2.441 | 2.443 | 2.478 | 2.459 | 2.483 | 2.525 | 2.45 | 276 | 292 | 292 | 296 | 292 | 293 | 293 | 296 | 287 | 279 | 273 | 259 | 24 | 27 | 33 | 36 | 37 | 36 | 36 | 33 | 32 | 28 | 24 | 24 | 702 | 997 | 1417 | 1881 | 2300 | 2622 | 2616 | 2347 | 1892 | 1327 | 843 | 613 | 119 | 138 | 167 | 181 | 165 | 121 | 91 | 81 | 72 | 96 | 67 | 105 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.72 | N/A | -1.96 | N/A | N/A | N/A | N/A | -205 | 248 | 76 | 41
| EL-CENTRO-NAF_STYP20 | 15 | 4 | USA | CA | EL CENTRO NAF | 722810 | 23199 | 32.817 | -115.683 | -42 | 14.72 | -8 | NAP | 06-19 | 2B | 12 | 35.5 | 38.5 | 3.6 | 6.6 | 57.7 | 7.8 | 8.2 | 61 | 31.5 | 62.4 | 27.2 | 64.4 | 5 | 260 | 0.487 | 8 | 27.1 | 111.9 | 70.7 | 109.6 | 70.5 | 107.6 | 70.3 | 78.9 | 95.1 | 77.8 | 94.9 | 76.8 | 94.8 | 7 | 140 | 75.1 | 131.7 | 86.4 | 73.3 | 123.7 | 86.7 | 71.2 | 114.9 | 88 | 42.3 | 94.6 | 41.2 | 94.4 | 40 | 94.9 | 82.9 | 29.3 | 25.9 | 22.3 | 30.1 | 117 | 3.6 | 1.8 | 27.5 | 118.3 | 25.4 | 119.3 | 23.4 | 120.3 | 20.8 | 121.6 | 24.6 | 81.1 | 2.9 | 1.2 | 22.5 | 81.9 | 20.8 | 82.6 | 19.2 | 83.3 | 17.1 | 84.2 | 74.5 | 56.7 | 60.5 | 67.2 | 72.5 | 78.1 | 87.5 | 93.2 | 93.4 | 87.5 | 75.8 | 65.2 | 55.4 | 14.28 | 5.47 | 5.7 | 6.19 | 6.06 | 6.26 | 5.2 | 3.48 | 3.64 | 5.76 | 5.72 | 6.11 | 5.08 | 29 | 14 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 11 | 842 | 260 | 143 | 50 | 10 | 1 | 0 | 0 | 0 | 0 | 4 | 74 | 300 | 8962 | 221 | 297 | 533 | 675 | 870 | 1124 | 1340 | 1345 | 1125 | 798 | 456 | 178 | 4302 | 2 | 17 | 119 | 235 | 406 | 674 | 875 | 880 | 675 | 338 | 79 | 2 | 66996 | 136 | 473 | 1770 | 3190 | 5695 | 10746 | 14658 | 14686 | 10258 | 4211 | 1106 | 67 | 43102 | 8 | 101 | 712 | 1563 | 3328 | 7302 | 10350 | 10387 | 6725 | 2226 | 398 | 2 | 7.9 | 5.9 | 7.6 | 8.9 | 10.8 | 11 | 9.1 | 7.7 | 6.9 | 7.1 | 7.4 | 6.4 | 6.3 | 2.5 | 0.5 | 0.5 | 0.3 | 0.1 | 0 | 0 | 0.1 | 0.2 | 0.2 | 0.2 | 0.2 | 0.4 | 5.9 | 3.5 | 2.5 | 1.9 | 0.6 | 0.6 | 0.2 | 0.9 | 0.9 | 1.4 | 1.1 | 1 | 1.3 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 0.8 | 0.6 | 0.4 | 0.1 | 0.1 | 0 | 0.2 | 0.3 | 0.3 | 0.4 | 0.3 | 0.4 | 80.8 | 86.6 | 94.5 | 100.4 | 106.8 | 115.3 | 114.3 | 114.1 | 110.6 | 101.6 | 91.4 | 79.4 | 54.4 | 57.5 | 60.4 | 62.9 | 64.7 | 68.3 | 70.8 | 71 | 69.9 | 65 | 60.7 | 57.2 | 77.8 | 83.1 | 90.7 | 96.1 | 102.4 | 110.7 | 111.3 | 111.6 | 107.6 | 97.4 | 88.4 | 75.8 | 53.7 | 56.6 | 59.4 | 61.7 | 64 | 68 | 71.6 | 71.3 | 69.5 | 63.6 | 59.2 | 54.4 | 74.8 | 80 | 87.5 | 92.5 | 99.2 | 107.6 | 109.1 | 109.3 | 105.5 | 94.7 | 85 | 72.3 | 52.4 | 56.1 | 57.9 | 60.2 | 63.6 | 67.6 | 71.5 | 71.4 | 69.4 | 62.8 | 58.4 | 52.7 | 71.5 | 76.3 | 84 | 89 | 95.6 | 104.4 | 106.9 | 106.9 | 102.7 | 91.7 | 80.9 | 68.7 | 52.3 | 54.5 | 57.2 | 59.4 | 62.6 | 67.3 | 71.4 | 71.6 | 69.4 | 62.4 | 57.2 | 51.4 | 59.9 | 62 | 62.8 | 66.4 | 69.2 | 76.4 | 79.6 | 80.6 | 79.7 | 72.8 | 63.9 | 61.3 | 70.8 | 79.9 | 88.4 | 92.1 | 95.8 | 97.8 | 97.1 | 95 | 93.8 | 85.9 | 82.3 | 73.9 | 57.3 | 59 | 61.1 | 63.9 | 67.2 | 74.5 | 78.5 | 79.4 | 77.5 | 69.9 | 61.4 | 58.4 | 68.6 | 77.3 | 86.1 | 89.7 | 94.7 | 97.5 | 96.4 | 94.5 | 93.2 | 86.6 | 82.4 | 69 | 55.4 | 57 | 59.6 | 62.1 | 65.4 | 72.3 | 77.5 | 78.1 | 75.7 | 66.9 | 59.8 | 55.9 | 67.8 | 75.8 | 83.7 | 88.6 | 93.4 | 97.3 | 95.7 | 94.4 | 92.9 | 88.1 | 81.1 | 66.5 | 53.5 | 55.4 | 58.2 | 60.4 | 63.9 | 69.9 | 76.6 | 77 | 73.9 | 64.2 | 58.3 | 53.4 | 67.9 | 73.8 | 81.2 | 86.2 | 92.4 | 96.5 | 95.4 | 94.5 | 93 | 87.9 | 78.7 | 65.4 | 27.7 | 27.8 | 29 | 29.3 | 29.9 | 32.5 | 27.1 | 27.1 | 27.7 | 28.9 | 28.5 | 25.8 | 32.7 | 33.4 | 33.7 | 33.6 | 35.1 | 35.6 | 29.9 | 29.5 | 30.2 | 32.3 | 33.1 | 30.4 | 16.8 | 16.2 | 14.7 | 13.7 | 12.9 | 13.4 | 11.4 | 11.6 | 11.7 | 13.1 | 15.9 | 16.1 | 24.8 | 29.3 | 31.2 | 31.9 | 33.2 | 33.1 | 24.3 | 23.9 | 24.5 | 26.3 | 28.8 | 24.1 | 13.9 | 15.1 | 14.1 | 13.4 | 12.4 | 13.5 | 10.6 | 10.5 | 11.7 | 11.5 | 14.6 | 13.7 | 0.291 | 0.296 | 0.314 | 0.331 | 0.349 | 0.35 | 0.394 | 0.389 | 0.351 | 0.321 | 0.295 | 0.291 | 2.514 | 2.519 | 2.456 | 2.411 | 2.379 | 2.38 | 2.365 | 2.371 | 2.437 | 2.491 | 2.533 | 2.542 | 297 | 306 | 307 | 304 | 297 | 295 | 281 | 282 | 290 | 292 | 293 | 291 | 27 | 30 | 34 | 37 | 39 | 39 | 39 | 38 | 34 | 30 | 26 | 25 | 1108 | 1411 | 1875 | 2291 | 2551 | 2671 | 2427 | 2260 | 1990 | 1597 | 1211 | 1001 | 58 | 101 | 70 | 61 | 77 | 94 | 100 | 91 | 72 | 68 | 53 | 55 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.86 | N/A | -2.32 | 1.06 | N/A | N/A | N/A | -137 | 313 | 164 | 23
| MARCH-AFB_STYP20 | 10 | 4 | USA | CA | MARCH AFB | 722860 | 23119 | 33.9 | -117.25 | 1536 | 13.9 | -8 | NAP | 94-19 | 3B | 12 | 31.5 | 34.4 | 1.3 | 6.2 | 60.9 | 6.6 | 8.1 | 61.6 | 24.8 | 54.8 | 20.7 | 54.6 | 1.4 | 320 | 0.435 | 8 | 31.6 | 101.4 | 67.6 | 98.8 | 66.7 | 95.8 | 66.1 | 71.9 | 93.1 | 70.5 | 91.3 | 69.2 | 89.1 | 10.4 | 300 | 66.4 | 102.9 | 75.4 | 64.2 | 95.2 | 74.2 | 63 | 91.1 | 73 | 36.5 | 92.8 | 35.2 | 90.9 | 34.1 | 89.1 | 78.8 | 17.9 | 15.7 | 13.2 | 25.4 | 107.2 | 4.5 | 2.7 | 22.2 | 109.2 | 19.5 | 110.8 | 17 | 112.3 | 13.7 | 114.3 | 22.8 | 74.6 | 4 | 1.9 | 20 | 76 | 17.7 | 77.1 | 15.4 | 78.2 | 12.5 | 79.6 | 63.9 | 52.8 | 52.8 | 56.7 | 59.7 | 65.1 | 71.6 | 77.7 | 78.9 | 75 | 66.2 | 57.8 | 51.7 | 11.17 | 5.68 | 5.81 | 5.61 | 6.17 | 6.1 | 5.52 | 4.68 | 5.11 | 6.19 | 6.01 | 6.01 | 5.45 | 138 | 36 | 33 | 9 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 46 | 1944 | 378 | 344 | 262 | 179 | 74 | 10 | 0 | 0 | 4 | 57 | 224 | 412 | 5213 | 123 | 110 | 218 | 296 | 468 | 647 | 858 | 897 | 749 | 502 | 245 | 100 | 1543 | 1 | 1 | 5 | 21 | 76 | 207 | 393 | 432 | 303 | 94 | 10 | 0 | 21579 | 94 | 119 | 325 | 696 | 1311 | 2849 | 4895 | 5438 | 3760 | 1602 | 440 | 50 | 11479 | 10 | 18 | 80 | 252 | 586 | 1478 | 2804 | 3253 | 2120 | 740 | 136 | 2 | 5.3 | 4.7 | 5 | 5 | 5.8 | 6.1 | 6 | 6 | 5.6 | 5.1 | 4.9 | 4.5 | 4.8 | 11.6 | 2.4 | 3 | 1.6 | 0.7 | 0.2 | 0.1 | 0.2 | 0.1 | 0.2 | 0.4 | 1 | 1.7 | 22.2 | 11.3 | 11.2 | 6.6 | 2.4 | 2 | 0.7 | 1.5 | 0.4 | 1.5 | 5.5 | 2.1 | 8.5 | 4.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 5.3 | 2.9 | 2.5 | 1.5 | 0.6 | 0.4 | 0.2 | 0.3 | 0.1 | 0.3 | 1 | 0.5 | 1.8 | 81.2 | 82.8 | 87.3 | 92.6 | 97.4 | 102.4 | 104 | 105.5 | 103.7 | 97.6 | 89.2 | 78.9 | 54.3 | 54.9 | 58.6 | 58.9 | 64 | 65.9 | 69.7 | 69 | 66.7 | 61.8 | 57.3 | 52.5 | 76.7 | 77.9 | 81.6 | 86.5 | 91.4 | 96.6 | 99.4 | 101.6 | 99.3 | 92.5 | 84.1 | 74.8 | 52.2 | 53.5 | 57.3 | 58 | 62.3 | 65.4 | 68 | 67.7 | 66.4 | 59.7 | 55.7 | 51 | 72.4 | 72.5 | 77.3 | 82.1 | 86.9 | 92.7 | 96.6 | 98.7 | 95.9 | 88.5 | 79.3 | 70.3 | 51.1 | 52.2 | 55.9 | 57 | 61 | 64.9 | 67.7 | 67.2 | 65.8 | 59.1 | 53.9 | 49.7 | 67.9 | 67 | 72.7 | 77.2 | 81.6 | 89.1 | 93.3 | 95.3 | 91.9 | 83.7 | 74.1 | 65.5 | 49.7 | 50.7 | 54.5 | 55.9 | 60.6 | 64.4 | 67.2 | 66.7 | 65.1 | 58.8 | 52.3 | 49 | 59.5 | 59.9 | 63.4 | 64.1 | 67.4 | 70.9 | 73.2 | 74.4 | 73 | 68.8 | 61.1 | 59.6 | 66.4 | 67.4 | 78 | 82.2 | 90.9 | 93.1 | 94 | 92 | 92.9 | 79.8 | 68.8 | 63.8 | 56.8 | 57.1 | 60.5 | 61.5 | 65.2 | 68.4 | 71.4 | 72 | 71 | 65.9 | 58.9 | 56.7 | 64.3 | 66.5 | 73.7 | 78.5 | 85.1 | 89.9 | 92.8 | 94 | 90.5 | 80.2 | 71.8 | 62.8 | 54.8 | 55.3 | 58.6 | 59.4 | 63.6 | 67 | 70.2 | 70.3 | 69.2 | 63.6 | 57.3 | 54.4 | 62.6 | 65.5 | 70.9 | 74.6 | 81.8 | 87.3 | 91 | 92.3 | 86.7 | 77.2 | 70.3 | 60.7 | 53.1 | 53.7 | 56.6 | 57.5 | 61.8 | 65.6 | 68.9 | 68.8 | 67.6 | 61.7 | 55.7 | 52.2 | 61.6 | 62.4 | 67.9 | 71.1 | 77.5 | 84.2 | 88.8 | 89.9 | 85.3 | 74.4 | 68 | 59.6 | 25.8 | 24.6 | 27 | 28.1 | 27.1 | 30.2 | 30.9 | 31.6 | 30.3 | 29.5 | 29 | 25.7 | 35.5 | 37 | 37.1 | 38.9 | 37.7 | 37.2 | 34.1 | 34.6 | 35.4 | 39.3 | 38.8 | 35.1 | 16.9 | 17.2 | 16.7 | 15.7 | 14 | 12.9 | 11.7 | 12.3 | 12.3 | 14.9 | 17.1 | 16.8 | 24.4 | 25.9 | 30.3 | 31.5 | 32.2 | 32.8 | 30.4 | 30.7 | 29.4 | 29 | 29.5 | 22.7 | 13.7 | 14.1 | 15.2 | 14 | 12.4 | 11.8 | 10.8 | 11.4 | 10.7 | 11.9 | 14.5 | 13.1 | 0.29 | 0.299 | 0.319 | 0.333 | 0.346 | 0.347 | 0.375 | 0.359 | 0.341 | 0.327 | 0.297 | 0.298 | 2.573 | 2.558 | 2.482 | 2.449 | 2.444 | 2.454 | 2.437 | 2.467 | 2.503 | 2.515 | 2.588 | 2.578 | 296 | 304 | 304 | 302 | 298 | 296 | 287 | 291 | 293 | 289 | 291 | 286 | 25 | 28 | 33 | 36 | 36 | 36 | 36 | 35 | 32 | 29 | 24 | 23 | 1033 | 1318 | 1774 | 2158 | 2370 | 2545 | 2426 | 2291 | 1960 | 1501 | 1148 | 935 | 70 | 126 | 86 | 92 | 121 | 124 | 114 | 65 | 63 | 88 | 55 | 64 | N/A | -1.89 | -3.56 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.13 | N/A | -3.04 | 1.26 | N/A | N/A | N/A | -196 | 400 | 205 | 52
| PALM-SPRINGS_STYP20 | 15 | 4 | USA | CA | PALM SPRINGS | 722868 | 93138 | 33.822 | -116.504 | 409 | 14.48 | -8 | NAP | 98-19 | 1B | 12 | 41.2 | 43.9 | -0.1 | 5.5 | 64.6 | 4.3 | 6.9 | 66.2 | 23.3 | 61.4 | 18.9 | 61.8 | 4 | 330 | 0.442 | 7 | 25.8 | 112.4 | 70.2 | 109.7 | 70.2 | 107.8 | 69.8 | 78.3 | 97.9 | 76.9 | 97.2 | 75.3 | 97.6 | 10 | 320 | 72.8 | 123.6 | 90.4 | 70.3 | 113.4 | 90.9 | 67.1 | 101.1 | 91.8 | 42.1 | 96.9 | 40.4 | 96.9 | 38.9 | 97.5 | 89.8 | 22.9 | 19.9 | 17.8 | 35.6 | 117.5 | 3.1 | 2.7 | 33.3 | 119.4 | 31.5 | 121 | 29.7 | 122.5 | 27.4 | 124.5 | 29 | 81.3 | 2.6 | 3.7 | 27.1 | 84 | 25.6 | 86.2 | 24.2 | 88.3 | 22.3 | 91 | 75.4 | 59.2 | 61.2 | 67.4 | 72.3 | 79.5 | 88.1 | 93.9 | 93.2 | 87.7 | 77.2 | 66.3 | 57.6 | 14.15 | 6.12 | 6.57 | 7.11 | 7.18 | 7.23 | 6.27 | 4.27 | 4.34 | 6.05 | 6.54 | 6.79 | 5.52 | 12 | 6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 723 | 197 | 142 | 58 | 19 | 2 | 0 | 0 | 0 | 0 | 3 | 64 | 238 | 9275 | 290 | 314 | 540 | 670 | 914 | 1142 | 1362 | 1340 | 1131 | 843 | 488 | 241 | 4510 | 16 | 35 | 133 | 239 | 450 | 692 | 897 | 875 | 681 | 381 | 102 | 9 | 67829 | 181 | 405 | 1576 | 2955 | 6127 | 10909 | 15128 | 14611 | 10351 | 4478 | 1014 | 94 | 43740 | 23 | 93 | 622 | 1438 | 3604 | 7386 | 10812 | 10343 | 6731 | 2330 | 349 | 9 | 6.5 | 5 | 5.3 | 6.5 | 8 | 8.9 | 8.1 | 7.2 | 6.5 | 6.5 | 6.1 | 5.2 | 4.8 | 4.9 | 1 | 0.8 | 0.5 | 0.1 | 0.1 | 0 | 0.2 | 0.4 | 0.4 | 0.2 | 0.7 | 0.7 | 13.7 | 4.3 | 5.4 | 2.1 | 1 | 1.1 | 0.8 | 2.6 | 4.3 | 4.2 | 1.9 | 6.3 | 2.9 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.3 | 1.3 | 1.1 | 0.6 | 0.2 | 0.2 | 0.2 | 0.5 | 0.9 | 0.9 | 0.4 | 1.2 | 0.8 | 82.4 | 86.9 | 95.2 | 100.6 | 108.4 | 115 | 116.9 | 115.1 | 110.5 | 101.9 | 92.1 | 81.2 | 54.5 | 56.5 | 61 | 63.8 | 69.3 | 68 | 74 | 71.4 | 68.7 | 65.2 | 59.4 | 55.1 | 79 | 82.8 | 90.5 | 96.5 | 103.6 | 110.5 | 112.7 | 111.4 | 107.7 | 98.8 | 88.1 | 76.6 | 53.7 | 55.3 | 59.8 | 61.6 | 65.2 | 68 | 70.8 | 71 | 68.8 | 64 | 58.4 | 53.7 | 75.2 | 79.4 | 87.1 | 92.5 | 100 | 107.7 | 109.7 | 108.9 | 105.1 | 94.9 | 84 | 72.8 | 52.3 | 54.6 | 58.3 | 60.5 | 65.8 | 67.4 | 71.2 | 70.8 | 67.9 | 62.4 | 57.3 | 52 | 72.1 | 75 | 82.9 | 88.5 | 96.7 | 104.5 | 107.6 | 106.4 | 102 | 91.4 | 80.4 | 69.9 | 51.4 | 53 | 57.2 | 59.1 | 63.5 | 66.8 | 70.9 | 70.7 | 67.6 | 61.6 | 56 | 50.8 | 59.3 | 60.4 | 64.8 | 67.8 | 73.5 | 78.4 | 80.5 | 81 | 77.6 | 70.8 | 62.6 | 59.3 | 73.4 | 75.4 | 84.8 | 91.9 | 97.9 | 98.3 | 100.2 | 100.3 | 94.1 | 86.8 | 82.3 | 72.2 | 57.1 | 57.9 | 62.1 | 64.1 | 70.2 | 74 | 78.2 | 78.6 | 75.7 | 68.3 | 60.3 | 56.8 | 68.6 | 73.7 | 83.3 | 90.6 | 96.9 | 98.8 | 97.6 | 98.7 | 94.6 | 89.9 | 81.5 | 68.9 | 55.2 | 56.2 | 60.2 | 62.1 | 67.3 | 71.5 | 76.8 | 77 | 74 | 65.9 | 58.8 | 54.7 | 68.2 | 73 | 81.8 | 87.4 | 94.2 | 99.7 | 97.4 | 97.9 | 94.9 | 89.1 | 79.8 | 67.2 | 53.4 | 54.8 | 58.7 | 60.4 | 65.4 | 69.5 | 75.3 | 75.3 | 72.1 | 63.9 | 57.2 | 52.8 | 68.4 | 71.3 | 79.6 | 84.2 | 91.6 | 98.3 | 98.2 | 98 | 94.1 | 86.7 | 76.8 | 66 | 21.3 | 21.7 | 24 | 25 | 26.3 | 29 | 25.8 | 25.7 | 25.3 | 24 | 22.5 | 20.8 | 25.4 | 27.1 | 28.6 | 29.9 | 30.3 | 31.9 | 28.8 | 28.1 | 28.1 | 27.4 | 26.5 | 24.8 | 11.3 | 11.3 | 10 | 9.9 | 9.3 | 8.3 | 8.1 | 8.6 | 8.2 | 10 | 11.3 | 11.4 | 20.7 | 23.2 | 26.8 | 27.8 | 28.6 | 29 | 22.1 | 20.8 | 20.9 | 24 | 23.8 | 20.9 | 9.8 | 10.3 | 10.1 | 10.1 | 10 | 11 | 10.4 | 11.7 | 9.7 | 9.5 | 10.8 | 10.2 | 0.307 | 0.312 | 0.331 | 0.35 | 0.365 | 0.368 | 0.401 | 0.391 | 0.359 | 0.349 | 0.313 | 0.315 | 2.49 | 2.488 | 2.422 | 2.381 | 2.369 | 2.376 | 2.372 | 2.385 | 2.447 | 2.423 | 2.512 | 2.496 | 288 | 298 | 300 | 297 | 292 | 289 | 279 | 281 | 287 | 280 | 284 | 278 | 27 | 30 | 35 | 38 | 39 | 39 | 39 | 37 | 34 | 32 | 26 | 26 | 1054 | 1349 | 1823 | 2234 | 2509 | 2684 | 2438 | 2279 | 1988 | 1559 | 1171 | 954 | 71 | 118 | 85 | 72 | 100 | 101 | 116 | 98 | 74 | 78 | 49 | 58 | 1.08 | N/A | -3.69 | 1.51 | -1.48 | N/A | N/A | -176 | 482 | 310 | 1.04 | N/A | -2.92 | 1.12 | N/A | N/A | N/A | -167 | 367 | 193 | 47
| RIVERSIDE_STYP20 | 10 | 4 | USA | CA | RIVERSIDE | 722869 | 03171 | 33.952 | -117.439 | 804 | 14.27 | -8 | NAP | 98-19 | 3B | 12 | 36.6 | 38.9 | 1.1 | 6 | 61.7 | 6.6 | 8 | 64.5 | 26.6 | 62.4 | 23.4 | 63.1 | 2.6 | 60 | 0.398 | 8 | 29.2 | 100.7 | 69.1 | 98.3 | 68.6 | 95.1 | 67.4 | 72.9 | 93.6 | 71.4 | 91.9 | 70.1 | 90 | 10.3 | 270 | 66.2 | 99.3 | 80.2 | 64.2 | 92.6 | 78.6 | 63.2 | 89.4 | 77.3 | 36.8 | 93.7 | 35.6 | 91.9 | 34.5 | 90.5 | 84 | 18.6 | 16.1 | 13.6 | 32.2 | 107.8 | 2.4 | 3.8 | 30.4 | 110.5 | 29 | 112.7 | 27.7 | 114.9 | 25.9 | 117.6 | 28.4 | 75 | 1.7 | 1.4 | 27.2 | 76 | 26.1 | 76.8 | 25.2 | 77.6 | 23.9 | 78.6 | 66.3 | 56.4 | 56.4 | 59.6 | 62.6 | 67.3 | 72.8 | 78.8 | 79.2 | 76.4 | 69 | 61.2 | 55.2 | 10.34 | 6.35 | 6.37 | 6.15 | 6.14 | 5.37 | 5.16 | 4.81 | 4.73 | 6.01 | 6.14 | 6.36 | 5.58 | 46 | 14 | 10 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 16 | 1357 | 277 | 252 | 188 | 117 | 35 | 3 | 0 | 0 | 1 | 29 | 147 | 308 | 5989 | 212 | 188 | 302 | 378 | 535 | 683 | 891 | 905 | 792 | 588 | 339 | 176 | 1823 | 9 | 10 | 22 | 44 | 105 | 236 | 426 | 440 | 343 | 151 | 34 | 3 | 20881 | 179 | 249 | 452 | 739 | 1227 | 2466 | 4581 | 4837 | 3697 | 1776 | 575 | 103 | 10632 | 29 | 62 | 137 | 283 | 528 | 1209 | 2533 | 2759 | 2038 | 843 | 200 | 11 | 4.9 | 4.9 | 4.6 | 4.8 | 5.2 | 5.5 | 5.5 | 5.4 | 4.9 | 4.4 | 4.3 | 4.4 | 4.7 | 11.6 | 2.4 | 3 | 1.6 | 0.7 | 0.2 | 0.1 | 0.2 | 0.1 | 0.2 | 0.4 | 1 | 1.7 | 22.2 | 11.3 | 11.2 | 6.6 | 2.4 | 2 | 0.7 | 1.5 | 0.4 | 1.5 | 5.5 | 2.1 | 8.5 | 4.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 5.3 | 2.9 | 2.5 | 1.5 | 0.6 | 0.4 | 0.2 | 0.3 | 0.1 | 0.3 | 1 | 0.5 | 1.8 | 83.6 | 85.9 | 89.8 | 93.4 | 97.2 | 101.1 | 103.5 | 104.4 | 104.4 | 98.9 | 91 | 81.4 | 54.8 | 56 | 59 | 60.2 | 64.5 | 67.5 | 70.2 | 69.5 | 68.6 | 64 | 58.5 | 54.6 | 79.1 | 81.4 | 83.7 | 87.7 | 90.9 | 95.2 | 99.2 | 100.1 | 99.8 | 93.7 | 85.8 | 77 | 53.4 | 54.7 | 57.2 | 59 | 63.1 | 67.3 | 70.5 | 69.8 | 68.6 | 61.2 | 57 | 52.5 | 74.9 | 76.4 | 79.2 | 82.2 | 86.3 | 91 | 95.9 | 97.2 | 95.9 | 89.7 | 81 | 72.5 | 52.1 | 53.6 | 56.4 | 57.9 | 62.5 | 66.4 | 69.4 | 69 | 67.6 | 60.6 | 55.4 | 50.9 | 70.9 | 70.3 | 74 | 77.4 | 81.2 | 87.7 | 92.6 | 93.3 | 91.4 | 84.2 | 75.5 | 68 | 51 | 51.7 | 55.2 | 57 | 61.8 | 65.6 | 68.6 | 68.1 | 66.7 | 59.9 | 53.7 | 50.1 | 59.9 | 60.4 | 63.3 | 64.8 | 69.2 | 71.1 | 74.8 | 75.4 | 74.3 | 68.8 | 62 | 59.3 | 71.9 | 73 | 80.9 | 85.7 | 90.7 | 94.2 | 97 | 94.7 | 95.4 | 84.5 | 75.2 | 68 | 57.3 | 57.8 | 60.8 | 62.1 | 66.7 | 69.3 | 72.8 | 72.7 | 72.1 | 66.3 | 59.9 | 57.3 | 66.5 | 70.7 | 77.2 | 80.7 | 85.6 | 91.3 | 93.7 | 93.1 | 91.8 | 83.9 | 75.1 | 65.3 | 55.4 | 56 | 59 | 60 | 64.6 | 67.9 | 71.3 | 71.1 | 70.2 | 64.4 | 58.3 | 55.3 | 66 | 68.7 | 73.5 | 77.3 | 81.8 | 87.9 | 91.4 | 92 | 89.5 | 81.1 | 72.4 | 64.3 | 53.7 | 54.4 | 57.2 | 58.4 | 62.6 | 66.4 | 69.8 | 69.5 | 68.4 | 62.6 | 57 | 53.4 | 64.9 | 65.3 | 69.9 | 73.5 | 77.8 | 84.3 | 88.7 | 89.9 | 86.7 | 77.3 | 69.8 | 62.4 | 23.3 | 22.6 | 24 | 24.5 | 24.1 | 26.6 | 28.1 | 29.2 | 28.3 | 26 | 25.2 | 22.8 | 31 | 33.4 | 32.7 | 34.3 | 34 | 33.1 | 31 | 32.5 | 33.9 | 35.4 | 33.7 | 31.7 | 13.8 | 14 | 13.4 | 13.1 | 12.7 | 11.2 | 10.2 | 11.3 | 11.3 | 13.1 | 13.7 | 14.7 | 23.8 | 25.6 | 27.9 | 29.9 | 29.9 | 30.5 | 28.4 | 29.7 | 29.8 | 28.9 | 26 | 22.6 | 12.2 | 12.1 | 12.7 | 12.5 | 11.9 | 11 | 9.8 | 10.8 | 10.9 | 11.4 | 12 | 12 | 0.303 | 0.313 | 0.335 | 0.349 | 0.356 | 0.362 | 0.383 | 0.367 | 0.35 | 0.34 | 0.305 | 0.305 | 2.547 | 2.534 | 2.45 | 2.416 | 2.429 | 2.423 | 2.428 | 2.46 | 2.494 | 2.493 | 2.582 | 2.576 | 290 | 299 | 298 | 297 | 294 | 291 | 284 | 288 | 290 | 284 | 288 | 283 | 26 | 29 | 34 | 37 | 37 | 37 | 36 | 35 | 32 | 30 | 24 | 24 | 1027 | 1311 | 1763 | 2142 | 2344 | 2522 | 2427 | 2297 | 1956 | 1491 | 1143 | 931 | 70 | 128 | 87 | 96 | 124 | 128 | 113 | 58 | 60 | 90 | 56 | 65 | 2.03 | 2.61 | N/A | 0.85 | N/A | N/A | N/A | -409 | 783 | 443 | 1.13 | N/A | -3.06 | 1.3 | N/A | N/A | N/A | -202 | 401 | 202 | 51
| LOS-ANGELES-USC_STYP20 | 9 | 4 | USA | CA | LOS ANGELES USC | 722874 | 93134 | 34.024 | -118.291 | 179 | 14.6 | -8 | NAP | 99-19 | 3A | 12 | 43.1 | 45.1 | 12 | 10.2 | 64.6 | 17.1 | 13.1 | 62.2 | 10.6 | 56.9 | 9 | 57.8 | 0.4 | 20 | 0.293 | 8 | 17.3 | 92 | 66.1 | 88.5 | 66.1 | 85.5 | 65.9 | 71.7 | 85.1 | 70.5 | 83 | 69.3 | 81 | 3 | 260 | 67.2 | 100.8 | 77.6 | 66 | 96.5 | 76.6 | 64.9 | 92.6 | 75.4 | 35.6 | 85.1 | 34.5 | 83 | 33.5 | 81.2 | 76.8 | 9.4 | 7.5 | 6.6 | 38.6 | 99.9 | 2 | 4.4 | 37.2 | 103 | 36.1 | 105.6 | 35 | 108.1 | 33.5 | 111.3 | 33 | 74.3 | 1.9 | 1.5 | 31.6 | 75.3 | 30.4 | 76.2 | 29.3 | 77.1 | 27.9 | 78.2 | 65.7 | 58.8 | 58.7 | 61.4 | 63.3 | 65.9 | 69.3 | 73.4 | 74 | 73.1 | 69.2 | 63.2 | 57.8 | 7.41 | 5.26 | 5.36 | 5.02 | 4.9 | 4.2 | 3.39 | 3.91 | 3.62 | 4.83 | 5.27 | 5.38 | 4.47 | 4 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 985 | 204 | 188 | 135 | 87 | 33 | 2 | 0 | 0 | 0 | 16 | 94 | 226 | 5739 | 273 | 244 | 354 | 400 | 493 | 578 | 725 | 744 | 693 | 595 | 396 | 244 | 1246 | 10 | 11 | 24 | 37 | 62 | 130 | 260 | 279 | 243 | 146 | 40 | 4 | 7772 | 143 | 139 | 228 | 325 | 375 | 546 | 1468 | 1633 | 1519 | 981 | 355 | 60 | 2435 | 22 | 31 | 61 | 110 | 128 | 125 | 403 | 479 | 562 | 394 | 116 | 4 | 1.9 | 1.4 | 1.9 | 2.1 | 2.4 | 2.3 | 2.1 | 2.1 | 2 | 1.8 | 1.5 | 1.3 | 1.4 | 15.9 | 3.6 | 4.2 | 2.2 | 0.9 | 0.4 | 0.1 | 0 | 0 | 0.2 | 0.7 | 1.1 | 2.4 | 29.5 | 16 | 14.6 | 7 | 2.4 | 4 | 0.8 | 0.3 | 0.1 | 2.3 | 5.4 | 2.6 | 9.7 | 6.5 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.3 | 3.9 | 3.7 | 2.1 | 0.7 | 0.8 | 0.2 | 0.1 | 0 | 0.5 | 1.1 | 0.8 | 2.3 | 83.1 | 84.8 | 86.8 | 90.5 | 91.3 | 90.2 | 92.8 | 92.7 | 97.4 | 95.3 | 89.4 | 79.8 | 55.4 | 56.5 | 59.9 | 61.5 | 61.6 | 69.2 | 71.8 | 70.2 | 68.1 | 62.2 | 59.7 | 54.3 | 78.1 | 78.4 | 80.2 | 82.3 | 82.8 | 83 | 87.4 | 88.5 | 91.1 | 89.4 | 83.3 | 75.1 | 54.6 | 55 | 57.3 | 58.2 | 62.7 | 67.2 | 70.3 | 69.3 | 68.7 | 61.8 | 57.8 | 53.6 | 73.9 | 73.1 | 75.1 | 76.8 | 77.4 | 79.5 | 84.3 | 85.1 | 86.4 | 84.3 | 77.5 | 70.9 | 53.3 | 54.7 | 56.7 | 57.8 | 62.7 | 66.5 | 69.5 | 68.8 | 67.4 | 61.4 | 56.1 | 52.8 | 69.2 | 68.2 | 70.6 | 72.2 | 73.3 | 76.6 | 81.4 | 82.1 | 82.3 | 79.1 | 73.1 | 66.8 | 52.8 | 54.1 | 56.2 | 57.7 | 61.5 | 65.1 | 68.6 | 68.3 | 66.9 | 62.3 | 55.8 | 52.6 | 60.5 | 62 | 63.7 | 65 | 68.4 | 70.2 | 74.2 | 73 | 73.2 | 69.7 | 63.6 | 60.5 | 69.1 | 70.2 | 77.3 | 78.9 | 81.5 | 84.8 | 87.5 | 87.5 | 91.2 | 82.2 | 74 | 66.8 | 58.7 | 59.4 | 61.3 | 62.2 | 65.8 | 68.4 | 71.8 | 71.2 | 71 | 67.3 | 61.9 | 59 | 66.1 | 68.5 | 73 | 74.6 | 77.4 | 81 | 84 | 84.2 | 85.4 | 79.4 | 71.7 | 65.4 | 57.3 | 57.8 | 59.7 | 60.4 | 63.9 | 66.9 | 70.5 | 70 | 69.3 | 65.7 | 60.4 | 57.4 | 64.4 | 66.1 | 69.4 | 71.4 | 74.1 | 78.2 | 81.9 | 82.1 | 82.1 | 76.4 | 69.5 | 63.8 | 56 | 56.4 | 58.3 | 59 | 62.3 | 65.7 | 69.2 | 68.9 | 68.1 | 64.2 | 59.4 | 55.9 | 63.5 | 64.3 | 66.2 | 68.8 | 71.3 | 75.8 | 79.7 | 80.2 | 79.5 | 73.2 | 67.9 | 62.2 | 18.8 | 17.4 | 17 | 16.5 | 14.8 | 14.7 | 16.5 | 17.3 | 17.6 | 17.8 | 18.7 | 18.1 | 26.7 | 25.8 | 25.3 | 24.8 | 22.2 | 19.8 | 19.6 | 20.7 | 23.6 | 27.3 | 26.8 | 25.2 | 11.8 | 11.2 | 10.5 | 10.2 | 9.1 | 8.2 | 7.7 | 7.8 | 8.4 | 10.3 | 11.6 | 12.4 | 18.4 | 19.2 | 19.1 | 19.3 | 18.2 | 18 | 18.2 | 18.8 | 19.9 | 19.2 | 18.8 | 17.4 | 9.4 | 9.8 | 8.9 | 8.8 | 8.1 | 7.8 | 7.5 | 7.6 | 7.6 | 7.9 | 9.1 | 9.8 | 0.343 | 0.356 | 0.382 | 0.384 | 0.385 | 0.405 | 0.402 | 0.383 | 0.369 | 0.38 | 0.325 | 0.326 | 2.463 | 2.437 | 2.34 | 2.347 | 2.376 | 2.324 | 2.401 | 2.433 | 2.465 | 2.397 | 2.558 | 2.551 | 274 | 282 | 283 | 286 | 286 | 279 | 279 | 283 | 283 | 270 | 280 | 274 | 28 | 32 | 38 | 39 | 39 | 41 | 37 | 36 | 33 | 33 | 25 | 24 | 1000 | 1281 | 1719 | 2104 | 2285 | 2402 | 2382 | 2262 | 1912 | 1450 | 1116 | 908 | 73 | 129 | 97 | 108 | 149 | 141 | 123 | 72 | 73 | 103 | 65 | 68 | 1.44 | N/A | N/A | 2.75 | N/A | N/A | N/A | -243 | 556 | 331 | 1.15 | N/A | -2.97 | 1.31 | N/A | N/A | N/A | -212 | 405 | 194 | 52
| HOLLYWOOD-BURBANK_STYP20 | 9 | 4 | USA | CA | HOLLYWOOD BURBANK | 722880 | 23152 | 34.201 | -118.358 | 775 | 14.29 | -8 | NAP | 94-19 | 3A | 12 | 38.9 | 41.3 | 5.3 | 7.4 | 63.2 | 11.3 | 10.1 | 62.8 | 25 | 59 | 20.8 | 58.5 | 1.7 | 350 | 0.387 | 8 | 23.2 | 97.9 | 67.8 | 94.3 | 66.8 | 91.2 | 66.1 | 72.4 | 89.8 | 70.9 | 87.6 | 69.3 | 85.5 | 8.4 | 180 | 66.4 | 100.2 | 78 | 65.1 | 95.7 | 77 | 63.8 | 91.1 | 75.3 | 36.4 | 89.7 | 35 | 87.6 | 33.8 | 85.9 | 82.9 | 18.1 | 14.8 | 12.6 | 34.2 | 105.4 | 2.3 | 3.8 | 32.5 | 108.1 | 31.1 | 110.4 | 29.8 | 112.5 | 28.1 | 115.2 | 28.9 | 75 | 2.3 | 3.2 | 27.2 | 77.3 | 25.8 | 79.2 | 24.6 | 81 | 22.9 | 83.3 | 65.4 | 56.6 | 56.7 | 60 | 62.5 | 65.7 | 70.4 | 75.8 | 77.1 | 74.8 | 68.2 | 61.2 | 55.6 | 9.39 | 5.79 | 5.95 | 5.91 | 6.31 | 5.7 | 5.26 | 4.78 | 4.98 | 6.11 | 6.02 | 5.93 | 5.18 | 31 | 9 | 8 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 10 | 1345 | 267 | 241 | 176 | 122 | 57 | 8 | 0 | 0 | 2 | 32 | 145 | 295 | 5662 | 213 | 195 | 313 | 374 | 488 | 612 | 801 | 840 | 743 | 564 | 336 | 183 | 1502 | 7 | 8 | 22 | 46 | 80 | 170 | 336 | 375 | 294 | 131 | 30 | 3 | 14776 | 140 | 170 | 345 | 587 | 779 | 1419 | 2981 | 3605 | 2879 | 1372 | 423 | 76 | 6519 | 20 | 40 | 98 | 207 | 307 | 557 | 1328 | 1786 | 1427 | 602 | 138 | 9 | 5.3 | 4.5 | 5 | 5.3 | 6.2 | 6.2 | 6.2 | 6.3 | 5.7 | 5.1 | 4.5 | 3.9 | 4.4 | 15.9 | 3.6 | 4.2 | 2.2 | 0.9 | 0.4 | 0.1 | 0 | 0 | 0.2 | 0.7 | 1.1 | 2.4 | 29.5 | 16 | 14.6 | 7 | 2.4 | 4 | 0.8 | 0.3 | 0.1 | 2.3 | 5.4 | 2.6 | 9.7 | 6.5 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.3 | 3.9 | 3.7 | 2.1 | 0.7 | 0.8 | 0.2 | 0.1 | 0 | 0.5 | 1.1 | 0.8 | 2.3 | 82.7 | 84.9 | 88.4 | 91.7 | 94.6 | 98.4 | 99.3 | 101.1 | 101.9 | 96.9 | 89.8 | 81 | 54.7 | 57 | 58.7 | 59.5 | 63.2 | 67 | 70.8 | 68.7 | 69.3 | 63.1 | 58.8 | 54.7 | 78.3 | 79.7 | 82.2 | 86 | 88.3 | 91 | 93.5 | 97.1 | 97.1 | 91.4 | 83.9 | 75.4 | 53.4 | 54.6 | 57.3 | 58.6 | 62.9 | 66.9 | 68.7 | 68.6 | 67.6 | 60.8 | 57.2 | 52.8 | 73.5 | 73.8 | 77.4 | 81 | 82.3 | 86.1 | 90.5 | 93.1 | 92.8 | 87.2 | 78.9 | 71.6 | 52.1 | 53.7 | 55.9 | 57.6 | 62.1 | 65.4 | 68.3 | 68 | 66.7 | 60.3 | 55.4 | 51.5 | 69.5 | 69 | 72.8 | 75.7 | 77.3 | 81.9 | 87.7 | 90 | 88.5 | 81.9 | 73.6 | 66.6 | 51.4 | 52.4 | 55 | 56.5 | 61.5 | 65.2 | 68 | 67.7 | 65.7 | 59.9 | 54.3 | 50.7 | 60.2 | 60.8 | 62.7 | 65.3 | 69.3 | 71.2 | 75.4 | 74.4 | 73.4 | 69.7 | 62.4 | 59.4 | 67.4 | 75.4 | 78.7 | 83.2 | 85.7 | 88.3 | 91.7 | 92.2 | 93.6 | 84.4 | 74.7 | 67.2 | 57.5 | 58.2 | 60.4 | 62.3 | 66.4 | 68.8 | 72.3 | 72.2 | 71.1 | 66.8 | 60.6 | 57.4 | 65.8 | 69.4 | 74.2 | 78 | 81.3 | 85.8 | 88.2 | 90 | 89.1 | 80 | 72.2 | 65.7 | 55.9 | 56.3 | 58.9 | 60.1 | 64.4 | 67.2 | 70.5 | 70.6 | 69.3 | 64.7 | 59.2 | 55.7 | 64.2 | 66.4 | 71.6 | 73.8 | 77.9 | 82.8 | 85.7 | 88 | 85.9 | 77.7 | 70.4 | 63.3 | 54.3 | 54.8 | 57.3 | 58.4 | 62.4 | 65.7 | 68.9 | 69 | 67.9 | 62.9 | 57.6 | 54 | 63.3 | 64.4 | 68.2 | 71 | 74 | 80.3 | 83.6 | 85.5 | 83.3 | 74.4 | 68.1 | 61.7 | 20.8 | 19.9 | 20.1 | 20 | 18.3 | 19.7 | 21.9 | 23.2 | 22.5 | 22 | 22.5 | 20.8 | 29.1 | 29.8 | 29.3 | 29.6 | 27.3 | 27.5 | 25.7 | 27.8 | 28.6 | 31.2 | 30.9 | 29.1 | 13.3 | 13.5 | 12.5 | 11.9 | 11.4 | 10.7 | 9.6 | 10.9 | 11.1 | 12.5 | 13.6 | 14 | 20 | 22.1 | 23.4 | 23.6 | 23.2 | 24.2 | 23.2 | 24.6 | 24.3 | 23.7 | 23.2 | 19.7 | 10.9 | 11.5 | 11.5 | 10.8 | 10.5 | 9.9 | 9.2 | 10.3 | 10.1 | 11.2 | 12.1 | 11.2 | 0.332 | 0.344 | 0.369 | 0.379 | 0.381 | 0.401 | 0.4 | 0.378 | 0.367 | 0.374 | 0.319 | 0.319 | 2.465 | 2.445 | 2.357 | 2.334 | 2.361 | 2.311 | 2.378 | 2.416 | 2.443 | 2.382 | 2.546 | 2.534 | 277 | 286 | 287 | 288 | 287 | 280 | 279 | 285 | 284 | 271 | 281 | 276 | 28 | 31 | 37 | 40 | 39 | 41 | 38 | 36 | 34 | 33 | 25 | 25 | 994 | 1275 | 1718 | 2107 | 2315 | 2464 | 2423 | 2294 | 1938 | 1466 | 1119 | 905 | 75 | 135 | 99 | 107 | 142 | 136 | 115 | 67 | 63 | 98 | 60 | 68 | N/A | N/A | -2.88 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.15 | N/A | -2.97 | 1.31 | N/A | N/A | N/A | -212 | 405 | 194 | 52
| SANTA-MONICA_STYP20 | 6 | 4 | USA | CA | SANTA MONICA | 722885 | 93197 | 34.016 | -118.451 | 174 | 14.6 | -8 | NAP | 00-19 | 3C | 12 | 43.3 | 45.3 | 8.8 | 8.7 | 63.1 | 14.5 | 11.6 | 61.2 | 16.9 | 57.8 | 14.9 | 57.2 | 3.2 | 40 | 0.349 | 8 | 11.1 | 85.7 | 62 | 82.1 | 62.5 | 79.3 | 63 | 70.3 | 77.4 | 69 | 76.1 | 67.8 | 74.9 | 6.5 | 210 | 67.7 | 102.4 | 74.1 | 66.2 | 97.1 | 73.2 | 64.8 | 92.3 | 71.7 | 34.3 | 77.6 | 33.2 | 76.4 | 32.2 | 74.9 | 75.6 | 14.5 | 12.5 | 11.2 | 39.6 | 94 | 2 | 4.7 | 38.1 | 97.4 | 37 | 100.2 | 35.9 | 102.8 | 34.4 | 106.2 | 32.6 | 71.5 | 2.3 | 2.1 | 30.9 | 73 | 29.6 | 74.2 | 28.3 | 75.4 | 26.6 | 76.9 | 62.9 | 57.8 | 57 | 59 | 60.4 | 62.8 | 65.6 | 69 | 69.5 | 69.2 | 66.1 | 61.6 | 56.9 | 6.42 | 5.48 | 5.06 | 4.56 | 4.51 | 3.92 | 2.72 | 3.39 | 3.41 | 4.61 | 5.1 | 5.32 | 4.53 | 7 | 3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1369 | 233 | 230 | 197 | 155 | 91 | 20 | 4 | 3 | 8 | 45 | 130 | 253 | 4731 | 245 | 198 | 280 | 311 | 395 | 469 | 590 | 603 | 575 | 499 | 349 | 217 | 620 | 11 | 7 | 12 | 16 | 22 | 39 | 129 | 141 | 133 | 79 | 28 | 3 | 2475 | 95 | 71 | 103 | 128 | 144 | 71 | 264 | 360 | 527 | 469 | 215 | 28 | 576 | 13 | 14 | 23 | 36 | 56 | 15 | 29 | 39 | 132 | 160 | 58 | 1 | 4.7 | 4.3 | 4.6 | 4.9 | 5.4 | 5.3 | 5.1 | 5 | 4.7 | 4.4 | 4.1 | 4.1 | 4.2 | 15.9 | 3.6 | 4.2 | 2.2 | 0.9 | 0.4 | 0.1 | 0 | 0 | 0.2 | 0.7 | 1.1 | 2.4 | 29.5 | 16 | 14.6 | 7 | 2.4 | 4 | 0.8 | 0.3 | 0.1 | 2.3 | 5.4 | 2.6 | 9.7 | 6.5 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.3 | 3.9 | 3.7 | 2.1 | 0.7 | 0.8 | 0.2 | 0.1 | 0 | 0.5 | 1.1 | 0.8 | 2.3 | 81.7 | 82.2 | 83 | 85 | 87.5 | 81.8 | 83.3 | 83.8 | 90.1 | 91.2 | 86.4 | 78 | 55.8 | 55.8 | 57.7 | 57.3 | 57.8 | 66.6 | 69.4 | 68.2 | 67.2 | 62.1 | 58 | 53.4 | 76.4 | 74.8 | 76.1 | 77.1 | 76.6 | 75 | 79.3 | 80.6 | 83.3 | 84.2 | 80.3 | 72.6 | 53.1 | 53.6 | 55.3 | 56 | 59.2 | 64.5 | 68.1 | 67.7 | 67.3 | 59.9 | 56.5 | 52.5 | 72.3 | 69.9 | 70.9 | 71.8 | 71.6 | 72.4 | 76.7 | 77.9 | 79.4 | 79.1 | 75 | 68.5 | 52.5 | 53.3 | 54.6 | 55.4 | 60.4 | 63.5 | 67.3 | 67.3 | 66.6 | 60.5 | 54.9 | 52.2 | 67.6 | 65.1 | 66.4 | 67.6 | 68.3 | 70.5 | 74.6 | 75.4 | 76.3 | 74.4 | 70.5 | 64.9 | 51.3 | 53 | 54.9 | 55.9 | 59.3 | 62.5 | 66.6 | 66.6 | 66.1 | 61.8 | 55.3 | 52.4 | 60.1 | 60.3 | 61.9 | 61.9 | 64.4 | 67.7 | 71.6 | 71.6 | 71.9 | 69.6 | 63.2 | 61.1 | 66.8 | 67.5 | 72.5 | 73.1 | 73.9 | 77.5 | 78.1 | 78.7 | 80.9 | 77.5 | 69.5 | 64.3 | 58.4 | 58.5 | 59.9 | 59.8 | 62.6 | 65.7 | 69.9 | 69.8 | 69.8 | 66.9 | 61.5 | 59.1 | 64.3 | 64.4 | 68.1 | 67.9 | 70.7 | 73.5 | 76 | 77.1 | 77.9 | 75.2 | 68.3 | 64 | 57.2 | 57.2 | 58.5 | 58.7 | 61.4 | 64.4 | 68.7 | 68.4 | 68.5 | 65.3 | 60.2 | 57.7 | 63.3 | 62.9 | 65.4 | 66 | 68.6 | 71 | 74.7 | 75.6 | 76.3 | 72.6 | 67.2 | 62.7 | 55.9 | 56 | 57.4 | 57.6 | 60.2 | 63.4 | 67.4 | 67.2 | 67.1 | 63.9 | 59.1 | 56.3 | 62.1 | 62.1 | 63.2 | 64.6 | 66.7 | 69.2 | 73.5 | 74.1 | 74.5 | 69.9 | 66.2 | 61.4 | 16.6 | 15.4 | 13.8 | 13.2 | 11.1 | 10 | 10.3 | 11.1 | 12.5 | 14.3 | 16.4 | 15.9 | 24.2 | 23.7 | 21.8 | 21 | 16.6 | 13 | 12.8 | 13.7 | 17.4 | 23.3 | 23.9 | 21.7 | 11.4 | 11.5 | 10.3 | 9.5 | 7.5 | 6 | 5.5 | 6 | 7.5 | 11 | 12 | 11.9 | 15.8 | 15.6 | 14.5 | 14.7 | 12.7 | 12.2 | 11.9 | 12.2 | 14.3 | 15.7 | 16.4 | 14.7 | 9.3 | 8.9 | 7.8 | 7.3 | 6.2 | 5.8 | 5.2 | 5.8 | 6.5 | 8.6 | 9.7 | 9.6 | 0.332 | 0.345 | 0.368 | 0.378 | 0.385 | 0.4 | 0.404 | 0.383 | 0.371 | 0.372 | 0.321 | 0.323 | 2.504 | 2.48 | 2.395 | 2.367 | 2.378 | 2.342 | 2.393 | 2.433 | 2.461 | 2.43 | 2.57 | 2.562 | 279 | 287 | 287 | 288 | 286 | 280 | 278 | 283 | 283 | 273 | 281 | 276 | 27 | 30 | 36 | 39 | 39 | 40 | 38 | 36 | 33 | 32 | 25 | 24 | 995 | 1276 | 1709 | 2096 | 2271 | 2372 | 2369 | 2252 | 1900 | 1441 | 1111 | 903 | 73 | 129 | 99 | 110 | 155 | 145 | 126 | 75 | 76 | 107 | 67 | 69 | 1.49 | N/A | -2.9 | 2.05 | 1.71 | N/A | N/A | -277 | 529 | 290 | 1.15 | N/A | -2.97 | 1.31 | N/A | N/A | N/A | -212 | 405 | 194 | 52
| VAN-NUYS_STYP20 | 9 | 4 | USA | CA | VAN NUYS | 722886 | 23130 | 34.21 | -118.489 | 770 | 14.29 | -8 | NAP | 98-19 | 3A | 12 | 38.6 | 41.1 | 0.1 | 5.7 | 60.9 | 5.5 | 7.5 | 63.1 | 25.9 | 58.8 | 24 | 59.1 | 1.7 | 0 | 0.391 | 8 | 26.1 | 100 | 67.5 | 97 | 66.9 | 93.5 | 65.8 | 72.1 | 91.9 | 70.5 | 89.6 | 69.1 | 87.5 | 8.1 | 130 | 65.6 | 97.3 | 79.3 | 63.9 | 91.6 | 76.4 | 63 | 88.6 | 74.9 | 36.1 | 92.3 | 34.7 | 89.6 | 33.6 | 87.6 | 84.2 | 20.7 | 18 | 15.3 | 34.1 | 106.4 | 2.5 | 3.8 | 32.3 | 109.1 | 30.8 | 111.4 | 29.4 | 113.5 | 27.5 | 116.2 | 29.5 | 75.2 | 2.5 | 3.5 | 27.7 | 77.7 | 26.2 | 79.7 | 24.8 | 81.6 | 23 | 84.2 | 66.1 | 57.2 | 56.7 | 60.3 | 62.7 | 66.7 | 71.5 | 77.4 | 78.2 | 75.6 | 68.9 | 61.8 | 55.9 | 9.92 | 6.59 | 6.35 | 6.45 | 6.48 | 6.01 | 5.75 | 5.05 | 5.09 | 6.33 | 6.31 | 6.41 | 5.89 | 39 | 12 | 9 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 13 | 1307 | 257 | 244 | 175 | 119 | 47 | 8 | 0 | 0 | 2 | 31 | 135 | 289 | 5923 | 234 | 196 | 321 | 381 | 517 | 645 | 849 | 873 | 768 | 587 | 356 | 196 | 1716 | 14 | 11 | 28 | 50 | 99 | 203 | 384 | 408 | 320 | 152 | 40 | 7 | 18392 | 135 | 178 | 418 | 672 | 1107 | 1988 | 3913 | 4320 | 3377 | 1656 | 539 | 89 | 8920 | 17 | 32 | 116 | 243 | 481 | 909 | 2021 | 2353 | 1808 | 748 | 183 | 9 | 5.2 | 6.2 | 5.3 | 5.3 | 5.8 | 5.5 | 5.4 | 5.1 | 4.6 | 4.2 | 4.5 | 4.9 | 5.9 | 15.9 | 3.6 | 4.2 | 2.2 | 0.9 | 0.4 | 0.1 | 0 | 0 | 0.2 | 0.7 | 1.1 | 2.4 | 29.5 | 16 | 14.6 | 7 | 2.4 | 4 | 0.8 | 0.3 | 0.1 | 2.3 | 5.4 | 2.6 | 9.7 | 6.5 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.3 | 3.9 | 3.7 | 2.1 | 0.7 | 0.8 | 0.2 | 0.1 | 0 | 0.5 | 1.1 | 0.8 | 2.3 | 82.2 | 84 | 88.9 | 92.7 | 97.4 | 101.8 | 102.2 | 103.6 | 104.1 | 97.7 | 90.3 | 81.1 | 54.6 | 56 | 59.2 | 60.2 | 65.6 | 66 | 69.8 | 68.1 | 69.4 | 62.8 | 58.3 | 54.5 | 78.1 | 79.9 | 83 | 87 | 90.8 | 93.9 | 97.2 | 99.4 | 99.2 | 92.6 | 85.6 | 76.3 | 53.6 | 55.3 | 57.9 | 59.3 | 62.8 | 67 | 68.4 | 67.7 | 67 | 60.8 | 57.4 | 52.5 | 74 | 74.8 | 78.7 | 81.6 | 85.3 | 89.5 | 93.5 | 95.8 | 95.1 | 88.5 | 80.3 | 72.2 | 52.2 | 53.7 | 56.5 | 57.6 | 62.1 | 65.8 | 68.1 | 67 | 66.3 | 59.9 | 55.2 | 51.4 | 70.4 | 70 | 74.1 | 76.9 | 80 | 84.7 | 90.6 | 92 | 90.5 | 83.6 | 75.3 | 68.1 | 50.8 | 51.8 | 55.3 | 56.3 | 61.4 | 65 | 67.4 | 66.5 | 65 | 58.9 | 53.5 | 50.2 | 59.7 | 60.3 | 64 | 65.7 | 72 | 71.7 | 74.6 | 73.5 | 73.1 | 68.8 | 61.7 | 59.2 | 70.8 | 72.1 | 77 | 83.6 | 86.3 | 89.9 | 94.7 | 94.9 | 96.2 | 83.9 | 75.6 | 68.1 | 57.3 | 57.6 | 60.8 | 62.1 | 66.5 | 69.2 | 72 | 71.3 | 70.8 | 66.1 | 59.8 | 57.3 | 67.4 | 70.6 | 76.4 | 78.7 | 83.1 | 88.1 | 91 | 91.7 | 91.3 | 82 | 74.8 | 65.8 | 55.5 | 55.9 | 59 | 59.9 | 64.4 | 67.6 | 70.3 | 69.6 | 68.9 | 64.1 | 58.3 | 55.5 | 65.5 | 68.1 | 73.9 | 75.8 | 80.4 | 85 | 88.5 | 89.3 | 87.7 | 79 | 71.6 | 63.6 | 53.9 | 54.3 | 57.1 | 58.2 | 62.3 | 66 | 68.8 | 68.3 | 67.4 | 62.3 | 56.9 | 53.6 | 64 | 65.1 | 69.5 | 72.7 | 76.3 | 82.1 | 86.2 | 87.2 | 85 | 75.6 | 68.8 | 63 | 20.1 | 20 | 21 | 21.2 | 21.2 | 22.7 | 24.9 | 26.1 | 25.1 | 23.3 | 22.8 | 20.2 | 26.4 | 29.4 | 29.2 | 30.5 | 30.9 | 30.5 | 28.4 | 30.6 | 31.7 | 32.1 | 31.2 | 27.7 | 11.8 | 12.8 | 11.9 | 11.9 | 11.3 | 9.8 | 9.1 | 9.7 | 9.6 | 10.7 | 11.6 | 12.5 | 20.5 | 23.3 | 24.9 | 25.1 | 26.3 | 26.9 | 25.7 | 26.6 | 26.9 | 24.8 | 24.2 | 20.4 | 10.7 | 11.4 | 11.6 | 11.4 | 11.2 | 10 | 9.3 | 9.4 | 9.3 | 10.2 | 10.6 | 10.8 | 0.325 | 0.338 | 0.36 | 0.378 | 0.385 | 0.399 | 0.407 | 0.381 | 0.372 | 0.372 | 0.318 | 0.319 | 2.491 | 2.471 | 2.391 | 2.339 | 2.35 | 2.318 | 2.357 | 2.406 | 2.426 | 2.392 | 2.549 | 2.536 | 280 | 289 | 290 | 288 | 285 | 280 | 277 | 284 | 282 | 272 | 282 | 277 | 27 | 31 | 36 | 40 | 40 | 41 | 39 | 37 | 34 | 33 | 25 | 25 | 990 | 1269 | 1710 | 2099 | 2306 | 2451 | 2421 | 2293 | 1934 | 1461 | 1115 | 901 | 75 | 137 | 101 | 110 | 146 | 139 | 115 | 67 | 63 | 100 | 61 | 69 | 1.94 | N/A | -6.44 | 1.26 | N/A | N/A | N/A | -299 | 688 | 367 | 1.15 | N/A | -2.97 | 1.3 | N/A | N/A | N/A | -225 | 414 | 182 | 52
| LOMPOC_STYP20 | 5 | 4 | USA | CA | LOMPOC | 722895 | 23243 | 34.667 | -120.467 | 88 | 14.65 | -8 | NAP | 94-19 | 3C | 12 | 32.3 | 35.5 | 22.5 | 17 | 46.9 | 25.8 | 19.9 | 44.1 | 20.8 | 57.8 | 18.6 | 58.3 | 4.4 | 80 | 0.524 | 8 | 15.7 | 82.1 | 62 | 78.7 | 61.4 | 74.8 | 60.8 | 66 | 76.7 | 64.3 | 74.1 | 62.9 | 72 | 10.3 | 270 | 61.5 | 81.8 | 70.1 | 60.5 | 79.1 | 69.2 | 58.8 | 74.1 | 67.2 | 30.6 | 76.9 | 29.4 | 74.2 | 28.4 | 71.9 | 90.7 | 20.2 | 18.5 | 17 | 27.6 | 93.4 | 2.1 | 9.5 | 26.1 | 100.2 | 24.9 | 105.8 | 23.7 | 111.1 | 22.2 | 118 | 25.3 | 70.8 | 1.9 | 6 | 23.9 | 75.2 | 22.8 | 78.7 | 21.7 | 82 | 20.3 | 86.4 | 57.6 | 52.7 | 52.7 | 54.7 | 55.8 | 57.9 | 60.2 | 62.3 | 63 | 62.9 | 60.5 | 56.8 | 51.9 | 5.63 | 4.71 | 4.6 | 4.23 | 4.02 | 3.42 | 2.82 | 2.68 | 2.65 | 3.77 | 4.49 | 5.11 | 4.7 | 100 | 27 | 22 | 9 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 33 | 2761 | 381 | 345 | 320 | 278 | 224 | 148 | 93 | 74 | 85 | 155 | 253 | 405 | 2891 | 111 | 98 | 155 | 177 | 244 | 305 | 381 | 404 | 387 | 326 | 209 | 94 | 74 | 0 | 0 | 1 | 2 | 3 | 3 | 8 | 13 | 22 | 16 | 6 | 0 | 968 | 25 | 26 | 42 | 64 | 70 | 33 | 38 | 62 | 206 | 278 | 118 | 6 | 259 | 1 | 3 | 8 | 22 | 21 | 5 | 5 | 7 | 59 | 93 | 35 | 0 | 7 | 6 | 6.6 | 7.1 | 7.9 | 8.6 | 8.4 | 7.7 | 7.2 | 6.5 | 6.2 | 5.9 | 6.1 | 17.3 | 3.9 | 4.2 | 2.6 | 1.1 | 0.4 | 0.1 | 0 | 0 | 0 | 0.8 | 1.3 | 2.8 | 32.2 | 16.7 | 15.8 | 12.6 | 3.9 | 2.3 | 0.7 | 0.2 | 0.1 | 0.4 | 3.9 | 4.1 | 9.1 | 5.8 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7 | 4 | 3.6 | 3.1 | 1.2 | 0.6 | 0.2 | 0 | 0 | 0.1 | 1 | 1.1 | 2.4 | 77.4 | 78.3 | 79.3 | 82.2 | 81.5 | 78.6 | 78.8 | 80.6 | 88 | 89.8 | 84.5 | 73.4 | 56 | 57.5 | 57.7 | 60 | 61.9 | 63.8 | 65.4 | 65.9 | 66.5 | 62.2 | 60.4 | 55 | 72.3 | 71.5 | 72.3 | 72.6 | 73.1 | 72.8 | 73.4 | 75 | 80.1 | 81.3 | 76.8 | 69.6 | 54.9 | 55.3 | 56.9 | 58.1 | 60.6 | 61.7 | 63.3 | 63.9 | 63.9 | 61.2 | 58.2 | 54.9 | 66.3 | 64.7 | 67.7 | 68.4 | 69.7 | 70.2 | 71.8 | 72.4 | 74.8 | 75.2 | 71.8 | 64.3 | 54.4 | 53.5 | 56.4 | 57.5 | 59.2 | 60.3 | 62.5 | 62.6 | 63.1 | 60 | 56.8 | 54.2 | 63.2 | 62.6 | 63.9 | 64.8 | 65.9 | 67.6 | 69.8 | 70.3 | 72 | 71.6 | 66.5 | 62.7 | 53.8 | 53.2 | 55.1 | 55.8 | 57.5 | 59.1 | 61.3 | 61.7 | 62 | 59.5 | 56.4 | 54 | 60.9 | 60.3 | 61.6 | 62.4 | 64.5 | 65.3 | 66.8 | 67 | 69.3 | 67 | 63.8 | 61 | 67.8 | 71.2 | 70.9 | 73.8 | 75.7 | 76.6 | 75.9 | 77.9 | 80.6 | 80 | 73.4 | 66 | 58.4 | 57.6 | 59.4 | 60 | 61.8 | 62.3 | 64.3 | 64.7 | 66 | 63.9 | 61.2 | 58.8 | 65.5 | 65.6 | 68.4 | 69.5 | 71.7 | 71.9 | 73.2 | 73.9 | 76.4 | 74.8 | 70.9 | 63.9 | 56.7 | 55.9 | 57.8 | 58.3 | 59.5 | 60.8 | 62.4 | 63.1 | 64 | 62 | 59.3 | 56.9 | 63.2 | 63.1 | 65.6 | 66.7 | 68.2 | 69 | 70.5 | 71.5 | 73.5 | 72.2 | 67.7 | 62.3 | 54.8 | 54.2 | 56.2 | 56.7 | 57.8 | 59.3 | 61.2 | 61.9 | 62.2 | 60.3 | 57.8 | 54.9 | 61.2 | 60.6 | 63.4 | 64.2 | 65.1 | 66.3 | 68.6 | 69.8 | 70.8 | 69.3 | 65.3 | 60.4 | 23.1 | 21.1 | 21 | 20.3 | 17.7 | 16.2 | 15.1 | 15.7 | 19.3 | 23.3 | 24.3 | 22.4 | 30.9 | 28.1 | 29.3 | 27.4 | 25.4 | 20.9 | 18.3 | 19.1 | 25.7 | 32.8 | 32.2 | 26.5 | 17.6 | 16.3 | 16.7 | 15.5 | 14.5 | 12.2 | 10.6 | 10.7 | 14.1 | 17.5 | 17.5 | 16.4 | 22.5 | 22.3 | 23.2 | 23.3 | 22 | 19.1 | 17.2 | 17.9 | 22.3 | 26.3 | 24.9 | 18.8 | 14.4 | 14.1 | 14.5 | 14.3 | 13 | 11.4 | 9.9 | 10.2 | 12.7 | 15.3 | 15.1 | 12.8 | 0.305 | 0.319 | 0.327 | 0.347 | 0.358 | 0.353 | 0.367 | 0.35 | 0.35 | 0.342 | 0.307 | 0.309 | 2.596 | 2.565 | 2.544 | 2.469 | 2.46 | 2.471 | 2.487 | 2.505 | 2.509 | 2.534 | 2.604 | 2.595 | 289 | 296 | 301 | 298 | 294 | 293 | 289 | 293 | 289 | 283 | 286 | 280 | 24 | 28 | 31 | 35 | 36 | 35 | 34 | 33 | 31 | 28 | 24 | 23 | 960 | 1232 | 1675 | 2087 | 2305 | 2366 | 2243 | 2078 | 1801 | 1397 | 1072 | 857 | 74 | 123 | 106 | 125 | 149 | 109 | 81 | 92 | 95 | 105 | 60 | 74 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.19 | N/A | -2.48 | 1.48 | N/A | N/A | N/A | -299 | 437 | 142 | 27
| SAN-LUIS-OBISPO_STYP20 | 5 | 4 | USA | CA | SAN LUIS OBISPO | 722897 | 93206 | 35.237 | -120.641 | 200 | 14.59 | -8 | NAP | 94-19 | 3C | 12 | 34.2 | 36.5 | 19.9 | 15 | 53.5 | 24.4 | 18.7 | 52.9 | 21.9 | 57.2 | 19 | 58 | 1.9 | 100 | 0.501 | 9 | 23.6 | 89.9 | 64 | 85.3 | 63.3 | 81.8 | 62.9 | 67.5 | 83.2 | 66 | 80.8 | 64.6 | 78.5 | 10.9 | 310 | 61.9 | 83.5 | 71.5 | 60.6 | 79.6 | 70.2 | 59.1 | 75.3 | 68.4 | 31.8 | 83.2 | 30.6 | 80.8 | 29.7 | 78.5 | 78.6 | 24.2 | 20.9 | 18.9 | 29.8 | 99.9 | 2.9 | 4.6 | 27.7 | 103.3 | 26 | 106 | 24.4 | 108.5 | 22.3 | 111.9 | 27.7 | 70.7 | 3.1 | 2.7 | 25.4 | 72.6 | 23.6 | 74.3 | 21.9 | 75.8 | 19.7 | 77.8 | 60 | 53.9 | 54.1 | 56.3 | 57.4 | 60.3 | 63.2 | 66.2 | 66.8 | 66.6 | 63.9 | 58.2 | 53.1 | 6.98 | 5.02 | 5.61 | 5.37 | 5.29 | 4.71 | 3.97 | 3.37 | 3.27 | 4.81 | 5.85 | 5.86 | 4.78 | 79 | 20 | 19 | 8 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 23 | 2155 | 345 | 308 | 276 | 238 | 163 | 79 | 23 | 14 | 31 | 91 | 218 | 369 | 3737 | 140 | 133 | 202 | 225 | 319 | 395 | 501 | 521 | 498 | 433 | 251 | 119 | 341 | 1 | 3 | 6 | 9 | 17 | 24 | 60 | 70 | 79 | 58 | 14 | 0 | 3742 | 51 | 65 | 99 | 158 | 249 | 314 | 527 | 577 | 760 | 706 | 208 | 28 | 1194 | 8 | 13 | 19 | 53 | 86 | 97 | 124 | 151 | 290 | 292 | 59 | 2 | 6.9 | 5.3 | 6.1 | 7.1 | 8.3 | 8.9 | 8.3 | 7.4 | 7.3 | 6.9 | 6.4 | 5.3 | 5.1 | 25.9 | 5.3 | 5.3 | 4 | 1.6 | 0.4 | 0.1 | 0 | 0 | 0.4 | 1 | 2.8 | 3.9 | 49.9 | 24.6 | 15.2 | 16.5 | 6.9 | 3.4 | 0.8 | 0.5 | 1.4 | 3.9 | 5.2 | 7.8 | 10.9 | 11.7 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8 | 5.2 | 4.8 | 3.4 | 1.6 | 0.8 | 0.2 | 0.1 | 0.2 | 0.7 | 1.1 | 2.2 | 2.8 | 80.3 | 82.2 | 82 | 87.6 | 89.3 | 90 | 89.5 | 90.4 | 95.9 | 94.8 | 87 | 78.3 | 55.2 | 60.5 | 62 | 62.4 | 64.6 | 65.3 | 66.3 | 65.8 | 66.2 | 63.8 | 61.7 | 54.7 | 73.5 | 74.6 | 76.1 | 78.6 | 80.8 | 82.2 | 83.2 | 83.8 | 88.1 | 87.8 | 80.1 | 71.9 | 55.7 | 57.8 | 58.5 | 59.5 | 62.2 | 63.6 | 65.1 | 65.8 | 64.5 | 61.7 | 58.6 | 54.1 | 69 | 69.1 | 71.2 | 72.7 | 74.7 | 77.2 | 79.8 | 80.1 | 82.2 | 81.7 | 74.3 | 67.1 | 54.7 | 55.8 | 57.5 | 58.3 | 60.2 | 62.1 | 64.4 | 64.5 | 63.7 | 59.8 | 56.8 | 53.4 | 64 | 63.9 | 66.5 | 68.1 | 70.3 | 73.3 | 76.3 | 76.7 | 77.7 | 76 | 69.8 | 63.3 | 53.8 | 53.9 | 56.2 | 56.9 | 58.8 | 61 | 63.2 | 63.5 | 62.8 | 59 | 55.8 | 52.6 | 61.4 | 62.5 | 64.2 | 64.5 | 66.4 | 67.5 | 69 | 69 | 70.2 | 68 | 63.9 | 61.3 | 66.4 | 73 | 77.3 | 80.6 | 83 | 85.4 | 83.3 | 83.5 | 83.2 | 85 | 77.6 | 65.8 | 58.9 | 59.9 | 61 | 61.6 | 63.4 | 64.8 | 66.4 | 66.5 | 66.7 | 64.6 | 61.3 | 59.1 | 65.9 | 69.2 | 71.6 | 75.2 | 77.5 | 79.5 | 80.6 | 81.3 | 82.1 | 79 | 72.1 | 63.5 | 57.1 | 57.8 | 58.9 | 59.5 | 61.1 | 62.9 | 64.9 | 65 | 65 | 62.6 | 59.6 | 56.9 | 63.8 | 65.7 | 67.9 | 70.4 | 72.6 | 76 | 78.6 | 79 | 78.8 | 75.3 | 69.9 | 62.1 | 55.4 | 55.9 | 57.1 | 57.5 | 59.2 | 61.3 | 63.4 | 63.7 | 63.4 | 60.9 | 58 | 54.9 | 62 | 62.6 | 65 | 66.5 | 69.4 | 72.8 | 75.9 | 76.6 | 76.6 | 72.5 | 66.7 | 60.9 | 22 | 20.4 | 21 | 21.3 | 21 | 22 | 21.9 | 22.3 | 23.6 | 24.7 | 23.9 | 22.4 | 31 | 29.3 | 28.8 | 29.8 | 29.5 | 28.5 | 27.4 | 27.7 | 31 | 34.3 | 31.8 | 30 | 16.5 | 15.7 | 15.2 | 15 | 14.1 | 13.2 | 12 | 11.9 | 13 | 14.7 | 14.7 | 16.4 | 21.4 | 22.9 | 23.7 | 25.5 | 25.6 | 25.5 | 24.9 | 25.6 | 26.2 | 27.4 | 25.2 | 19.8 | 13.1 | 13.4 | 13.9 | 13.9 | 13.1 | 12.4 | 11.3 | 11.3 | 11.7 | 12.7 | 13 | 12.4 | 0.308 | 0.324 | 0.329 | 0.334 | 0.343 | 0.353 | 0.351 | 0.343 | 0.341 | 0.344 | 0.308 | 0.313 | 2.563 | 2.523 | 2.515 | 2.499 | 2.491 | 2.453 | 2.514 | 2.503 | 2.514 | 2.505 | 2.577 | 2.561 | 286 | 293 | 300 | 302 | 298 | 293 | 293 | 295 | 291 | 281 | 284 | 277 | 25 | 29 | 31 | 34 | 35 | 36 | 33 | 33 | 31 | 29 | 24 | 23 | 924 | 1197 | 1650 | 2069 | 2358 | 2502 | 2357 | 2171 | 1865 | 1409 | 1047 | 821 | 75 | 128 | 119 | 141 | 134 | 98 | 79 | 74 | 74 | 88 | 56 | 79 | N/A | N/A | N/A | 1.37 | N/A | N/A | N/A | -436 | 463 | N/A | 1.03 | N/A | -2.21 | 1.26 | N/A | N/A | N/A | -284 | 373 | 101 | 28
| CHINO_STYP20 | 10 | 4 | USA | CA | CHINO | 722899 | 03179 | 33.975 | -117.636 | 650 | 14.35 | -8 | NAP | 98-19 | 3B | 12 | 34.3 | 36.6 | 6.3 | 7.8 | 65.3 | 12.2 | 10.5 | 65.9 | 24.5 | 62.7 | 20.6 | 63.3 | 1.7 | 10 | 0.438 | 8 | 31.7 | 101.1 | 69.6 | 98.2 | 69 | 95.1 | 68 | 73.6 | 94.2 | 72.1 | 92.1 | 70.7 | 90.1 | 11.4 | 270 | 67.3 | 103 | 80.7 | 65.2 | 95.5 | 79.2 | 63.7 | 90.4 | 77.1 | 37.4 | 94.7 | 36 | 92.3 | 34.8 | 90 | 85.1 | 18.8 | 17.2 | 16 | 29.5 | 108.1 | 2.5 | 4.3 | 27.7 | 111.2 | 26.3 | 113.7 | 24.9 | 116.1 | 23.1 | 119.3 | 27.3 | 76.1 | 2.3 | 2.9 | 25.7 | 78.2 | 24.3 | 79.8 | 23 | 81.4 | 21.3 | 83.5 | 65.1 | 55 | 55.1 | 58.5 | 61.5 | 66.3 | 71.6 | 77.4 | 77.8 | 75 | 67.8 | 60.1 | 53.9 | 10.08 | 5.73 | 5.7 | 5.73 | 5.88 | 5.08 | 5 | 4.54 | 4.38 | 5.71 | 5.67 | 5.8 | 5.2 | 60 | 17 | 13 | 4 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 21 | 1541 | 313 | 280 | 214 | 136 | 44 | 5 | 0 | 0 | 2 | 35 | 168 | 344 | 5557 | 173 | 156 | 268 | 347 | 505 | 649 | 849 | 861 | 750 | 551 | 305 | 143 | 1563 | 4 | 3 | 12 | 31 | 84 | 204 | 384 | 396 | 302 | 121 | 21 | 1 | 19567 | 169 | 206 | 396 | 714 | 1184 | 2324 | 4273 | 4504 | 3446 | 1699 | 550 | 102 | 10162 | 26 | 52 | 123 | 280 | 516 | 1145 | 2400 | 2623 | 1964 | 824 | 197 | 12 | 5.3 | 4.3 | 4.5 | 5.2 | 6.2 | 6.8 | 6.8 | 6.5 | 6 | 5.2 | 4.7 | 4 | 3.9 | 11.5 | 2.3 | 2.5 | 1.4 | 1 | 0.2 | 0 | 0.1 | 0 | 0.2 | 0.5 | 1.2 | 1.9 | 24.4 | 8.4 | 8.4 | 3.4 | 2.9 | 0.9 | 0.1 | 0.9 | 0.2 | 0.5 | 5.5 | 2.2 | 8.5 | 4.4 | 0.4 | 0.2 | 0.3 | 0.3 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0.4 | 0.2 | 5.4 | 2.2 | 2.1 | 0.8 | 0.6 | 0.2 | 0 | 0.2 | 0 | 0.1 | 1.2 | 0.5 | 1.9 | 83.6 | 85.7 | 89.5 | 94.4 | 97.3 | 102.1 | 104.1 | 105.2 | 105.7 | 99 | 91.4 | 81.6 | 55 | 56.7 | 60.8 | 60.4 | 64.9 | 68.3 | 71.8 | 70.2 | 70.1 | 64.6 | 59.2 | 55.8 | 78.9 | 80.8 | 83.4 | 87.5 | 91.1 | 95.3 | 99.1 | 100.1 | 100 | 94 | 85.8 | 76.9 | 54.6 | 56 | 58.8 | 59.9 | 63.9 | 68.2 | 71 | 70.1 | 69.6 | 62.5 | 58.1 | 53.8 | 74.6 | 74.8 | 78.4 | 82 | 85.9 | 90.8 | 95.5 | 97.1 | 96.3 | 89.7 | 80.7 | 72.4 | 53.4 | 54.4 | 57.7 | 59 | 63.4 | 67.3 | 70.3 | 69.4 | 68.4 | 61.5 | 56.6 | 52 | 70.1 | 69.2 | 72.9 | 76.9 | 80.8 | 86.9 | 92.2 | 93.2 | 91.4 | 83.9 | 75.1 | 67.4 | 51.9 | 53.2 | 56.6 | 58.1 | 62.7 | 66.2 | 69.6 | 68.9 | 67 | 60.8 | 55.3 | 51.7 | 60.9 | 61.1 | 65 | 66.1 | 70.7 | 72.3 | 76.6 | 74.9 | 74.7 | 69.7 | 62.9 | 60.2 | 71.8 | 72.9 | 81.4 | 85.7 | 89.8 | 93 | 94.2 | 97.3 | 97.2 | 87.5 | 76.9 | 69.2 | 58.2 | 58.7 | 61.8 | 63 | 67.4 | 70.1 | 73.9 | 72.8 | 72.6 | 67.2 | 60.8 | 57.9 | 68.7 | 71.7 | 77.2 | 80.4 | 86.3 | 90.1 | 93.1 | 94.2 | 94.1 | 84 | 76.9 | 66.4 | 56.4 | 56.9 | 59.7 | 60.8 | 65.2 | 68.4 | 72.2 | 71.3 | 70.6 | 65.1 | 59.3 | 56.1 | 66.9 | 69.6 | 73.8 | 77.5 | 82.1 | 87.7 | 90.9 | 92.1 | 90.7 | 81.7 | 73.8 | 64.8 | 54.6 | 55.1 | 57.9 | 59.1 | 63 | 66.9 | 70.6 | 69.9 | 68.7 | 63.3 | 57.8 | 54.2 | 64.8 | 65.5 | 69.5 | 73.8 | 78.1 | 84.8 | 88.6 | 90 | 87 | 77.6 | 70.5 | 62.8 | 26.6 | 25.1 | 25.8 | 26.6 | 25.9 | 28 | 30.2 | 31.7 | 31.3 | 29.3 | 29.1 | 26.6 | 35.8 | 37.2 | 36.2 | 37.6 | 37.1 | 35.9 | 33.9 | 36.2 | 38.4 | 40.2 | 38.5 | 36.2 | 16.5 | 16.7 | 16 | 15 | 14.3 | 12.6 | 11.2 | 11.9 | 12.5 | 14.1 | 15.7 | 17.1 | 27.3 | 29.3 | 30.1 | 31.8 | 32.1 | 32.7 | 30.9 | 32.3 | 33.3 | 32.1 | 30.9 | 26.6 | 14.2 | 14.6 | 14.6 | 14.2 | 13.6 | 12.4 | 11.5 | 11.6 | 12.2 | 12.9 | 14.2 | 14 | 0.309 | 0.317 | 0.341 | 0.354 | 0.355 | 0.366 | 0.379 | 0.363 | 0.348 | 0.343 | 0.304 | 0.303 | 2.543 | 2.533 | 2.443 | 2.412 | 2.442 | 2.42 | 2.448 | 2.48 | 2.509 | 2.498 | 2.596 | 2.594 | 288 | 297 | 297 | 296 | 295 | 290 | 285 | 289 | 290 | 284 | 288 | 285 | 26 | 29 | 34 | 37 | 36 | 37 | 36 | 34 | 32 | 30 | 24 | 23 | 1021 | 1304 | 1753 | 2132 | 2327 | 2494 | 2418 | 2291 | 1947 | 1481 | 1137 | 926 | 71 | 128 | 89 | 99 | 129 | 131 | 115 | 59 | 62 | 93 | 57 | 65 | 2.66 | 1.24 | -5.89 | 2.05 | N/A | N/A | N/A | -414 | 994 | 536 | 1.13 | N/A | -3.06 | 1.3 | N/A | N/A | N/A | -202 | 401 | 202 | 51
| SAN-DIEGO-INTL_STYP20 | 7 | 4 | USA | CA | SAN DIEGO INTL | 722900 | 23188 | 32.734 | -117.183 | 15 | 14.69 | -8 | NAP | 94-19 | 3B | 12 | 45.3 | 47.2 | 16.8 | 12.9 | 61.2 | 21.9 | 16.4 | 61.5 | 20.2 | 59.7 | 17.9 | 59.6 | 1.8 | 340 | 0.353 | 8 | 8.6 | 84.8 | 64.4 | 81.6 | 65.6 | 79 | 65.8 | 71.4 | 78.4 | 70.3 | 77 | 69.3 | 75.6 | 8.5 | 300 | 68.9 | 106.1 | 75.1 | 67.7 | 102 | 74.4 | 66.7 | 98.4 | 73.6 | 35.2 | 78.6 | 34.3 | 77.2 | 33.3 | 75.8 | 76.1 | 16.7 | 14.6 | 12.7 | 41.7 | 92.5 | 2 | 4.5 | 40.3 | 95.7 | 39.1 | 98.4 | 37.9 | 100.9 | 36.4 | 104.2 | 34.3 | 73.3 | 2.2 | 1.8 | 32.7 | 74.6 | 31.4 | 75.6 | 30.1 | 76.6 | 28.5 | 77.9 | 64.1 | 58 | 58.3 | 60.2 | 61.9 | 64 | 66.4 | 70.1 | 71.8 | 71.1 | 67.4 | 62.2 | 57.5 | 6.22 | 4.08 | 3.91 | 3.72 | 3.94 | 3.43 | 2.92 | 3.21 | 3.27 | 3.97 | 4.06 | 4.29 | 3.62 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1101 | 221 | 192 | 156 | 108 | 57 | 15 | 1 | 0 | 0 | 16 | 103 | 232 | 5157 | 248 | 232 | 318 | 358 | 435 | 493 | 622 | 676 | 634 | 540 | 367 | 234 | 784 | 3 | 4 | 9 | 17 | 27 | 58 | 158 | 211 | 184 | 91 | 21 | 1 | 2415 | 37 | 40 | 72 | 109 | 105 | 67 | 271 | 548 | 614 | 386 | 154 | 12 | 469 | 2 | 6 | 15 | 27 | 36 | 10 | 21 | 70 | 126 | 114 | 42 | 0 | 5.9 | 4.7 | 5.7 | 6.1 | 6.9 | 6.9 | 6.8 | 6.5 | 6.4 | 6.2 | 5.2 | 4.5 | 4.5 | 8.7 | 1.7 | 1.6 | 1.6 | 0.7 | 0.2 | 0 | 0 | 0 | 0.2 | 0.3 | 1.2 | 1.3 | 19.9 | 6.1 | 6.9 | 6.3 | 2.9 | 1.3 | 0.7 | 0.1 | 0.3 | 1.4 | 2 | 5.7 | 5.6 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 3.9 | 1.7 | 1.7 | 1.6 | 0.8 | 0.3 | 0.1 | 0 | 0 | 0.4 | 0.4 | 1.3 | 1.2 | 78.5 | 79.8 | 81.6 | 83.9 | 84.9 | 80.4 | 82.4 | 85.7 | 88.9 | 88.9 | 85.7 | 75.6 | 54.4 | 55.3 | 58 | 57.2 | 58.6 | 66.8 | 69.7 | 69.6 | 69 | 62.2 | 59.2 | 52.9 | 73.6 | 73.2 | 74.6 | 76.4 | 75.2 | 75.3 | 79.3 | 81.8 | 83.3 | 83 | 78.1 | 70.9 | 53.2 | 54.3 | 55.7 | 57.4 | 61.9 | 65.8 | 68.8 | 69.7 | 68.7 | 61.3 | 56.5 | 53.7 | 69.5 | 68.6 | 69.8 | 71.5 | 70.9 | 72.5 | 76.9 | 79 | 80 | 77.8 | 73.2 | 67.3 | 53.6 | 54.3 | 56.3 | 58 | 61.7 | 64.4 | 68.1 | 69.1 | 69.1 | 62.5 | 56.3 | 54.2 | 65.5 | 65 | 66.4 | 68 | 68.4 | 70.9 | 74.9 | 76.9 | 77.3 | 74 | 69.5 | 64.7 | 53.8 | 54.7 | 56.4 | 58.3 | 60.6 | 63.3 | 67.2 | 68.3 | 68.3 | 63.2 | 57.7 | 54.9 | 60.9 | 61.2 | 62.2 | 63.4 | 66.1 | 68.4 | 71.9 | 72.8 | 73.3 | 70.3 | 64.9 | 62.2 | 64.6 | 66.4 | 70.1 | 70.3 | 73.1 | 76 | 79.3 | 81.2 | 81.6 | 77.6 | 69.8 | 65.6 | 59.3 | 59.5 | 60.2 | 61.7 | 64.2 | 66.8 | 69.9 | 71.2 | 71.7 | 67.9 | 63.1 | 60.2 | 63.6 | 64.6 | 67.1 | 68.9 | 70.7 | 73.6 | 76.6 | 78.2 | 78.7 | 74.6 | 68.1 | 64.2 | 58.2 | 58.3 | 59.1 | 60.3 | 62.8 | 65.5 | 68.9 | 70.1 | 70.5 | 66.3 | 61.8 | 58.9 | 62.6 | 63.4 | 65.3 | 67.2 | 68.8 | 71.6 | 75.1 | 76.7 | 77.1 | 72.6 | 67 | 63 | 57.1 | 57.2 | 58.1 | 59.3 | 61.7 | 64.2 | 67.9 | 69.2 | 69.3 | 64.9 | 60.4 | 57.5 | 61.9 | 62.3 | 63.9 | 65.8 | 67.4 | 70 | 73.9 | 75.4 | 75.6 | 71 | 65.9 | 61.8 | 14.5 | 12.8 | 11.3 | 10.4 | 8 | 7.6 | 8 | 8.6 | 9.5 | 11.5 | 13.9 | 14.5 | 22.1 | 20.7 | 19.3 | 18.7 | 12.8 | 10.7 | 10.3 | 11.4 | 14.2 | 20.4 | 22.2 | 20.1 | 11.1 | 10.4 | 9.5 | 9 | 6 | 4.6 | 4.2 | 4.7 | 6.2 | 11.6 | 12.4 | 11.9 | 13.5 | 13.1 | 12.4 | 13.3 | 10.7 | 11.2 | 9.8 | 10.9 | 12.3 | 14.1 | 14.5 | 13.1 | 8.7 | 7.9 | 7 | 6.9 | 5.2 | 4.8 | 4.2 | 4.6 | 5.6 | 8.6 | 9.4 | 8.7 | 0.317 | 0.328 | 0.341 | 0.352 | 0.372 | 0.371 | 0.4 | 0.399 | 0.365 | 0.372 | 0.325 | 0.328 | 2.55 | 2.532 | 2.479 | 2.453 | 2.418 | 2.424 | 2.426 | 2.408 | 2.479 | 2.432 | 2.555 | 2.545 | 288 | 295 | 298 | 297 | 290 | 289 | 280 | 279 | 286 | 275 | 282 | 277 | 26 | 29 | 33 | 36 | 37 | 37 | 37 | 37 | 33 | 32 | 26 | 25 | 1048 | 1324 | 1731 | 2086 | 2179 | 2260 | 2220 | 2145 | 1857 | 1451 | 1137 | 949 | 64 | 110 | 97 | 115 | 166 | 146 | 150 | 95 | 104 | 106 | 77 | 67 | 0.95 | N/A | -2.65 | 1.69 | N/A | N/A | N/A | -185 | 338 | 162 | 1.15 | N/A | -2.86 | 1.37 | N/A | N/A | N/A | -189 | 414 | 214 | 39
| MONTGOMERY-GIBBS_STYP20 | 7 | 4 | USA | CA | MONTGOMERY-GIBBS | 722903 | 03131 | 32.816 | -117.139 | 417 | 14.48 | -8 | NAP | 98-19 | 3B | 12 | 40.8 | 43.1 | 11.5 | 10 | 63.8 | 16.6 | 12.9 | 63.1 | 18.8 | 58.7 | 16.7 | 58.5 | 1.6 | 110 | 0.365 | 8 | 14.6 | 90.8 | 65.6 | 87.2 | 64.8 | 83.9 | 65 | 71.4 | 83 | 70.2 | 80.8 | 69 | 78.8 | 8.7 | 300 | 67.8 | 103.6 | 76.5 | 66.3 | 98.2 | 75.2 | 65.2 | 94.8 | 74.1 | 35.5 | 83 | 34.3 | 80.9 | 33.4 | 79.2 | 76.5 | 15.8 | 12.9 | 11.9 | 36.5 | 99.5 | 1.9 | 4.4 | 35.2 | 102.7 | 34.1 | 105.3 | 33 | 107.8 | 31.7 | 111 | 31.1 | 73.7 | 2 | 1.8 | 29.7 | 75 | 28.5 | 76.1 | 27.4 | 77.1 | 25.9 | 78.4 | 63.9 | 56.9 | 56.7 | 58.9 | 60.9 | 63.5 | 66.9 | 71.6 | 73.1 | 72 | 67.5 | 61.7 | 56.3 | 7.61 | 5.28 | 4.99 | 4.72 | 4.93 | 4.09 | 3.78 | 4.07 | 4.02 | 5.07 | 5.28 | 5.33 | 4.67 | 10 | 4 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1359 | 256 | 238 | 199 | 141 | 75 | 18 | 1 | 0 | 1 | 30 | 128 | 272 | 5076 | 219 | 189 | 276 | 328 | 419 | 508 | 670 | 716 | 659 | 542 | 351 | 199 | 950 | 6 | 5 | 10 | 19 | 29 | 76 | 206 | 251 | 210 | 107 | 28 | 3 | 5841 | 107 | 101 | 146 | 238 | 233 | 288 | 907 | 1330 | 1301 | 816 | 318 | 56 | 1798 | 12 | 19 | 37 | 78 | 87 | 75 | 217 | 374 | 477 | 315 | 101 | 6 | 5.1 | 4.3 | 5 | 5.3 | 6 | 6 | 5.7 | 5.4 | 5.3 | 5.3 | 4.7 | 4.2 | 4.2 | 10.6 | 2 | 2 | 2 | 0.9 | 0.2 | 0.1 | 0 | 0 | 0.2 | 0.4 | 1.3 | 1.4 | 28.1 | 8.9 | 11.8 | 7.7 | 3.9 | 1.3 | 0.7 | 0.5 | 1.4 | 1.3 | 2.6 | 5.7 | 4.7 | 2.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9 | 2.1 | 2.4 | 2 | 1 | 0.3 | 0.2 | 0.1 | 0.2 | 0.3 | 0.6 | 1.4 | 1.2 | 81.8 | 82.9 | 85.1 | 88.2 | 89.7 | 88.1 | 90.3 | 92.5 | 96.6 | 94.4 | 88.5 | 80.4 | 55.6 | 55.9 | 59.1 | 57.4 | 58.9 | 67.2 | 69.1 | 69.3 | 68.3 | 62.8 | 58.4 | 54 | 77 | 76.9 | 77.8 | 80.6 | 80.5 | 80.8 | 85 | 87.9 | 90 | 88 | 82.4 | 74.2 | 53.7 | 54.2 | 56.3 | 57.1 | 60.3 | 66.4 | 69.2 | 69 | 68.3 | 60.1 | 57 | 52.9 | 72.6 | 71.9 | 72.5 | 74.7 | 73.7 | 76.6 | 81.9 | 83.8 | 85.3 | 82.5 | 76.8 | 70.4 | 52.9 | 53.8 | 55.6 | 56.9 | 61.1 | 64.8 | 68.3 | 69 | 67.7 | 60.5 | 55.6 | 52.4 | 67.8 | 66.3 | 68.1 | 70 | 70.3 | 73.5 | 79 | 81 | 81.4 | 77.8 | 72.3 | 65.9 | 51.9 | 53 | 55.9 | 57.4 | 60.1 | 63.6 | 67.5 | 68 | 66.7 | 61.1 | 55.3 | 52.7 | 60.1 | 60.5 | 62.2 | 63.1 | 65.7 | 69 | 72.5 | 73.1 | 73.4 | 70 | 63 | 61 | 70 | 68.8 | 75.4 | 76.8 | 78 | 82.6 | 84.1 | 86.2 | 88.7 | 79.1 | 71.8 | 68 | 58.4 | 58.3 | 60.2 | 60.7 | 63.5 | 67 | 70.7 | 71.2 | 71.5 | 67.2 | 61.4 | 59 | 66.2 | 67.4 | 71 | 72.6 | 74.2 | 78.8 | 81.3 | 82.8 | 83.6 | 77.3 | 71.3 | 65 | 56.9 | 56.8 | 58.8 | 59.4 | 62 | 65.4 | 69.3 | 69.9 | 70 | 65.3 | 60.1 | 57.3 | 64 | 65.3 | 67.7 | 69.4 | 71.3 | 75.2 | 79.4 | 80.4 | 80 | 74.8 | 68.9 | 62.9 | 55.4 | 55.4 | 57.2 | 58.1 | 60.5 | 64.2 | 68.1 | 68.8 | 68.5 | 63.9 | 58.9 | 55.8 | 62.7 | 63.2 | 64.5 | 66.5 | 68 | 72.9 | 77.2 | 78.5 | 77.6 | 71.9 | 67.1 | 61.6 | 19.7 | 18.1 | 16.6 | 15.7 | 12.7 | 12.7 | 13.6 | 14.6 | 15.6 | 17.3 | 19.3 | 19.2 | 27.8 | 28.1 | 26.2 | 26.5 | 21.2 | 18.2 | 17.6 | 19.2 | 22.4 | 27.9 | 27.9 | 27 | 12.6 | 12.7 | 11.6 | 11.4 | 9 | 7 | 6.6 | 7.1 | 8 | 11.9 | 12.6 | 13.5 | 18.6 | 19.7 | 19.1 | 19.1 | 16.9 | 17 | 16.2 | 17.1 | 18.6 | 19.3 | 19.5 | 17.4 | 10.2 | 10.3 | 9.4 | 8.9 | 7.5 | 6.9 | 6.4 | 6.6 | 7.2 | 8.7 | 10.1 | 9.8 | 0.311 | 0.322 | 0.334 | 0.345 | 0.364 | 0.364 | 0.392 | 0.393 | 0.359 | 0.365 | 0.319 | 0.322 | 2.556 | 2.541 | 2.489 | 2.464 | 2.43 | 2.436 | 2.435 | 2.414 | 2.488 | 2.44 | 2.562 | 2.552 | 290 | 297 | 300 | 299 | 292 | 291 | 282 | 281 | 288 | 277 | 284 | 279 | 26 | 29 | 33 | 35 | 37 | 36 | 36 | 36 | 33 | 32 | 26 | 25 | 1049 | 1324 | 1740 | 2099 | 2210 | 2307 | 2251 | 2166 | 1872 | 1461 | 1141 | 950 | 65 | 113 | 96 | 111 | 161 | 141 | 145 | 91 | 98 | 104 | 74 | 67 | 1.98 | N/A | N/A | 3.2 | N/A | N/A | N/A | -364 | 729 | 347 | 1.19 | N/A | -2.9 | 1.35 | N/A | N/A | N/A | -193 | 423 | 223 | 41
| BROWN-FIELD_STYP20 | 7 | 4 | USA | CA | BROWN FIELD | 722904 | 03178 | 32.572 | -116.979 | 515 | 14.42 | -8 | NAP | 97-19 | 3C | 12 | 39.1 | 41.8 | 7.9 | 8.4 | 61.8 | 13.2 | 10.9 | 62.2 | 20.5 | 61.1 | 18.3 | 60.5 | 6 | 120 | 0.378 | 8 | 15.8 | 89.9 | 64.3 | 85.8 | 64.6 | 82.4 | 64.8 | 71.5 | 82.3 | 70.1 | 79.9 | 68.9 | 77.8 | 8.4 | 290 | 68 | 105 | 75.3 | 66.5 | 99.5 | 74.2 | 65.6 | 96.3 | 73.5 | 35.5 | 82.5 | 34.4 | 79.9 | 33.3 | 78.1 | 77.7 | 16.2 | 12.9 | 11.9 | 34.6 | 98.3 | 2.4 | 3.5 | 32.9 | 100.8 | 31.5 | 102.8 | 30.1 | 104.8 | 28.4 | 107.4 | 29.7 | 73.5 | 2.5 | 1.9 | 27.9 | 74.9 | 26.4 | 76 | 25 | 77 | 23.2 | 78.4 | 62.7 | 56.2 | 55.5 | 57.7 | 59.8 | 62.8 | 66 | 70 | 71 | 70.5 | 66.3 | 60.9 | 55.6 | 7.34 | 5.58 | 5.18 | 4.67 | 4.7 | 3.98 | 3.45 | 3.63 | 3.61 | 4.8 | 5.09 | 5.63 | 4.9 | 23 | 8 | 6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 1557 | 279 | 269 | 235 | 169 | 91 | 23 | 1 | 1 | 4 | 41 | 152 | 292 | 4669 | 199 | 162 | 239 | 294 | 397 | 479 | 619 | 652 | 614 | 505 | 327 | 182 | 730 | 6 | 5 | 8 | 13 | 23 | 52 | 155 | 188 | 169 | 81 | 28 | 2 | 4630 | 99 | 88 | 136 | 206 | 220 | 209 | 661 | 914 | 1028 | 696 | 329 | 44 | 1354 | 15 | 19 | 41 | 69 | 84 | 53 | 133 | 216 | 338 | 271 | 111 | 4 | 5.2 | 5.4 | 5.9 | 5.3 | 5.8 | 5.6 | 5.1 | 4.7 | 4.5 | 4.5 | 4.8 | 5.1 | 5.5 | 12 | 1.9 | 2.5 | 1.7 | 1 | 0.3 | 0 | 0.1 | 0.1 | 0.2 | 0.6 | 1.2 | 2 | 22.4 | 5 | 10.1 | 3.7 | 2 | 1.6 | 0.2 | 0.9 | 0.2 | 1.2 | 5.6 | 3.5 | 6.3 | 6.4 | 0.2 | 0.1 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.1 | 4.3 | 1.6 | 2.3 | 0.9 | 0.6 | 0.4 | 0 | 0.2 | 0.1 | 0.3 | 1.3 | 0.6 | 1.6 | 82 | 82.8 | 85.2 | 87.9 | 90 | 86.9 | 88.2 | 90.7 | 95.1 | 93.8 | 89.1 | 79.1 | 55.4 | 56.1 | 57.8 | 57.2 | 59.4 | 67 | 70.4 | 69.3 | 67.8 | 61.8 | 57.6 | 53.5 | 76.5 | 75.9 | 77.1 | 80.1 | 80.1 | 79 | 83.5 | 85.3 | 88.1 | 87.5 | 83 | 73.5 | 53.8 | 54.6 | 56.2 | 57.8 | 61.7 | 66.6 | 69.6 | 69.5 | 68.7 | 60.2 | 56.7 | 52.3 | 72.2 | 70.4 | 71.7 | 73.5 | 73.4 | 75.2 | 80.4 | 81.8 | 83.5 | 81.6 | 76.9 | 70 | 52.7 | 53.4 | 56.2 | 57.6 | 61.4 | 64.8 | 68.4 | 69.1 | 68.2 | 60.3 | 55 | 52 | 67.3 | 65.4 | 67 | 69.4 | 70.4 | 72.9 | 77.4 | 79.1 | 80 | 76.4 | 71.9 | 65.6 | 51.9 | 53.1 | 56.1 | 58 | 60.5 | 63.5 | 67.3 | 68.1 | 67.3 | 60.6 | 54.6 | 52.4 | 60.2 | 60.4 | 62.2 | 63.1 | 66.5 | 69.3 | 72.9 | 72.9 | 73.5 | 69.4 | 63.3 | 61.2 | 68.4 | 67.7 | 74.2 | 75.5 | 77.9 | 82.2 | 82.8 | 85.1 | 86.6 | 77.4 | 72.7 | 67.3 | 58.4 | 58.2 | 60.1 | 61.4 | 64.2 | 67 | 70.7 | 71 | 71.7 | 66.8 | 61.3 | 58.8 | 65.9 | 66.8 | 69.7 | 72.6 | 74.2 | 77.8 | 80.6 | 82.1 | 82.7 | 75.9 | 70.6 | 64.3 | 56.9 | 56.8 | 58.7 | 59.8 | 62.4 | 65.6 | 69.2 | 69.5 | 70.1 | 65 | 59.8 | 57.2 | 64.1 | 65.2 | 67.2 | 69.3 | 71.4 | 74.4 | 78.5 | 79.4 | 78.8 | 73.8 | 68.3 | 62.5 | 55.4 | 55.3 | 57.3 | 58.4 | 60.9 | 64.2 | 68 | 68.5 | 68.6 | 63.5 | 58.6 | 55.5 | 62.4 | 63.4 | 64.6 | 66.7 | 68.8 | 72.1 | 76.2 | 77.4 | 76.4 | 71.3 | 66.6 | 61.2 | 20.5 | 19 | 18.6 | 18 | 15.2 | 14.4 | 15 | 15.8 | 17.1 | 18.9 | 20.6 | 20.2 | 27.7 | 28.1 | 28.1 | 27.3 | 22 | 17.8 | 18.5 | 19.7 | 22.9 | 28.7 | 28.8 | 26.8 | 14 | 14.1 | 14 | 13.3 | 10.2 | 7.8 | 7.3 | 7.6 | 9.3 | 14 | 14.1 | 14.4 | 19.4 | 20.8 | 20.8 | 20.5 | 18.8 | 17.5 | 17.1 | 17.9 | 19 | 20 | 20.9 | 18.2 | 11.9 | 12 | 11.5 | 10.6 | 8.9 | 8 | 6.9 | 7.1 | 7.8 | 10.3 | 12 | 11.3 | 0.31 | 0.321 | 0.332 | 0.344 | 0.363 | 0.365 | 0.394 | 0.396 | 0.359 | 0.365 | 0.32 | 0.322 | 2.556 | 2.539 | 2.491 | 2.462 | 2.428 | 2.424 | 2.429 | 2.402 | 2.483 | 2.437 | 2.554 | 2.549 | 291 | 298 | 301 | 300 | 293 | 290 | 282 | 280 | 288 | 277 | 285 | 279 | 26 | 29 | 33 | 35 | 37 | 37 | 36 | 37 | 33 | 32 | 26 | 25 | 1063 | 1335 | 1753 | 2117 | 2235 | 2339 | 2249 | 2161 | 1883 | 1479 | 1153 | 963 | 66 | 111 | 97 | 109 | 162 | 134 | 147 | 99 | 101 | 105 | 72 | 66 | 1.53 | N/A | N/A | 2.59 | 1.37 | 1.26 | N/A | -342 | 565 | 252 | 1.19 | N/A | -2.9 | 1.39 | N/A | N/A | N/A | -191 | 419 | 227 | 33
| NORTH-ISLAND-NAS_STYP20 | 7 | 4 | USA | CA | NORTH ISLAND NAS | 722906 | 93112 | 32.7 | -117.2 | 26 | 14.68 | -8 | NAP | 94-19 | 3B | 12 | 44.9 | 46.3 | 21.1 | 15.9 | 65 | 26.5 | 20.5 | 63.8 | 24.4 | 59.1 | 20.8 | 58.9 | 2.2 | 90 | 0.366 | 8 | 8.8 | 85.1 | 63.8 | 81.5 | 65.1 | 79.1 | 65.8 | 71.4 | 77.9 | 70.3 | 76.7 | 69.3 | 75.5 | 9 | 320 | 69.5 | 108.5 | 74.9 | 67.9 | 102.8 | 74.2 | 66.5 | 97.6 | 73.3 | 35.2 | 78.5 | 34.3 | 76.7 | 33.3 | 75.9 | 80.6 | 18.7 | 16.5 | 14.6 | 40.3 | 93.6 | 2 | 5.4 | 38.9 | 97.5 | 37.8 | 100.7 | 36.7 | 103.8 | 35.2 | 107.7 | 35 | 73.7 | 2.3 | 2.2 | 33.4 | 75.3 | 32 | 76.6 | 30.7 | 77.9 | 29 | 79.5 | 64.2 | 58.1 | 58.5 | 60.2 | 61.8 | 64.2 | 66.6 | 70.1 | 71.7 | 71.2 | 67.5 | 62.4 | 57.7 | 6.26 | 4.47 | 4.07 | 4.02 | 4.06 | 3.58 | 2.98 | 3.1 | 3.1 | 3.97 | 3.95 | 4.65 | 3.79 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1093 | 218 | 188 | 159 | 111 | 56 | 15 | 1 | 0 | 1 | 14 | 103 | 227 | 5187 | 253 | 237 | 317 | 355 | 440 | 497 | 623 | 674 | 635 | 543 | 372 | 241 | 801 | 5 | 5 | 11 | 17 | 30 | 61 | 158 | 209 | 186 | 92 | 25 | 2 | 2473 | 71 | 51 | 80 | 126 | 119 | 59 | 270 | 515 | 605 | 380 | 173 | 24 | 513 | 9 | 7 | 17 | 42 | 51 | 9 | 15 | 62 | 127 | 119 | 53 | 2 | 6.3 | 5.4 | 6.5 | 6.6 | 7.3 | 7.1 | 6.9 | 6.7 | 6.8 | 6.7 | 5.7 | 5.2 | 5.3 | 8.7 | 1.7 | 1.6 | 1.6 | 0.7 | 0.2 | 0 | 0 | 0 | 0.2 | 0.3 | 1.2 | 1.3 | 19.9 | 6.1 | 6.9 | 6.3 | 2.9 | 1.3 | 0.7 | 0.1 | 0.3 | 1.4 | 2 | 5.7 | 5.6 | 2.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 3.9 | 1.7 | 1.7 | 1.6 | 0.8 | 0.3 | 0.1 | 0 | 0 | 0.4 | 0.4 | 1.3 | 1.2 | 80.9 | 80.2 | 82.2 | 85.5 | 87 | 79.3 | 82.2 | 85.1 | 89 | 89.8 | 86.6 | 77.5 | 57.4 | 56.7 | 57.6 | 59.2 | 59 | 67.4 | 69.9 | 69.6 | 70.1 | 61.7 | 58.7 | 53.8 | 75.1 | 73.7 | 74.6 | 76.5 | 74.9 | 75.1 | 79.2 | 81.2 | 83.1 | 82.8 | 78.8 | 71.7 | 55.4 | 55.1 | 56.7 | 57.9 | 62.6 | 65 | 68.8 | 69.6 | 68.9 | 60.6 | 57.9 | 54.1 | 70 | 68.5 | 70.1 | 71.5 | 71.4 | 73.1 | 77 | 78.9 | 79.7 | 77.5 | 73 | 67.8 | 54.9 | 55.6 | 57.2 | 58.8 | 61.8 | 63.9 | 67.9 | 68.9 | 69.1 | 62.8 | 57.6 | 55.4 | 65.7 | 65 | 66.5 | 68 | 69 | 71.4 | 75.1 | 76.6 | 77.1 | 73.8 | 69.7 | 64.9 | 55 | 55.4 | 57 | 58.2 | 60.7 | 63.3 | 67 | 67.9 | 68.1 | 63.5 | 58.5 | 55.5 | 62.9 | 61.7 | 62.2 | 63.3 | 66.6 | 69.1 | 72.2 | 72.2 | 73.3 | 70.6 | 64.8 | 62.4 | 66.7 | 66.8 | 69.4 | 70.7 | 73.2 | 75.2 | 78.5 | 79.2 | 81.8 | 76.5 | 70.1 | 65.9 | 60.3 | 59.6 | 60.5 | 61.7 | 64.4 | 66.9 | 70.1 | 70.9 | 71.8 | 68 | 63.2 | 60.4 | 64.3 | 65.6 | 67.4 | 69.3 | 70.2 | 73 | 76.3 | 77.6 | 78.6 | 74.2 | 68.4 | 64.5 | 58.9 | 58.5 | 59.4 | 60.4 | 63.1 | 65.4 | 69 | 69.9 | 70.7 | 66.3 | 62 | 59.2 | 63.7 | 64.2 | 65.8 | 67.5 | 68.6 | 71.1 | 75 | 76.5 | 77 | 72.3 | 67.6 | 63.5 | 57.5 | 57.4 | 58.4 | 59.4 | 61.9 | 64.1 | 68 | 69 | 69.4 | 64.9 | 60.8 | 57.8 | 62.5 | 62.9 | 64.6 | 66.1 | 67.3 | 69.7 | 73.7 | 75.3 | 75.5 | 70.7 | 66.7 | 62.5 | 15.4 | 13.7 | 11.9 | 11.2 | 8.8 | 7.9 | 8.3 | 8.8 | 10 | 12.4 | 14.8 | 15.5 | 23.9 | 21.4 | 19.4 | 19.2 | 13.4 | 10.5 | 10.7 | 11.4 | 14.4 | 21.6 | 22.7 | 21.4 | 10.5 | 9.8 | 8.9 | 8.6 | 6.2 | 4.9 | 4.5 | 4.7 | 5.8 | 9.6 | 10.6 | 11.1 | 14.1 | 13.7 | 12.9 | 13.8 | 11.3 | 10.7 | 10 | 10.6 | 12.6 | 14.1 | 15.1 | 13.3 | 9.1 | 8 | 7.2 | 7.3 | 6.3 | 5.3 | 4.7 | 4.8 | 5.3 | 7.4 | 9 | 9.1 | 0.316 | 0.327 | 0.34 | 0.351 | 0.371 | 0.37 | 0.399 | 0.397 | 0.364 | 0.37 | 0.324 | 0.327 | 2.554 | 2.536 | 2.483 | 2.456 | 2.421 | 2.426 | 2.429 | 2.413 | 2.482 | 2.443 | 2.559 | 2.551 | 288 | 295 | 298 | 297 | 290 | 289 | 280 | 280 | 286 | 276 | 283 | 277 | 26 | 29 | 33 | 36 | 37 | 37 | 36 | 36 | 33 | 32 | 26 | 25 | 1048 | 1324 | 1728 | 2081 | 2166 | 2240 | 2206 | 2136 | 1850 | 1447 | 1135 | 949 | 63 | 109 | 98 | 117 | 168 | 147 | 153 | 97 | 106 | 107 | 78 | 67 | 1.06 | N/A | N/A | 1.93 | N/A | N/A | N/A | N/A | N/A | N/A | 1.15 | N/A | -2.86 | 1.37 | N/A | N/A | N/A | -189 | 414 | 214 | 38
; | SAN-DIEGO-GILLESPIE_STYP20 | 10 |  |  |  | SAN DIEGO - GILLESPIE | 722907
| IMPERIAL-BEACH-NOLF_STYP20 | 7 | 4 | USA | CA | IMPERIAL BEACH NOLF | 722909 | 93115 | 32.567 | -117.117 | 24 | 14.68 | -8 | NAP | 07-19 | 3C | 12 | 42.3 | 44.1 | 14.7 | 11.6 | 62.7 | 20.5 | 15.4 | 59.4 | 24.4 | 58.5 | 20.9 | 59.2 | 6 | 90 | 0.393 | 8 | 10.5 | 85.9 | 64.5 | 81.4 | 65.7 | 78.7 | 65.6 | 71.8 | 79.8 | 70.4 | 77.7 | 69.3 | 76 | 8.7 | 300 | 68.9 | 106.1 | 75.7 | 67.6 | 101.6 | 75.2 | 66.4 | 97.5 | 74.1 | 35.5 | 80.1 | 34.4 | 77.8 | 33.4 | 76.2 | 79.9 | 18.7 | 16.5 | 14.8 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 62.5 | 57.1 | 56.5 | 57.8 | 59.8 | 62.2 | 65.5 | 68.8 | 69.8 | 68.9 | 65.3 | 61 | 56.1 | 6.41 | 4.12 | 4.5 | 4.05 | 3.57 | 3.46 | 3.28 | 3.14 | 4.49 | 5.48 | 4.61 | 4.21 | 3.92 | 5 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1496 | 248 | 241 | 227 | 162 | 101 | 30 | 5 | 6 | 16 | 50 | 134 | 276 | 4550 | 221 | 184 | 243 | 294 | 378 | 464 | 584 | 615 | 568 | 476 | 331 | 192 | 566 | 2 | 4 | 5 | 6 | 14 | 44 | 124 | 156 | 134 | 61 | 15 | 1 | 2370 | 45 | 62 | 67 | 72 | 103 | 68 | 191 | 541 | 619 | 394 | 190 | 18 | 570 | 3 | 15 | 19 | 18 | 35 | 8 | 16 | 104 | 197 | 95 | 59 | 1 | 6.6 | 6.5 | 7 | 6.7 | 7.2 | 7.4 | 7 | 6.7 | 6.4 | 6.1 | 5.8 | 6.2 | 6.8 | 7.5 | 1.4 | 0.9 | 1.5 | 0.6 | 0.2 | 0.1 | 0 | 0 | 0.1 | 0.2 | 1.4 | 1.1 | 16.7 | 5.8 | 3.1 | 5.4 | 3.2 | 1.1 | 0.5 | 0.1 | 0.1 | 1.5 | 0.8 | 6.4 | 4.4 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1 | 1.3 | 0.9 | 1.3 | 0.8 | 0.2 | 0.2 | 0 | 0 | 0.3 | 0.2 | 1.4 | 1.1 | 79.3 | 81.9 | 81.5 | 82.4 | 85.4 | 80.3 | 81.4 | 87.2 | 95.3 | 88.3 | 87.7 | 76.6 | 53.9 | 55.7 | 57.9 | 57.7 | 60.1 | 68 | 69.9 | 71.3 | 72 | 63.3 | 57.5 | 51.4 | 73.8 | 74 | 73.4 | 74.5 | 75.3 | 75.3 | 78.1 | 81.5 | 84.6 | 82.2 | 78.7 | 71.1 | 52.9 | 54.4 | 56.8 | 57.8 | 60.2 | 65 | 69.1 | 70.2 | 68.7 | 63 | 56.9 | 53.7 | 69.7 | 68.9 | 68.3 | 70.2 | 70.2 | 72.9 | 76 | 78.6 | 79.5 | 78.1 | 74.2 | 67.2 | 53.3 | 55.6 | 57.6 | 58.7 | 60.7 | 64.1 | 67.7 | 68.9 | 70 | 64.6 | 56.5 | 54.6 | 65.9 | 65.5 | 65.7 | 67.5 | 68 | 71.1 | 74.3 | 76.6 | 76.8 | 74.9 | 70.2 | 64.8 | 54.5 | 55.9 | 57.2 | 58.7 | 59.8 | 63.1 | 66.6 | 68.1 | 68.9 | 64.4 | 57.6 | 54.9 | 60.5 | 62 | 62.7 | 63.6 | 65.4 | 68.3 | 72 | 73.3 | 74.1 | 71.8 | 64.4 | 61.7 | 64.9 | 66.9 | 69.3 | 71.3 | 73.2 | 78 | 80.1 | 83.1 | 86.7 | 79.3 | 70.7 | 65.6 | 59.5 | 59.9 | 60.9 | 61.4 | 63.1 | 66.4 | 70 | 71.1 | 72.3 | 69.2 | 62.5 | 60 | 64.4 | 66 | 68.4 | 68.6 | 69.9 | 73.9 | 76.5 | 79.1 | 80.6 | 76.6 | 68.9 | 64.5 | 58.4 | 58.5 | 59.5 | 60.3 | 61.6 | 65.2 | 68.8 | 69.7 | 70.9 | 67.3 | 61.4 | 58.7 | 63.4 | 64.9 | 65.4 | 67.4 | 68.3 | 71.5 | 74.7 | 77.2 | 78.3 | 75.4 | 68.4 | 63.4 | 57.2 | 57.2 | 58.3 | 59.3 | 60.3 | 64 | 67.6 | 68.8 | 69.6 | 65.5 | 60.1 | 57.1 | 62.4 | 63.6 | 63.9 | 66.4 | 66.6 | 70.1 | 73.1 | 75.7 | 75.9 | 72.7 | 67.3 | 62.3 | 17.8 | 16.9 | 15 | 14.8 | 11.5 | 9.4 | 9.4 | 10.5 | 13.5 | 16.7 | 18.8 | 17.8 | 25.8 | 25.6 | 21.1 | 22.9 | 16.3 | 11.8 | 11.6 | 13.1 | 17.2 | 23.5 | 27.2 | 23 | 13.6 | 14.2 | 12.3 | 13.2 | 8.8 | 6.5 | 5.9 | 6.3 | 8.1 | 13.4 | 15.3 | 14.4 | 16 | 19.6 | 16.3 | 17.8 | 14.1 | 11.7 | 11.7 | 12.8 | 14.9 | 18.8 | 19.2 | 16.1 | 11 | 12.6 | 10.5 | 10.7 | 8 | 6.6 | 6 | 6.5 | 7.4 | 11.7 | 13.1 | 11.5 | 0.315 | 0.327 | 0.339 | 0.352 | 0.372 | 0.373 | 0.4 | 0.399 | 0.366 | 0.368 | 0.324 | 0.326 | 2.556 | 2.537 | 2.486 | 2.453 | 2.417 | 2.417 | 2.424 | 2.406 | 2.477 | 2.448 | 2.557 | 2.552 | 289 | 296 | 298 | 297 | 290 | 288 | 280 | 279 | 286 | 276 | 283 | 278 | 26 | 29 | 33 | 36 | 37 | 37 | 37 | 37 | 33 | 31 | 26 | 25 | 1055 | 1329 | 1734 | 2090 | 2176 | 2253 | 2201 | 2130 | 1853 | 1455 | 1141 | 956 | 64 | 108 | 98 | 116 | 169 | 143 | 155 | 102 | 108 | 108 | 78 | 67 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.17 | N/A | -2.83 | 1.4 | N/A | N/A | N/A | -189 | 414 | 220 | 35
; | SAN-NICHOLAS-ISLAND_STYP20 | 6 |  |  |  | SAN-NICHOLAS-ISLAND | 722910
| CATALINA_STYP20 | 7 | 4 | USA | CA | CATALINA | 722920 | 23191 | 33.405 | -118.416 | 1602 | 13.86 | -8 | NAP | 00-19 | 3C | 2 | 42.8 | 44.4 | 4.1 | 7.2 | 65.6 | 8.5 | 9 | 64.7 | 28.1 | 47.8 | 25.6 | 47.5 | 10.7 | 280 | 0.403 | 9 | 13.4 | 90.5 | 63 | 87.7 | 62.4 | 84.5 | 60.9 | 68.3 | 81.9 | 66.9 | 79.9 | 65.4 | 78.1 | 6.5 | 270 | 63.8 | 94 | 72.8 | 62.3 | 89.1 | 70.9 | 61 | 85 | 69.1 | 33.5 | 81.9 | 32.2 | 79.6 | 31 | 77.7 | 73.9 | 23.1 | 18.9 | 16.3 | 40.1 | 97.2 | 1.7 | 3.7 | 38.9 | 99.9 | 37.9 | 102.1 | 37 | 104.2 | 35.8 | 106.9 | 33.7 | 70.9 | 1.6 | 1.7 | 32.5 | 72.1 | 31.6 | 73.1 | 30.7 | 74 | 29.5 | 75.2 | 61.5 | 56.3 | 54.8 | 56.4 | 56.9 | 59.4 | 63.4 | 68.5 | 70.1 | 70.1 | 65.4 | 60.6 | 55.3 | 9.4 | 7.37 | 7.58 | 7.3 | 7.23 | 7.27 | 7.22 | 7.21 | 7.59 | 8.57 | 8.57 | 7.82 | 6.34 | 69 | 16 | 23 | 11 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 13 | 2183 | 286 | 303 | 290 | 268 | 215 | 117 | 41 | 27 | 38 | 103 | 183 | 312 | 4262 | 212 | 156 | 209 | 212 | 293 | 402 | 574 | 624 | 604 | 479 | 320 | 177 | 898 | 17 | 16 | 23 | 26 | 42 | 68 | 151 | 186 | 192 | 117 | 50 | 10 | 6799 | 18 | 31 | 85 | 162 | 307 | 580 | 1145 | 1584 | 1740 | 891 | 247 | 9 | 2087 | 0 | 0 | 9 | 36 | 87 | 206 | 331 | 492 | 626 | 257 | 43 | 0 | 7 | 7.8 | 8.4 | 8.3 | 8.3 | 7.1 | 5.6 | 5.3 | 5.5 | 6.1 | 6.8 | 7.2 | 7.9 | 11.6 | 2.2 | 2.4 | 1.6 | 0.7 | 0.3 | 0.1 | 0.1 | 0 | 0.2 | 0.6 | 1.1 | 2 | 27.4 | 7.9 | 7.5 | 3.7 | 1.8 | 1.1 | 0.3 | 0.6 | 0.1 | 1 | 3.5 | 2 | 7 | 5.1 | 0.2 | 0 | 0.5 | 0.2 | 0 | 0 | 0 | 0 | 0.2 | 0 | 0.2 | 0 | 6.1 | 2.5 | 2.1 | 1.1 | 0.6 | 0.3 | 0.1 | 0.2 | 0 | 0.2 | 1 | 0.6 | 2.1 | 76.7 | 77.9 | 81.3 | 84.6 | 88.1 | 92.8 | 92.9 | 92.8 | 95.2 | 91.1 | 84.9 | 75.1 | 51.5 | 53.1 | 56.3 | 56.3 | 60.4 | 62 | 66.9 | 62.8 | 64.5 | 60.6 | 56.5 | 51 | 73.3 | 73.9 | 75.7 | 78.8 | 81.7 | 85.7 | 86.9 | 88.3 | 90.2 | 86.2 | 80.3 | 71.8 | 50.7 | 51.2 | 53.6 | 55 | 57.9 | 61.4 | 64.7 | 63 | 63.1 | 58.8 | 54.7 | 49.9 | 70.6 | 70.9 | 72.3 | 73.6 | 76.6 | 80.7 | 83.3 | 85.2 | 86.8 | 82.3 | 76.6 | 68.4 | 49.4 | 50.2 | 52.4 | 52.8 | 56.4 | 60.6 | 62.8 | 62.1 | 62.3 | 57.2 | 53 | 48.4 | 67.9 | 67.6 | 68.4 | 69.2 | 72 | 75.7 | 80.5 | 82.2 | 83.1 | 79.2 | 73.1 | 65.5 | 48.5 | 48.8 | 50.7 | 51.9 | 55.1 | 59.2 | 62.3 | 60.9 | 60.5 | 55.6 | 51.6 | 47.7 | 58.1 | 58.5 | 59.7 | 61.5 | 63.9 | 67.4 | 70.2 | 70.1 | 69.8 | 65.7 | 60.5 | 58.3 | 64.6 | 63.9 | 71.2 | 75.4 | 80.4 | 84.9 | 85.7 | 83.5 | 85.6 | 77.6 | 68.1 | 61.7 | 55.7 | 56 | 57.3 | 58.2 | 61.2 | 64.4 | 68.2 | 68.1 | 67.5 | 63.5 | 58.8 | 56.4 | 60.9 | 62.6 | 67.6 | 70.4 | 74.8 | 79.5 | 81.4 | 81.2 | 80.7 | 74.7 | 66.7 | 60.4 | 54 | 53.9 | 55.5 | 56.2 | 59.4 | 62.7 | 66.6 | 66.3 | 65.7 | 61.7 | 57.1 | 54.6 | 60.3 | 62.1 | 65.1 | 66.9 | 70.6 | 75.2 | 78.6 | 79 | 79.9 | 72.3 | 64.9 | 59.3 | 52.3 | 52.3 | 54 | 54.5 | 57.5 | 61.3 | 65 | 64.7 | 63.9 | 60 | 55.7 | 53.1 | 59.3 | 60 | 62.7 | 63.1 | 66.3 | 72.2 | 76 | 76.6 | 76.6 | 69.5 | 64.2 | 57.8 | 9.6 | 9.8 | 11.4 | 12.3 | 12.1 | 13.5 | 14.6 | 14.3 | 13.4 | 11.7 | 10.6 | 9.1 | 12 | 13.7 | 15.2 | 17.9 | 17.5 | 18.4 | 17.2 | 15.2 | 16.1 | 14.8 | 13.3 | 12.4 | 7.4 | 8.7 | 9.5 | 10 | 10.4 | 11.1 | 11.7 | 11.9 | 10.5 | 9 | 7.5 | 7.5 | 10.4 | 11.9 | 13.9 | 15.7 | 15.8 | 17.1 | 16.5 | 15.2 | 15 | 13.8 | 12.2 | 10 | 8.7 | 9.2 | 9.8 | 9.9 | 9.8 | 10.5 | 11.3 | 11.7 | 11.1 | 10 | 8.7 | 8.4 | 0.291 | 0.304 | 0.32 | 0.323 | 0.337 | 0.339 | 0.352 | 0.341 | 0.326 | 0.324 | 0.292 | 0.292 | 2.638 | 2.618 | 2.548 | 2.538 | 2.523 | 2.512 | 2.54 | 2.555 | 2.597 | 2.587 | 2.659 | 2.658 | 298 | 304 | 305 | 306 | 300 | 298 | 293 | 297 | 298 | 292 | 295 | 292 | 23 | 27 | 31 | 33 | 34 | 34 | 33 | 32 | 29 | 27 | 23 | 22 | 1007 | 1289 | 1696 | 2071 | 2146 | 2121 | 2196 | 2115 | 1797 | 1380 | 1098 | 908 | 69 | 110 | 98 | 115 | 185 | 161 | 154 | 103 | 114 | 126 | 85 | 71 | 1.85 | N/A | N/A | N/A | 1.4 | 1.39 | N/A | N/A | N/A | N/A | 1.15 | N/A | -2.92 | 1.4 | N/A | N/A | N/A | -212 | 414 | 196 | 50
; | SAN-CLEMENTE-IS-NAAS_STYP20 | 6 |  |  |  | SAN-CLEMENTE-IS-NAAS | 722925
| CAMP-PENDLETON-MCAS_STYP20 | 7 | 4 | USA | CA | CAMP PENDLETON MCAS | 722926 | 03154 | 33.3 | -117.35 | 75 | 14.66 | -8 | NAP | 94-19 | 3C | 12 | 31.9 | 34.6 | 10.5 | 9.4 | 63 | 16.8 | 12.9 | 60.5 | 18.9 | 61.4 | 16.4 | 60.4 | 0.6 | 30 | 0.386 | 8 | 20 | 91.3 | 65 | 87.5 | 65 | 84 | 65.2 | 71.6 | 82.9 | 70.3 | 81.1 | 69.2 | 79.4 | 8.8 | 210 | 68 | 103.1 | 76 | 66.3 | 97.2 | 75.4 | 65.2 | 93.3 | 74.6 | 35.4 | 82.8 | 34.3 | 81.2 | 33.3 | 79.5 | 87.1 | 15 | 12.7 | 11.7 | 27.2 | 101 | 3 | 3 | 25 | 103.1 | 23.3 | 104.9 | 21.6 | 106.6 | 19.4 | 108.7 | 25.1 | 75.1 | 3.1 | 3.6 | 22.8 | 77.7 | 21 | 79.8 | 19.2 | 81.9 | 17 | 84.5 | 61.4 | 54.2 | 54.2 | 56.7 | 58.5 | 62.4 | 66 | 69.7 | 70.7 | 69.4 | 64 | 58 | 53.1 | 7.62 | 5.25 | 4.91 | 4.4 | 4.39 | 3.73 | 3.26 | 3.58 | 3.95 | 4.85 | 4.58 | 4.9 | 4.84 | 60 | 16 | 14 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 23 | 1904 | 336 | 303 | 260 | 200 | 98 | 24 | 4 | 6 | 11 | 75 | 218 | 369 | 4238 | 147 | 133 | 210 | 257 | 384 | 479 | 611 | 641 | 582 | 433 | 241 | 120 | 607 | 2 | 2 | 2 | 6 | 17 | 53 | 150 | 182 | 143 | 42 | 7 | 1 | 5829 | 154 | 108 | 176 | 280 | 261 | 294 | 850 | 1289 | 1235 | 766 | 354 | 62 | 1856 | 30 | 26 | 57 | 104 | 108 | 69 | 177 | 372 | 463 | 316 | 127 | 7 | 4 | 3.3 | 3.7 | 4 | 4.5 | 4.7 | 4.6 | 4.6 | 4.4 | 4.1 | 3.8 | 3.2 | 3.2 | 11.7 | 2.1 | 2.8 | 1.7 | 0.8 | 0.3 | 0.1 | 0.2 | 0 | 0.2 | 0.6 | 0.9 | 1.7 | 23.6 | 9.4 | 11.3 | 6.9 | 2.4 | 1.4 | 0.6 | 2.3 | 0.4 | 1.5 | 5.6 | 2.7 | 9.1 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2 | 2.4 | 2.4 | 1.7 | 0.7 | 0.4 | 0.2 | 0.5 | 0.1 | 0.3 | 1.1 | 0.8 | 1.8 | 84 | 84.1 | 87.2 | 90.3 | 91 | 87.8 | 88.7 | 92.6 | 98.2 | 95.3 | 90.4 | 80.5 | 56.6 | 57.9 | 59 | 60.5 | 60.2 | 67.7 | 70.4 | 67.7 | 68 | 63.4 | 59.4 | 55.5 | 78.5 | 77 | 78.7 | 81.8 | 80.8 | 80.4 | 84.2 | 87.6 | 90.1 | 88.6 | 83.8 | 74.9 | 55.4 | 55.6 | 57.5 | 59.1 | 63.3 | 67 | 69.5 | 69.3 | 68.9 | 60.8 | 57.6 | 53.9 | 73.3 | 71.3 | 72.7 | 74.8 | 74.5 | 76.9 | 81.3 | 83.8 | 85 | 82.1 | 77.2 | 70.5 | 54.2 | 54.9 | 57.4 | 58.3 | 63.1 | 65.5 | 68.8 | 68.8 | 67.6 | 61.3 | 56.3 | 54.1 | 67.6 | 66.3 | 68 | 69.9 | 71.2 | 74.3 | 78.8 | 80.9 | 81.1 | 76.9 | 72.2 | 66.2 | 53.9 | 54.9 | 57.4 | 58.7 | 61.8 | 64.5 | 67.8 | 68.4 | 67.6 | 62.1 | 56.5 | 53.4 | 61.9 | 62.1 | 64.5 | 64.5 | 67.8 | 69.5 | 73.1 | 73.1 | 73.6 | 70.2 | 63.8 | 62.1 | 71.8 | 74.2 | 73.4 | 76.8 | 77.7 | 82.1 | 82.9 | 87.3 | 86.6 | 79.5 | 74.5 | 69.3 | 59.6 | 59.5 | 61.4 | 62.2 | 65.4 | 67.8 | 71.1 | 71.1 | 71.4 | 67.4 | 62.1 | 59.6 | 68.2 | 67.8 | 72 | 73.9 | 75.7 | 79.2 | 81.2 | 82.8 | 83.8 | 77.6 | 72.9 | 66.1 | 58 | 57.9 | 59.5 | 60.3 | 63.5 | 66.3 | 69.7 | 69.9 | 69.8 | 65.6 | 60.4 | 58 | 65.8 | 65.6 | 68.3 | 70.4 | 72.6 | 76.2 | 79.3 | 80.8 | 80.8 | 75.5 | 70.6 | 64.4 | 56.5 | 56.5 | 58.2 | 59 | 62 | 64.9 | 68.4 | 68.9 | 68.4 | 64 | 59.1 | 56.2 | 64.1 | 64 | 65.9 | 67.9 | 69.8 | 73.4 | 77.4 | 79 | 78.7 | 72.8 | 68.5 | 62.8 | 26.8 | 23.8 | 22.3 | 22.2 | 17.8 | 16.8 | 18.1 | 20 | 22.3 | 25.7 | 28.7 | 27.4 | 38 | 35.8 | 34.5 | 36.3 | 27.6 | 23.3 | 23 | 26.3 | 30.7 | 39.4 | 39.7 | 36 | 19.4 | 19 | 18.5 | 18.1 | 14.7 | 12.1 | 11 | 12.3 | 14.3 | 19 | 19.8 | 20.4 | 25.1 | 24.1 | 24.6 | 25.4 | 21.9 | 21.3 | 21 | 22.1 | 24.6 | 25.7 | 28 | 24.2 | 15.6 | 15.1 | 15 | 14.4 | 12.6 | 11.4 | 10.2 | 11 | 12.7 | 14.8 | 17.2 | 16.3 | 0.309 | 0.319 | 0.338 | 0.352 | 0.37 | 0.368 | 0.396 | 0.389 | 0.361 | 0.355 | 0.316 | 0.318 | 2.567 | 2.552 | 2.482 | 2.449 | 2.427 | 2.44 | 2.434 | 2.433 | 2.498 | 2.485 | 2.581 | 2.574 | 290 | 298 | 298 | 297 | 291 | 290 | 281 | 282 | 287 | 280 | 285 | 280 | 25 | 29 | 33 | 36 | 37 | 36 | 36 | 36 | 32 | 30 | 25 | 24 | 1033 | 1308 | 1737 | 2095 | 2230 | 2364 | 2337 | 2233 | 1899 | 1454 | 1134 | 934 | 66 | 124 | 91 | 109 | 151 | 146 | 123 | 62 | 78 | 101 | 68 | 68 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.12 | N/A | -3.04 | 1.22 | N/A | N/A | N/A | -193 | 394 | 202 | 49
| MCCLELLAN-PALOMAR_STYP20 | 7 | 4 | USA | CA | MCCLELLAN-PALOMAR | 722927 | 03177 | 33.128 | -117.279 | 328 | 14.52 | -8 | NAP | 98-19 | 3C | 12 | 43 | 44.9 | 11.8 | 10.2 | 59.6 | 17.3 | 13.3 | 57.9 | 17.1 | 60.9 | 14.8 | 59.1 | 3.1 | 80 | 0.337 | 8 | 9.1 | 84.3 | 62.9 | 81.1 | 64 | 78.5 | 64.3 | 71 | 77.5 | 69.6 | 75.7 | 68.7 | 74.6 | 6.4 | 250 | 68.6 | 106.4 | 74.3 | 67.3 | 101.5 | 73.5 | 66.2 | 97.7 | 72.7 | 35 | 77.7 | 33.9 | 76 | 33 | 74.8 | 76.3 | 13.4 | 11.9 | 10.7 | 38.5 | 94.4 | 1.7 | 5.1 | 37.3 | 98 | 36.3 | 101 | 35.3 | 103.8 | 34.1 | 107.5 | 32.2 | 73 | 2 | 1.8 | 30.8 | 74.3 | 29.6 | 75.3 | 28.4 | 76.3 | 26.9 | 77.5 | 62.5 | 56.8 | 56.2 | 57.7 | 59.5 | 62.2 | 65 | 69.3 | 70.3 | 69.3 | 65.9 | 60.8 | 56.1 | 6.62 | 5.17 | 4.67 | 4.23 | 4.33 | 3.5 | 2.92 | 3.13 | 3.03 | 4.23 | 4.71 | 4.89 | 4.3 | 8 | 4 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1523 | 261 | 251 | 232 | 175 | 101 | 33 | 1 | 0 | 3 | 42 | 145 | 279 | 4556 | 214 | 176 | 240 | 285 | 378 | 449 | 598 | 628 | 580 | 492 | 325 | 191 | 594 | 6 | 5 | 6 | 10 | 14 | 32 | 134 | 163 | 133 | 69 | 20 | 2 | 1974 | 46 | 42 | 56 | 83 | 96 | 48 | 213 | 336 | 488 | 391 | 154 | 21 | 422 | 5 | 8 | 12 | 25 | 34 | 8 | 20 | 38 | 117 | 112 | 40 | 3 | 4.3 | 3.8 | 4.5 | 4.6 | 5.1 | 5.3 | 4.9 | 4.5 | 4.1 | 4 | 3.8 | 3.6 | 3.8 | 11.3 | 2.3 | 2.3 | 1.6 | 0.9 | 0.3 | 0.1 | 0.1 | 0 | 0.2 | 0.6 | 0.9 | 1.7 | 23 | 9.9 | 10 | 6.3 | 2.1 | 1.1 | 0.8 | 1.7 | 0.4 | 1.1 | 5 | 3 | 8 | 3.5 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4 | 2.4 | 2.2 | 1.5 | 0.6 | 0.3 | 0.2 | 0.4 | 0.1 | 0.2 | 1.1 | 0.8 | 1.7 | 79.1 | 80.1 | 80.6 | 82.7 | 84.2 | 79.5 | 82.2 | 84.2 | 89.5 | 88.3 | 84.4 | 76.7 | 55.7 | 55.6 | 56.6 | 56.8 | 57.8 | 67 | 69.7 | 68.6 | 70.4 | 62.2 | 57.7 | 53.4 | 73.7 | 72.7 | 73.3 | 74.9 | 73.7 | 73.8 | 78.8 | 80.5 | 82.8 | 82.8 | 78.4 | 70.8 | 53.6 | 53.2 | 55 | 56.4 | 60.3 | 65.4 | 68.7 | 68.6 | 67.7 | 59.5 | 56.2 | 52.4 | 70 | 67.9 | 68.1 | 70 | 69.7 | 71.6 | 76.2 | 77.6 | 79.3 | 78.5 | 73 | 66.7 | 52.7 | 53.3 | 54.9 | 56.5 | 60.6 | 64.2 | 68.1 | 68.4 | 68 | 59.9 | 54.7 | 52.5 | 65.7 | 63.8 | 64.3 | 66 | 66.4 | 69.8 | 74.1 | 75.2 | 75.8 | 73.5 | 68.9 | 63.7 | 52.2 | 53.2 | 55.5 | 57.1 | 59.2 | 63.1 | 67.3 | 67.7 | 67 | 61.7 | 55.4 | 52.9 | 60.1 | 60.5 | 61.7 | 62.2 | 64.6 | 67.9 | 72.2 | 72.2 | 72.8 | 69.8 | 63.1 | 61.2 | 66.5 | 65.3 | 69.7 | 70.6 | 71.9 | 75.8 | 78.2 | 78.9 | 82.9 | 75.8 | 68.3 | 66.3 | 58.4 | 58.4 | 59.6 | 60.3 | 62.6 | 66.2 | 70.1 | 70.4 | 71 | 67.1 | 61.3 | 59.3 | 63.8 | 63.6 | 66 | 67.1 | 68.7 | 72.7 | 75.9 | 76.7 | 78.4 | 74.3 | 67.9 | 63 | 57.1 | 57 | 58.3 | 59.1 | 61.5 | 64.9 | 69 | 69.3 | 69.5 | 65.3 | 60 | 57.7 | 62.3 | 62.5 | 64 | 65.3 | 67.1 | 70.4 | 74.6 | 75.2 | 75.9 | 71.7 | 66.3 | 61.9 | 55.7 | 55.7 | 57.2 | 58.1 | 60.3 | 63.8 | 67.9 | 68.4 | 68.3 | 63.9 | 59 | 56.2 | 61.3 | 61.5 | 62.3 | 63.9 | 65.2 | 68.7 | 73.1 | 74.1 | 74.4 | 69.7 | 65 | 60.7 | 15.9 | 14.2 | 12.3 | 11.5 | 9 | 8.2 | 8.5 | 9.1 | 10.6 | 13 | 15.3 | 15.6 | 23 | 21.8 | 20 | 20.2 | 14.7 | 11.3 | 11.2 | 12 | 15.7 | 22 | 22.5 | 21.2 | 12.3 | 12.2 | 11.1 | 10.7 | 7.8 | 5.2 | 4.6 | 5.4 | 7.5 | 12.6 | 13.2 | 13 | 15.4 | 15.2 | 13.7 | 13.8 | 11.1 | 11 | 10.4 | 10.8 | 12.6 | 14.8 | 15.7 | 14.5 | 9.9 | 9.7 | 8.3 | 7.7 | 6.1 | 5.2 | 4.5 | 5 | 6.1 | 9.5 | 10.5 | 10.3 | 0.307 | 0.317 | 0.334 | 0.346 | 0.365 | 0.362 | 0.391 | 0.386 | 0.357 | 0.355 | 0.315 | 0.317 | 2.569 | 2.557 | 2.493 | 2.463 | 2.435 | 2.449 | 2.444 | 2.435 | 2.5 | 2.479 | 2.581 | 2.574 | 291 | 298 | 300 | 298 | 292 | 291 | 282 | 283 | 288 | 280 | 286 | 281 | 25 | 29 | 33 | 35 | 36 | 36 | 36 | 36 | 32 | 30 | 25 | 24 | 1038 | 1314 | 1736 | 2094 | 2218 | 2333 | 2299 | 2203 | 1886 | 1454 | 1135 | 939 | 65 | 119 | 93 | 110 | 155 | 145 | 133 | 74 | 87 | 102 | 71 | 68 | 1.67 | N/A | N/A | 2.45 | 1.71 | 1.58 | N/A | -378 | 551 | 238 | 1.08 | N/A | -2.92 | 1.19 | N/A | N/A | N/A | -176 | 380 | 198 | 45
| OCEANSIDE_STYP20 | 7 | 4 | USA | CA | OCEANSIDE | 722934 | 53121 | 33.219 | -117.349 | 28 | 14.68 | -8 | NAP | 99-19 | 3C | 12 | 34.6 | 36.8 | 17.7 | 13.4 | 55.9 | 22.5 | 16.9 | 54.6 | 16.9 | 58.2 | 15.1 | 59.4 | 1.9 | 30 | 0.369 | 8 | 13.8 | 85.7 | 64.5 | 82.2 | 65.8 | 79.5 | 66.3 | 71.3 | 79.6 | 70.2 | 78 | 69.1 | 76.4 | 8.5 | 250 | 68.3 | 104.2 | 76 | 67 | 99.5 | 75.1 | 66 | 96.1 | 74.2 | 35.1 | 79.5 | 34.1 | 78.4 | 33.2 | 76.6 | 76.6 | 14.4 | 12.5 | 11.3 | 30.1 | 95 | 2.5 | 5 | 28.4 | 98.6 | 26.9 | 101.5 | 25.5 | 104.3 | 23.8 | 107.9 | 27.7 | 73.5 | 2.9 | 1.5 | 25.6 | 74.6 | 23.9 | 75.5 | 22.3 | 76.4 | 20.2 | 77.5 | 61.2 | 53.8 | 54.1 | 56.5 | 58.7 | 62.4 | 65.6 | 69.6 | 69.9 | 68.4 | 63.7 | 58 | 53 | 7.14 | 4.49 | 4.4 | 3.97 | 3.73 | 3.23 | 2.5 | 2.99 | 2.96 | 4.29 | 4.09 | 4.34 | 4.14 | 43 | 14 | 11 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 16 | 1899 | 349 | 307 | 267 | 192 | 91 | 20 | 2 | 1 | 11 | 73 | 215 | 371 | 4125 | 130 | 125 | 202 | 262 | 385 | 468 | 607 | 618 | 551 | 426 | 241 | 110 | 506 | 0 | 1 | 2 | 4 | 11 | 39 | 143 | 155 | 112 | 34 | 5 | 0 | 2680 | 44 | 49 | 70 | 122 | 135 | 76 | 413 | 551 | 622 | 419 | 166 | 13 | 577 | 6 | 7 | 16 | 38 | 52 | 12 | 39 | 67 | 160 | 134 | 44 | 2 | 4.2 | 3.6 | 4.2 | 4.2 | 4.7 | 4.9 | 4.7 | 4.5 | 4.3 | 4.2 | 3.8 | 3.5 | 3.5 | 11.3 | 2.3 | 2.3 | 1.6 | 0.9 | 0.3 | 0.1 | 0.1 | 0 | 0.2 | 0.6 | 0.9 | 1.7 | 23 | 9.9 | 10 | 6.3 | 2.1 | 1.1 | 0.8 | 1.7 | 0.4 | 1.1 | 5 | 3 | 8 | 3.5 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4 | 2.4 | 2.2 | 1.5 | 0.6 | 0.3 | 0.2 | 0.4 | 0.1 | 0.2 | 1.1 | 0.8 | 1.7 | 79.2 | 80.6 | 81.5 | 86.2 | 86.6 | 81.1 | 84.1 | 85.5 | 91 | 89.5 | 85.1 | 75 | 56 | 57.5 | 59 | 60.3 | 58.6 | 67.5 | 70.3 | 69.6 | 70.1 | 63.7 | 59 | 53.8 | 73.3 | 73.3 | 74.2 | 77.1 | 76.1 | 75.5 | 80.5 | 81.6 | 84 | 83.6 | 78.9 | 70.6 | 54.3 | 55.1 | 57.3 | 58.6 | 62.6 | 66.3 | 70 | 69.9 | 69.2 | 61.3 | 57.5 | 53.9 | 69.6 | 68.3 | 68.9 | 71.3 | 71.8 | 73.3 | 78.2 | 79.2 | 80.5 | 78.3 | 73.1 | 66.7 | 54.3 | 55 | 57 | 59.2 | 62.3 | 64.7 | 69.1 | 69.1 | 68.9 | 62.2 | 56.4 | 54.8 | 64.6 | 64.1 | 65.5 | 67.8 | 69.5 | 72 | 76.1 | 77 | 77.1 | 74.2 | 69.6 | 63.8 | 53.9 | 55.1 | 57.3 | 58.7 | 60.9 | 63.8 | 67.9 | 68 | 67.3 | 63.5 | 58 | 54.6 | 60.9 | 61.6 | 62.5 | 65 | 66.2 | 68.6 | 72.7 | 72.6 | 73.2 | 70.3 | 64 | 62 | 67.8 | 70.2 | 71.9 | 77.6 | 75.5 | 77.8 | 79.7 | 81.4 | 84.4 | 77.5 | 70 | 66.4 | 59.2 | 59.2 | 60.4 | 62 | 64.1 | 66.9 | 70.9 | 70.8 | 71.3 | 67.9 | 62.5 | 59.7 | 65.1 | 65.4 | 67.7 | 70.6 | 71.8 | 74.8 | 78 | 79.1 | 80.7 | 75.9 | 68.6 | 63.9 | 57.7 | 57.9 | 59.2 | 60.3 | 62.6 | 65.7 | 69.7 | 69.6 | 69.8 | 66 | 61.2 | 58.2 | 63.7 | 64.4 | 65.9 | 67.9 | 69.4 | 72.7 | 76.8 | 77.5 | 77.7 | 73.2 | 68.3 | 62.7 | 56.3 | 56.6 | 58.1 | 59.1 | 61.5 | 64.5 | 68.7 | 68.7 | 68.4 | 64.5 | 59.7 | 56.7 | 62.5 | 63 | 64 | 66.2 | 67.6 | 70.4 | 75.3 | 76 | 75.4 | 70.9 | 67 | 61.7 | 23.7 | 21.4 | 18.7 | 18.4 | 14.6 | 12.7 | 12.9 | 13.8 | 16.8 | 20.7 | 24.2 | 23.6 | 31.8 | 30.9 | 27.6 | 29 | 21.1 | 15.9 | 15.5 | 17.2 | 22 | 32.2 | 33 | 29.4 | 17.8 | 17.5 | 15.7 | 15.6 | 11.1 | 8.3 | 7.4 | 8.4 | 10.8 | 17.4 | 18.3 | 17.9 | 22.7 | 22.6 | 19.6 | 21.1 | 17.1 | 15.7 | 14.7 | 15.7 | 18.9 | 22.5 | 24.2 | 20.5 | 14.6 | 14.3 | 12.3 | 12.5 | 9.4 | 8.3 | 7.1 | 7.9 | 9.7 | 13.7 | 15.6 | 14.5 | 0.31 | 0.32 | 0.338 | 0.352 | 0.371 | 0.368 | 0.396 | 0.391 | 0.362 | 0.357 | 0.317 | 0.319 | 2.568 | 2.553 | 2.485 | 2.452 | 2.426 | 2.44 | 2.434 | 2.43 | 2.498 | 2.482 | 2.58 | 2.573 | 290 | 297 | 298 | 297 | 290 | 289 | 281 | 281 | 286 | 279 | 285 | 279 | 25 | 29 | 33 | 36 | 37 | 36 | 36 | 36 | 32 | 30 | 25 | 24 | 1033 | 1309 | 1733 | 2090 | 2214 | 2336 | 2314 | 2216 | 1889 | 1450 | 1132 | 935 | 66 | 121 | 92 | 111 | 154 | 147 | 128 | 67 | 82 | 102 | 70 | 68 | 1.01 | N/A | N/A | 2.77 | N/A | N/A | N/A | -218 | 385 | 198 | 1.1 | N/A | -3.01 | 1.19 | N/A | N/A | N/A | -185 | 391 | 202 | 47
| LOS-ANGELES-INTL_STYP20 | 6 | 4 | USA | CA | LOS ANGELES INTL | 722950 | 23174 | 33.938 | -118.389 | 97 | 14.64 | -8 | NAP | 94-19 | 3C | 2 | 45 | 47 | 12.2 | 10.3 | 62 | 17.5 | 13.4 | 61.2 | 25.6 | 57.5 | 22.4 | 56.6 | 4.2 | 80 | 0.408 | 8 | 10.3 | 84.7 | 63.3 | 81.3 | 64.2 | 78.6 | 64.3 | 70.5 | 78.2 | 69.3 | 76.3 | 68.2 | 75 | 8.6 | 260 | 67.6 | 101.8 | 74.6 | 66.4 | 97.7 | 73.5 | 65.4 | 94 | 72.6 | 34.5 | 78.2 | 33.4 | 76.7 | 32.5 | 74.9 | 76.1 | 20.3 | 17.6 | 16 | 40.4 | 94.3 | 2 | 4.3 | 38.9 | 97.4 | 37.7 | 99.9 | 36.6 | 102.3 | 35.1 | 105.4 | 33.7 | 72.1 | 2.4 | 2 | 32 | 73.5 | 30.5 | 74.7 | 29.2 | 75.8 | 27.4 | 77.2 | 63.4 | 57.9 | 57.6 | 59.1 | 60.6 | 63.2 | 66.1 | 69.3 | 70.2 | 69.8 | 66.8 | 62.1 | 57.6 | 6.28 | 4.89 | 4.73 | 4.12 | 4.35 | 3.52 | 2.67 | 3.07 | 3.35 | 4.13 | 4.92 | 5.08 | 4.2 | 4 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1256 | 227 | 215 | 191 | 147 | 77 | 15 | 2 | 1 | 3 | 29 | 116 | 233 | 4894 | 248 | 213 | 283 | 318 | 409 | 483 | 599 | 628 | 593 | 521 | 363 | 236 | 672 | 8 | 7 | 9 | 15 | 21 | 48 | 136 | 164 | 146 | 86 | 29 | 3 | 2127 | 61 | 57 | 59 | 93 | 86 | 65 | 235 | 387 | 462 | 419 | 178 | 25 | 453 | 8 | 12 | 10 | 25 | 27 | 9 | 26 | 48 | 95 | 139 | 52 | 2 | 7.3 | 6.2 | 7.4 | 7.8 | 8.6 | 8.2 | 7.8 | 7.9 | 7.6 | 7.2 | 6.6 | 6.2 | 6.2 | 12.1 | 2.6 | 2.8 | 1.8 | 0.7 | 0.1 | 0.1 | 0 | 0 | 0.2 | 0.4 | 1.3 | 1.9 | 29.5 | 12.7 | 13.3 | 6.4 | 4.5 | 0.9 | 1 | 0.4 | 1.3 | 1.9 | 3.8 | 7.5 | 8.8 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6 | 2.8 | 3 | 1.7 | 0.9 | 0.2 | 0.2 | 0.1 | 0.2 | 0.4 | 0.6 | 1.5 | 1.9 | 80.7 | 81.4 | 80.9 | 83.4 | 83.9 | 80.6 | 83.3 | 84.7 | 87.9 | 91 | 86.5 | 77.6 | 55.2 | 57 | 57.1 | 58.3 | 60.2 | 66.4 | 70.1 | 70 | 67 | 61.5 | 59 | 53.6 | 74.5 | 73.3 | 73.7 | 75.6 | 74.3 | 75.2 | 78.9 | 80.6 | 82.3 | 83.5 | 78.8 | 72 | 53.7 | 54.3 | 55.1 | 56.7 | 62.7 | 65.1 | 68.7 | 69 | 67.7 | 60.3 | 56.1 | 53.3 | 70.2 | 68.5 | 69 | 70.6 | 71.1 | 72.8 | 76.4 | 78 | 78.9 | 78.2 | 73.9 | 68.1 | 52.8 | 54 | 55.6 | 57.2 | 62.2 | 64.3 | 67.6 | 68 | 67.3 | 61.1 | 55.8 | 52.8 | 66 | 64.4 | 65.5 | 67.1 | 68.5 | 71.1 | 74.4 | 75.8 | 76.1 | 73.9 | 69.9 | 64.8 | 52.7 | 53.9 | 56.1 | 57.2 | 60.7 | 63.3 | 66.6 | 67.1 | 66.7 | 61.8 | 56.2 | 53 | 61.3 | 61.3 | 62 | 63.3 | 67.9 | 68.1 | 71.5 | 71.7 | 72.2 | 69.5 | 64.3 | 61.6 | 66.5 | 68.9 | 68.9 | 72.2 | 74.3 | 77.5 | 79.8 | 80.9 | 81.5 | 77.2 | 70.8 | 64.8 | 59.4 | 59.4 | 60.1 | 61 | 64.8 | 66.2 | 69.8 | 70.3 | 70.2 | 67.2 | 62.3 | 59.7 | 63.8 | 64.3 | 66.2 | 68.6 | 70.8 | 73.8 | 77.1 | 78.1 | 77.7 | 74.5 | 68.1 | 63.1 | 58 | 58.2 | 59 | 59.6 | 63.3 | 65 | 68.5 | 69.1 | 68.9 | 65.5 | 61.1 | 58.5 | 62.2 | 62.7 | 64.4 | 66.2 | 68.9 | 71.8 | 75 | 76.1 | 75.9 | 72 | 66.7 | 62.1 | 56.8 | 57 | 57.9 | 58.4 | 61.9 | 64 | 67.4 | 68 | 67.6 | 64.1 | 60 | 57.2 | 61.1 | 61.4 | 62.6 | 64.6 | 67.1 | 70.2 | 73.3 | 74.5 | 74.4 | 70.1 | 65.5 | 61.1 | 15.1 | 13.7 | 12.5 | 12.3 | 10.5 | 9.7 | 9.9 | 10.3 | 11 | 12.9 | 14.9 | 14.8 | 22.9 | 21.9 | 19.8 | 18.9 | 14.2 | 11.8 | 11.8 | 12.8 | 15.4 | 21.8 | 22.6 | 20.9 | 11.4 | 10.9 | 10 | 8.8 | 6.8 | 5.3 | 5.1 | 5.4 | 6.6 | 10 | 11.7 | 11.8 | 14.4 | 14.3 | 13.1 | 14.1 | 12.1 | 11.6 | 11.4 | 12.2 | 12.8 | 14.7 | 15.4 | 13.6 | 8.6 | 8.4 | 7.6 | 7.4 | 6.3 | 5.4 | 5 | 5.4 | 5.8 | 7.5 | 9 | 8.8 | 0.335 | 0.349 | 0.372 | 0.377 | 0.382 | 0.398 | 0.4 | 0.38 | 0.367 | 0.371 | 0.322 | 0.323 | 2.501 | 2.476 | 2.385 | 2.378 | 2.393 | 2.352 | 2.412 | 2.447 | 2.478 | 2.439 | 2.577 | 2.573 | 278 | 285 | 286 | 289 | 287 | 281 | 279 | 284 | 284 | 273 | 281 | 276 | 27 | 31 | 36 | 38 | 38 | 40 | 37 | 35 | 33 | 31 | 25 | 24 | 998 | 1280 | 1712 | 2096 | 2260 | 2349 | 2353 | 2240 | 1891 | 1435 | 1111 | 905 | 73 | 127 | 98 | 110 | 158 | 146 | 129 | 77 | 80 | 108 | 69 | 69 | 0.72 | N/A | -2.88 | N/A | N/A | N/A | N/A | N/A | 250 | N/A | 1.15 | N/A | -2.97 | 1.31 | N/A | N/A | N/A | -212 | 405 | 194 | 52
| TORRANCE-MUNI-AP_STYP20 | 6 | 4 | USA | CA | TORRANCE-MUNI-AP | 722955 | 03122 | 33.8 | -118.33 | 102 | 14.64 | -8 | NAP | N/A | 3C | 12 | 44.4 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 8 | 11.8 | 87.9 | 62.8 | N/A | N/A | N/A | N/A | 69.8 | 79.9 | N/A | N/A | N/A | N/A | N/A | N/A | 66.2 | N/A | 74.5 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 5.8 | 5.8 | 5.4 | 4.9 | 4 | 3.1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 83.3 | 84.92 | 86.18 | 92.66 | 92.84 | 87.98 | N/A | N/A | N/A | N/A | N/A | N/A | 67.1 | 70.16 | 67.82 | 67.1 | 60.98 | 59.36 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 10.44 | 11.34 | 11.88 | 12.78 | 14.22 | 16.38 | N/A | N/A | N/A | N/A | N/A | N/A | 13 | 14 | 14.8 | 18.7 | 24.5 | 25.6 | N/A | N/A | N/A | N/A | N/A | N/A | 5.8 | 5.6 | 5.9 | 6.8 | 9 | 11 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.399 | 0.399 | 0.381 | 0.367 | 0.374 | 0.323 | N/A | N/A | N/A | N/A | N/A | N/A | 2.348 | 2.415 | 2.448 | 2.48 | 2.43 | 2.574 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| LOS-ANGELES-HAWTHORNE_STYP20 | 8 | 4 | USA | CA | LOS ANGELES HAWTHORNE | 722956 | 03167 | 33.923 | -118.334 | 63 | 14.66 | -8 | NAP | 98-19 | 3C | 12 | 44.5 | 45.9 | 11.5 | 9.9 | 65.6 | 17.1 | 13.1 | 64.1 | 17.9 | 58.7 | 15.4 | 59.6 | 1 | 70 | 0.348 | 8 | 11.7 | 88.4 | 63.5 | 84.6 | 63.6 | 81.6 | 63.9 | 70.7 | 80.1 | 69.4 | 78.3 | 68.4 | 77 | 6.9 | 250 | 67.3 | 100.7 | 75.5 | 66 | 96.1 | 74.7 | 64.7 | 91.7 | 73 | 34.6 | 80.1 | 33.5 | 78.7 | 32.6 | 77 | 75.2 | 16.3 | 14 | 12.5 | 39.4 | 97.2 | 2.8 | 5 | 37.4 | 100.8 | 35.7 | 103.7 | 34.1 | 106.5 | 32.1 | 110.1 | 33.4 | 72.3 | 2.1 | 1.7 | 31.8 | 73.5 | 30.6 | 74.5 | 29.3 | 75.4 | 27.8 | 76.6 | 64.7 | 58.8 | 58.6 | 60.7 | 62.2 | 64.5 | 67.2 | 70.9 | 71.5 | 71.2 | 68.4 | 63.5 | 58.1 | 6.62 | 5.11 | 5 | 4.7 | 4.77 | 3.81 | 3 | 3.65 | 3.51 | 4.53 | 5.3 | 5.18 | 4.36 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1039 | 202 | 189 | 152 | 111 | 51 | 8 | 1 | 0 | 1 | 19 | 87 | 218 | 5352 | 275 | 241 | 331 | 365 | 449 | 517 | 648 | 666 | 635 | 570 | 404 | 251 | 913 | 10 | 10 | 18 | 26 | 36 | 75 | 184 | 201 | 185 | 124 | 41 | 3 | 4013 | 115 | 103 | 141 | 197 | 182 | 150 | 563 | 662 | 820 | 715 | 311 | 54 | 1058 | 18 | 25 | 38 | 66 | 66 | 29 | 89 | 111 | 240 | 272 | 100 | 4 | 4.7 | 3.1 | 4.2 | 5 | 5.8 | 6 | 5.8 | 5.8 | 5.5 | 5 | 4 | 3.2 | 3 | 12.1 | 2.6 | 2.8 | 1.8 | 0.7 | 0.1 | 0.1 | 0 | 0 | 0.2 | 0.4 | 1.3 | 1.9 | 29.5 | 12.7 | 13.3 | 6.4 | 4.5 | 0.9 | 1 | 0.4 | 1.3 | 1.9 | 3.8 | 7.5 | 8.8 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6 | 2.8 | 3 | 1.7 | 0.9 | 0.2 | 0.2 | 0.1 | 0.2 | 0.4 | 0.6 | 1.5 | 1.9 | 82.3 | 84 | 84.4 | 88.7 | 88.4 | 84 | 86.8 | 87.2 | 93 | 94.1 | 89.1 | 79.7 | 55.2 | 56.6 | 58 | 59.5 | 60.1 | 66.9 | 70.1 | 69.2 | 68.1 | 62.5 | 59.3 | 54.1 | 77 | 76.5 | 77.7 | 79.2 | 78.7 | 77.7 | 82.1 | 83.1 | 86.2 | 87.1 | 82.2 | 74.1 | 53 | 54.1 | 55.6 | 57.1 | 61 | 65.4 | 68.8 | 68.4 | 67.3 | 60.9 | 57.6 | 53.3 | 72.7 | 71.3 | 72.4 | 73.4 | 73.1 | 74.7 | 79.4 | 80.2 | 81.9 | 81.6 | 76.7 | 70.2 | 52.8 | 54.1 | 55.5 | 57.1 | 61.2 | 64.4 | 68.2 | 67.8 | 67.2 | 61.5 | 55.8 | 52.5 | 68 | 66.3 | 68.2 | 69.6 | 70.2 | 72.6 | 77 | 77.5 | 78.5 | 76.7 | 72.1 | 65.9 | 52.6 | 54.1 | 55.8 | 56.8 | 60 | 63.3 | 67.2 | 67.1 | 66.4 | 62.1 | 56.2 | 52.7 | 60.5 | 61 | 62.1 | 62.8 | 66.1 | 68.4 | 72.3 | 71.6 | 72.3 | 69.7 | 63.8 | 61.1 | 66.7 | 68.8 | 73.8 | 76 | 78.9 | 79.6 | 82.7 | 81.3 | 84.7 | 79.1 | 73.4 | 65.3 | 58.9 | 59.1 | 60.2 | 60.5 | 63.7 | 66.4 | 70.3 | 70.2 | 70.4 | 67.5 | 62.2 | 59.3 | 64.4 | 65.8 | 69.3 | 71.5 | 72.9 | 75.6 | 79.1 | 79.4 | 80.4 | 77.5 | 70.3 | 64.5 | 57.5 | 57.7 | 58.9 | 59.3 | 62.2 | 65.4 | 69.1 | 69 | 69 | 65.6 | 60.9 | 57.8 | 63.9 | 64.4 | 66.8 | 68.7 | 70.3 | 73.5 | 77.2 | 77.8 | 78.3 | 74.5 | 68.5 | 63.2 | 56.3 | 56.5 | 57.7 | 58.2 | 60.9 | 64.3 | 68 | 67.9 | 67.6 | 64.3 | 59.7 | 56.5 | 62.8 | 63.3 | 64.5 | 66.3 | 68.2 | 71.1 | 75.6 | 76.3 | 76.4 | 72.2 | 67.2 | 62.1 | 17.2 | 15.5 | 14.1 | 13.3 | 11.2 | 10.5 | 11.4 | 11.7 | 12.7 | 14.6 | 16.8 | 16.7 | 25.7 | 24.5 | 22.1 | 21.5 | 17.5 | 13.6 | 14 | 14.5 | 18.6 | 24.4 | 26 | 24.3 | 11 | 10.6 | 9.1 | 8.6 | 6.9 | 5.7 | 5.5 | 5.8 | 6.9 | 9.3 | 11.4 | 12 | 16.2 | 16.8 | 15.4 | 15.8 | 13.9 | 12.9 | 13.2 | 13.3 | 15.5 | 16.7 | 17.5 | 15.7 | 8.4 | 8.5 | 7 | 7 | 6.1 | 5.6 | 5.3 | 5.6 | 6.1 | 7 | 9 | 9 | 0.339 | 0.353 | 0.377 | 0.379 | 0.383 | 0.399 | 0.399 | 0.381 | 0.367 | 0.374 | 0.323 | 0.325 | 2.488 | 2.461 | 2.366 | 2.372 | 2.392 | 2.348 | 2.415 | 2.448 | 2.48 | 2.43 | 2.574 | 2.57 | 276 | 284 | 284 | 288 | 286 | 280 | 279 | 284 | 284 | 272 | 281 | 276 | 27 | 31 | 37 | 38 | 38 | 40 | 37 | 35 | 33 | 32 | 25 | 24 | 1000 | 1282 | 1714 | 2098 | 2261 | 2353 | 2354 | 2240 | 1892 | 1437 | 1112 | 907 | 72 | 127 | 97 | 109 | 156 | 146 | 128 | 76 | 80 | 108 | 69 | 69 | 1.37 | N/A | -2.14 | 2.2 | N/A | N/A | N/A | -293 | 612 | 319 | 1.12 | N/A | -2.95 | 1.3 | N/A | N/A | N/A | -209 | 396 | 189 | 52
| LONG-BEACH_STYP20 | 8 | 4 | USA | CA | LONG BEACH | 722970 | 23129 | 33.812 | -118.146 | 31 | 14.68 | -8 | NAP | 94-19 | 3B | 12 | 41.7 | 43.9 | 12 | 10.2 | 69.3 | 18.2 | 13.8 | 66.1 | 20.2 | 56.8 | 17.7 | 59.5 | 1.7 | 300 | 0.356 | 8 | 16.9 | 91.8 | 66 | 88.2 | 66 | 85.1 | 65.4 | 72.1 | 83 | 70.7 | 81.1 | 69.4 | 79.3 | 8.2 | 290 | 68.8 | 105.8 | 76 | 67.2 | 100.3 | 75.3 | 65.9 | 95.5 | 74.3 | 35.7 | 82.9 | 34.6 | 80.9 | 33.5 | 79.6 | 79.5 | 16.6 | 13.7 | 12.1 | 37.2 | 100.6 | 2 | 3.9 | 35.7 | 103.4 | 34.5 | 105.7 | 33.4 | 107.9 | 31.9 | 110.7 | 32.7 | 74.2 | 2.3 | 2.4 | 31.1 | 75.9 | 29.7 | 77.3 | 28.5 | 78.6 | 26.8 | 80.3 | 65.1 | 57.6 | 57.6 | 60.4 | 62.6 | 65.4 | 68.8 | 73 | 74.3 | 73 | 68.2 | 62.2 | 56.9 | 7.63 | 5.08 | 4.84 | 4.58 | 4.88 | 4.03 | 3.6 | 3.62 | 4.01 | 4.98 | 5.05 | 5.15 | 4.31 | 8 | 4 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1139 | 235 | 214 | 157 | 102 | 39 | 5 | 0 | 0 | 0 | 19 | 113 | 255 | 5504 | 240 | 214 | 323 | 379 | 477 | 564 | 714 | 755 | 691 | 566 | 366 | 215 | 1159 | 6 | 6 | 14 | 31 | 52 | 119 | 249 | 290 | 242 | 119 | 29 | 2 | 6898 | 131 | 113 | 186 | 312 | 299 | 426 | 1158 | 1615 | 1442 | 839 | 320 | 57 | 2237 | 25 | 31 | 54 | 106 | 104 | 105 | 297 | 526 | 535 | 338 | 109 | 7 | 5.1 | 4 | 4.8 | 5.4 | 6.1 | 6 | 5.9 | 5.8 | 5.5 | 5.1 | 4.5 | 3.9 | 3.9 | 12.4 | 2.8 | 3.2 | 1.8 | 0.7 | 0.3 | 0.1 | 0 | 0 | 0.1 | 0.5 | 0.9 | 2.1 | 24.9 | 12.8 | 13 | 6 | 2 | 2.1 | 0.9 | 0.4 | 0.1 | 1.6 | 4.4 | 2.2 | 9.8 | 4.8 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3.2 | 3 | 1.7 | 0.6 | 0.5 | 0.2 | 0.1 | 0 | 0.3 | 0.9 | 0.7 | 2.1 | 83.4 | 85.3 | 86.7 | 90.2 | 90.3 | 89.5 | 90.7 | 94.2 | 97 | 96.4 | 90 | 80 | 56.6 | 57.4 | 59.1 | 59.7 | 60.1 | 67.2 | 69.1 | 69.8 | 69.6 | 62.6 | 60 | 54.2 | 77.7 | 76.9 | 79.1 | 82.3 | 81.5 | 82.3 | 86.3 | 89.1 | 90.5 | 88.9 | 82.6 | 74.4 | 54.7 | 55.7 | 56.7 | 58.6 | 62.7 | 66.3 | 68.5 | 69 | 68.8 | 61.8 | 56.8 | 54.2 | 72.6 | 71 | 73.3 | 76.5 | 76 | 78.4 | 83.2 | 85.6 | 86 | 82.7 | 76.6 | 69.8 | 54.1 | 54.7 | 56.5 | 58.2 | 62.4 | 65.4 | 68 | 68.6 | 67.8 | 61.6 | 56.5 | 53.1 | 67.4 | 66.3 | 68.9 | 71.4 | 72.1 | 75.4 | 80.2 | 82.4 | 81.9 | 77.6 | 71.9 | 65.8 | 53.7 | 54.7 | 56.7 | 57.8 | 61.3 | 64.4 | 67.6 | 68.4 | 67.2 | 62.4 | 57.1 | 53.3 | 61.7 | 61.9 | 64.3 | 65.5 | 68.5 | 69.5 | 72.6 | 74 | 74.8 | 70.5 | 65.1 | 61.8 | 68.1 | 72.2 | 75.7 | 77.7 | 78.2 | 82.2 | 83.9 | 86.9 | 85.9 | 79.3 | 74 | 67.2 | 59.8 | 59.8 | 61.7 | 62.4 | 65.6 | 67.9 | 70.9 | 71.9 | 72.1 | 68.2 | 62.8 | 59.8 | 65.2 | 67.7 | 70.6 | 73.5 | 75 | 79.3 | 81.1 | 83 | 82.8 | 78.4 | 70.3 | 65.3 | 58.4 | 58.4 | 59.9 | 60.6 | 63.8 | 66.4 | 69.6 | 70.6 | 70.3 | 66.2 | 61.3 | 58.3 | 64.3 | 65.2 | 67.7 | 70.1 | 72.4 | 76.2 | 79.2 | 80.8 | 81 | 76.1 | 69.2 | 63.4 | 57.1 | 57.1 | 58.7 | 59.3 | 62.3 | 65.2 | 68.6 | 69.3 | 68.9 | 64.5 | 59.9 | 56.9 | 63.5 | 63.3 | 65.6 | 67.7 | 70.2 | 73.8 | 77.6 | 78.9 | 78.9 | 72.9 | 67.4 | 61.8 | 19.1 | 17.1 | 16.5 | 16.7 | 14 | 13.9 | 15.5 | 16.9 | 17.1 | 17.5 | 19 | 18.7 | 28.7 | 26.5 | 26.3 | 26.8 | 21.9 | 19.8 | 20 | 21.9 | 23.8 | 28 | 28.2 | 26.7 | 12.6 | 11.7 | 10.6 | 10 | 8.1 | 7.3 | 7.1 | 7.6 | 7.8 | 10.2 | 11.6 | 12.9 | 17.8 | 18.1 | 18 | 20.1 | 18.1 | 18 | 17.6 | 19.2 | 20.3 | 20.1 | 19.4 | 16.8 | 9.8 | 9.5 | 8.8 | 8.9 | 7.5 | 7.1 | 6.6 | 7.2 | 7.3 | 8.5 | 9.8 | 10.1 | 0.339 | 0.352 | 0.377 | 0.375 | 0.376 | 0.392 | 0.392 | 0.376 | 0.362 | 0.37 | 0.321 | 0.321 | 2.494 | 2.469 | 2.369 | 2.389 | 2.417 | 2.372 | 2.44 | 2.47 | 2.501 | 2.45 | 2.588 | 2.587 | 276 | 285 | 285 | 290 | 289 | 282 | 282 | 285 | 286 | 274 | 282 | 278 | 27 | 31 | 37 | 38 | 37 | 39 | 36 | 35 | 32 | 31 | 25 | 24 | 1007 | 1289 | 1721 | 2100 | 2253 | 2345 | 2346 | 2235 | 1889 | 1436 | 1116 | 912 | 71 | 125 | 95 | 108 | 156 | 146 | 129 | 74 | 81 | 108 | 69 | 69 | 0.77 | N/A | -4.72 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.12 | N/A | -2.97 | 1.26 | N/A | N/A | N/A | -202 | 396 | 193 | 54
| LOS-ALAMITOS-AAF_STYP20 | 8 | 4 | USA | CA | LOS ALAMITOS AAF | 722975 | 53141 | 33.79 | -118.052 | 35 | 14.68 | -8 | NAP | 08-19 | 3B | 12 | 38.9 | 41.3 | 9.5 | 9 | 69.6 | 17.3 | 13.2 | 66.2 | 21.1 | 62.7 | 18.5 | 59.4 | 2.1 | 20 | 0.372 | 8 | 17.6 | 92.1 | 66.1 | 88.5 | 65.9 | 85.5 | 65.8 | 72.4 | 83.1 | 71.2 | 80.9 | 70.1 | 79.3 | 9.3 | 210 | 69.5 | 108.6 | 74.7 | 68.3 | 104 | 74.4 | 67.1 | 99.7 | 74 | 36 | 82.8 | 35 | 81.1 | 34 | 79.6 | 76.6 | 16.8 | 14.4 | 12.5 | 34.3 | 102.3 | 1.7 | 4.2 | 33.1 | 105.3 | 32.1 | 107.7 | 31.2 | 110.1 | 30 | 113.2 | 31.2 | 74.2 | 1.6 | 1.8 | 30.1 | 75.5 | 29.2 | 76.6 | 28.3 | 77.6 | 27.2 | 78.9 | 64.1 | 57 | 56.4 | 59.4 | 62 | 64.2 | 67.7 | 71.8 | 72.9 | 72.6 | 67.8 | 61.5 | 55.6 | 7.5 | 4.56 | 5.26 | 4.41 | 4.29 | 3.63 | 3.11 | 3.59 | 3.83 | 4.86 | 4.81 | 4.82 | 4.28 | 16 | 4 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 1292 | 253 | 245 | 184 | 111 | 56 | 5 | 0 | 0 | 1 | 21 | 124 | 292 | 5167 | 219 | 187 | 290 | 360 | 439 | 530 | 674 | 710 | 679 | 553 | 347 | 179 | 970 | 3 | 5 | 9 | 21 | 30 | 85 | 210 | 245 | 230 | 110 | 21 | 1 | 7083 | 120 | 121 | 187 | 344 | 266 | 333 | 1102 | 1492 | 1658 | 1028 | 378 | 54 | 2363 | 22 | 34 | 60 | 117 | 118 | 85 | 268 | 451 | 659 | 419 | 122 | 8 | 4.9 | 3.9 | 4.8 | 5.1 | 5.9 | 6.2 | 5.8 | 5.6 | 5.1 | 4.7 | 4.3 | 3.8 | 4.1 | 12.4 | 2.8 | 3.2 | 1.8 | 0.7 | 0.3 | 0.1 | 0 | 0 | 0.1 | 0.5 | 0.9 | 2.1 | 24.9 | 12.8 | 13 | 6 | 2 | 2.1 | 0.9 | 0.4 | 0.1 | 1.6 | 4.4 | 2.2 | 9.8 | 4.8 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3.2 | 3 | 1.7 | 0.6 | 0.5 | 0.2 | 0.1 | 0 | 0.3 | 0.9 | 0.7 | 2.1 | 83.6 | 85.5 | 87.4 | 90.8 | 92.9 | 88.7 | 90.6 | 92.4 | 98.5 | 97.4 | 90.1 | 80.4 | 55.8 | 57.6 | 59.6 | 59.7 | 60.6 | 68.1 | 68.5 | 68.1 | 68.2 | 63.6 | 60.5 | 52.7 | 77.2 | 77.2 | 78.7 | 82.4 | 82.1 | 80.9 | 86 | 88.5 | 91.1 | 90 | 83.3 | 73.6 | 55.2 | 56.1 | 57.4 | 58.4 | 60.6 | 66.9 | 68.9 | 68.9 | 69.4 | 62.9 | 57.8 | 54.7 | 73.3 | 71.4 | 73.7 | 77.3 | 74.7 | 77.4 | 82.6 | 85.1 | 87.2 | 84.3 | 77.9 | 68.9 | 54.3 | 57.3 | 58.1 | 57.7 | 62.5 | 65.8 | 69 | 68.8 | 68.5 | 62.5 | 56.6 | 53.4 | 68.3 | 67 | 69.2 | 71.9 | 71.3 | 74.7 | 79.9 | 81.7 | 83.1 | 79 | 73.1 | 65.3 | 54.9 | 56.8 | 57.9 | 58.4 | 61.1 | 64.8 | 68.4 | 68.5 | 68.7 | 62.7 | 57 | 54.6 | 62.2 | 65.2 | 65.2 | 65.2 | 66.5 | 70.2 | 72.8 | 73.5 | 74.7 | 72.6 | 65.4 | 64 | 68.3 | 70.6 | 73.8 | 77.7 | 76.1 | 82.9 | 82.8 | 84.9 | 89.3 | 80.8 | 73.9 | 66.5 | 60.4 | 62.1 | 62.4 | 62.9 | 65 | 68.3 | 71.2 | 72.1 | 72.5 | 69.7 | 63.5 | 61.2 | 65 | 67.5 | 71 | 73.3 | 74.5 | 78.7 | 81.6 | 82.2 | 84 | 78.5 | 71.2 | 64.9 | 59.2 | 60.2 | 60.9 | 61.4 | 63.5 | 66.8 | 70.1 | 71 | 71.1 | 68 | 62.1 | 59.5 | 63.6 | 65.8 | 68.9 | 70.9 | 71.1 | 75.7 | 79.8 | 80.2 | 80.9 | 76.2 | 69.5 | 62.6 | 57.8 | 58.6 | 59.5 | 60.1 | 62.1 | 65.6 | 68.9 | 69.6 | 69.8 | 66.1 | 60.6 | 58 | 63.3 | 64 | 66.3 | 68.2 | 69.3 | 73.4 | 77.8 | 78.1 | 78.9 | 73.6 | 67.7 | 61.3 | 22.6 | 19.7 | 19 | 19.3 | 15.2 | 14.4 | 15.8 | 17.6 | 19.6 | 21 | 23 | 20.5 | 31.7 | 29.1 | 29.3 | 31.5 | 23.5 | 20.7 | 21 | 23.9 | 27.3 | 32.4 | 32.7 | 29.1 | 15.1 | 14.7 | 13.6 | 11.8 | 9.2 | 8 | 7.5 | 7.9 | 8.9 | 12 | 14.2 | 15 | 20.9 | 20.7 | 20.4 | 22 | 18.5 | 18.9 | 18.6 | 19.6 | 22.9 | 22.4 | 23 | 17.9 | 12.9 | 12.9 | 11.5 | 10.3 | 8.1 | 7.6 | 7 | 7.3 | 8.5 | 9.8 | 12.6 | 12.2 | 0.335 | 0.346 | 0.372 | 0.371 | 0.371 | 0.387 | 0.389 | 0.373 | 0.359 | 0.365 | 0.318 | 0.318 | 2.507 | 2.485 | 2.386 | 2.398 | 2.43 | 2.386 | 2.449 | 2.479 | 2.509 | 2.466 | 2.595 | 2.596 | 278 | 287 | 286 | 291 | 290 | 284 | 283 | 286 | 287 | 276 | 284 | 279 | 27 | 30 | 36 | 37 | 37 | 38 | 36 | 34 | 32 | 31 | 24 | 23 | 1010 | 1291 | 1725 | 2102 | 2256 | 2356 | 2351 | 2240 | 1893 | 1439 | 1118 | 914 | 71 | 125 | 93 | 107 | 154 | 146 | 127 | 71 | 79 | 106 | 68 | 68 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.12 | N/A | -2.93 | 1.3 | N/A | N/A | N/A | -198 | 389 | 187 | 52
| FULLERTON_STYP20 | 8 | 4 | USA | CA | FULLERTON | 722976 | 03166 | 33.872 | -117.979 | 96 | 14.64 | -8 | NAP | 98-19 | 3B | 12 | 40 | 42.8 | 8.8 | 8.7 | 68.1 | 15.2 | 11.9 | 69.9 | 18.9 | 66.7 | 16.3 | 64.7 | 1.2 | 90 | 0.327 | 8 | 19 | 95.3 | 66.8 | 91.7 | 66.8 | 88.7 | 66.2 | 72.4 | 87.4 | 71.1 | 85.3 | 69.9 | 83.1 | 6.5 | 210 | 67.5 | 101.4 | 78.5 | 66.1 | 96.4 | 77.3 | 64.6 | 91.7 | 75.5 | 36.1 | 87.6 | 34.9 | 85.1 | 33.9 | 83.5 | 81.5 | 12.8 | 10.9 | 10 | 35.2 | 103.8 | 2.4 | 4.3 | 33.5 | 106.9 | 32.1 | 109.4 | 30.8 | 111.9 | 29.1 | 115 | 31.5 | 74.2 | 2.1 | 1.8 | 29.9 | 75.5 | 28.7 | 76.6 | 27.5 | 77.6 | 25.9 | 78.9 | 66.1 | 58 | 58.3 | 61.2 | 63.6 | 66.8 | 70.5 | 75.1 | 76 | 74.4 | 69.2 | 62.8 | 56.9 | 8.19 | 5.15 | 5.22 | 5.16 | 5.23 | 4.41 | 3.85 | 3.92 | 4.1 | 5.25 | 5.14 | 5.15 | 4.46 | 9 | 3 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 1042 | 225 | 197 | 139 | 85 | 27 | 2 | 0 | 0 | 0 | 14 | 100 | 253 | 5885 | 250 | 233 | 348 | 409 | 520 | 614 | 777 | 805 | 733 | 596 | 383 | 217 | 1443 | 7 | 8 | 22 | 44 | 82 | 166 | 312 | 340 | 283 | 145 | 33 | 1 | 11384 | 212 | 193 | 320 | 500 | 566 | 903 | 2131 | 2540 | 2191 | 1272 | 465 | 91 | 4324 | 45 | 58 | 103 | 195 | 216 | 257 | 750 | 1012 | 959 | 553 | 166 | 10 | 3.7 | 3.1 | 3.7 | 3.9 | 4.4 | 4.5 | 4.4 | 4.1 | 3.7 | 3.4 | 3.2 | 2.8 | 2.9 | 13.3 | 3 | 3.2 | 1.8 | 1 | 0.3 | 0.1 | 0 | 0 | 0.2 | 0.5 | 1.1 | 2 | 26.4 | 12.2 | 13.6 | 6.2 | 2.5 | 2.4 | 1.1 | 0.4 | 0.1 | 1.7 | 5.2 | 3.1 | 9.8 | 4.3 | 0.1 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2 | 3.2 | 3 | 1.7 | 0.6 | 0.5 | 0.3 | 0.1 | 0 | 0.4 | 1 | 0.8 | 2.1 | 85 | 87.2 | 90 | 94.1 | 95.3 | 93.4 | 94.9 | 97 | 100.9 | 98.1 | 91.6 | 81.4 | 55.7 | 56.9 | 59.8 | 59.6 | 60.3 | 70.1 | 70.4 | 70.2 | 69.8 | 62.9 | 59.3 | 55.3 | 80.4 | 80.2 | 81.8 | 85.3 | 85 | 86.2 | 90.4 | 92.9 | 94.5 | 91.3 | 84.8 | 76.4 | 55.3 | 56 | 57.7 | 58.8 | 61.8 | 67.7 | 69.2 | 69.8 | 69.5 | 62.4 | 57.5 | 54.1 | 75.1 | 74.2 | 76.6 | 79.3 | 79.9 | 82 | 87.3 | 89.6 | 90 | 86.2 | 79.2 | 72.1 | 53.7 | 55.1 | 56.7 | 58.4 | 63.1 | 66.5 | 69.1 | 69.3 | 68.1 | 61.3 | 56.2 | 53 | 70.3 | 69.6 | 72 | 74.3 | 75.1 | 79.1 | 84 | 85.6 | 85.3 | 81 | 73.9 | 67.4 | 53.4 | 54.2 | 57 | 58.4 | 61.8 | 65.5 | 68.5 | 68.6 | 67.2 | 62.3 | 56.2 | 52.7 | 61.4 | 62 | 64.3 | 64.7 | 68.2 | 70.9 | 73.8 | 74.2 | 74.2 | 71.2 | 63.9 | 61.7 | 71.8 | 73.9 | 78.2 | 80.4 | 82.6 | 87.6 | 88.2 | 90.5 | 91.7 | 83.4 | 75.4 | 68.6 | 59.3 | 59.7 | 61.7 | 62.4 | 65.7 | 68.9 | 71.7 | 72.2 | 72 | 68.2 | 62.2 | 59.6 | 67.2 | 69.9 | 73.8 | 77.1 | 78.6 | 83.3 | 85 | 87.5 | 87.9 | 81.1 | 73.5 | 66.2 | 57.7 | 58.1 | 60 | 60.9 | 64 | 67.4 | 70.5 | 70.9 | 70.4 | 66.2 | 60.6 | 57.9 | 66.1 | 67.7 | 70.9 | 74.3 | 76.1 | 80.4 | 83.2 | 85.2 | 84.6 | 77.9 | 71.2 | 64.5 | 56.3 | 56.6 | 58.6 | 59.3 | 62.4 | 66 | 69.2 | 69.5 | 69 | 64.5 | 59.4 | 56.3 | 64.8 | 65.6 | 68.1 | 70.6 | 72.9 | 77.5 | 81.3 | 82.5 | 81.8 | 74.8 | 68.9 | 63.1 | 22 | 20.1 | 19.1 | 18.7 | 16.3 | 16 | 17.7 | 19 | 19.8 | 20.7 | 22.1 | 21.4 | 32 | 30.2 | 29.3 | 30.1 | 26 | 22.4 | 22.5 | 25 | 27.4 | 32.4 | 32 | 30.5 | 13.4 | 12.8 | 12 | 11.6 | 9.9 | 8.2 | 7.7 | 8.6 | 9.2 | 11.6 | 12.5 | 14 | 21 | 22.2 | 20.9 | 22.3 | 19.5 | 20 | 19.8 | 21.5 | 22.8 | 22 | 22.4 | 19.6 | 10.9 | 10.9 | 10 | 9.9 | 8.4 | 7.8 | 7.4 | 8.2 | 8.7 | 9.6 | 10.6 | 11.1 | 0.332 | 0.342 | 0.368 | 0.371 | 0.37 | 0.386 | 0.389 | 0.373 | 0.359 | 0.363 | 0.317 | 0.316 | 2.51 | 2.492 | 2.393 | 2.391 | 2.428 | 2.384 | 2.444 | 2.475 | 2.505 | 2.465 | 2.593 | 2.594 | 279 | 288 | 288 | 291 | 290 | 284 | 283 | 286 | 287 | 276 | 284 | 279 | 27 | 30 | 36 | 38 | 37 | 38 | 36 | 34 | 32 | 31 | 24 | 23 | 1011 | 1293 | 1731 | 2110 | 2278 | 2399 | 2374 | 2257 | 1910 | 1452 | 1123 | 916 | 71 | 127 | 93 | 105 | 147 | 141 | 123 | 68 | 73 | 102 | 65 | 68 | 2.09 | N/A | -4.82 | 2.38 | N/A | N/A | N/A | -346 | 880 | 441 | 1.12 | N/A | -2.97 | 1.26 | N/A | N/A | N/A | -202 | 396 | 193 | 54
| COSTA-MESA-WAYNE_STYP20 | 8 | 4 | USA | CA | COSTA MESA WAYNE | 722977 | 93184 | 33.68 | -117.866 | 54 | 14.67 | -8 | NAP | 99-19 | 3B | 12 | 42.8 | 44.9 | 6.9 | 7.8 | 67.1 | 14.7 | 11.6 | 67.4 | 21.3 | 62.6 | 18.5 | 63.8 | 1.3 | 30 | 0.345 | 8 | 13.2 | 89.8 | 65.3 | 86.3 | 65.3 | 83.2 | 64.9 | 71.3 | 82.3 | 70.1 | 80.3 | 69.1 | 78.6 | 7.9 | 230 | 67.7 | 102.1 | 76.4 | 66.3 | 97 | 75.3 | 65.3 | 93.7 | 74.3 | 35.1 | 82.2 | 34 | 80.3 | 33.2 | 78.8 | 77.7 | 16.1 | 13.1 | 12 | 38 | 99 | 2.5 | 5 | 36.3 | 102.7 | 34.8 | 105.6 | 33.4 | 108.4 | 31.6 | 112.1 | 33.1 | 73.5 | 2.2 | 1.5 | 31.5 | 74.6 | 30.2 | 75.5 | 29 | 76.3 | 27.4 | 77.4 | 64.8 | 58 | 57.9 | 60 | 62 | 64.9 | 68 | 72.2 | 73.1 | 72.4 | 68.5 | 62.9 | 57.4 | 7.12 | 5.12 | 4.83 | 4.31 | 4.35 | 3.78 | 3 | 3.38 | 3.37 | 4.61 | 4.8 | 4.93 | 4.34 | 5 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1106 | 227 | 205 | 166 | 110 | 42 | 4 | 0 | 0 | 0 | 16 | 97 | 239 | 5407 | 249 | 222 | 310 | 361 | 462 | 539 | 688 | 715 | 672 | 572 | 386 | 231 | 1033 | 9 | 6 | 11 | 21 | 39 | 93 | 223 | 250 | 222 | 123 | 33 | 3 | 5385 | 134 | 93 | 143 | 237 | 249 | 228 | 841 | 1114 | 1211 | 781 | 308 | 46 | 1525 | 26 | 22 | 37 | 79 | 100 | 45 | 164 | 256 | 409 | 287 | 94 | 6 | 4.8 | 3.8 | 4.4 | 4.9 | 5.6 | 6.1 | 6.1 | 5.9 | 5.3 | 4.7 | 4.1 | 3.5 | 3.6 | 10.6 | 2.4 | 2.7 | 2.2 | 0.8 | 0.1 | 0 | 0 | 0.1 | 0.4 | 0.2 | 1.2 | 1.5 | 26.1 | 7.9 | 12.4 | 10 | 4.1 | 0.5 | 0.5 | 0.2 | 1.7 | 1.9 | 1 | 5.3 | 4.2 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9 | 2.3 | 3 | 2.3 | 1.1 | 0.1 | 0.1 | 0 | 0.4 | 0.6 | 0.2 | 1.2 | 1.3 | 83.7 | 83.6 | 84.6 | 89 | 90.5 | 85.8 | 88.1 | 89.9 | 95.1 | 94.2 | 88.4 | 79.2 | 55.9 | 56.8 | 58.1 | 60.2 | 59.8 | 67.9 | 69.4 | 68.2 | 68.9 | 62.9 | 60 | 53.8 | 77.6 | 76.2 | 77.7 | 80.8 | 80.6 | 79.2 | 83.9 | 86.1 | 89 | 87.5 | 82.1 | 73.4 | 53.7 | 54.9 | 56 | 57.8 | 61.2 | 66.3 | 68.4 | 68.7 | 69 | 61.6 | 57.5 | 54.8 | 73.2 | 71.4 | 72.3 | 74.4 | 74.2 | 75.9 | 81.2 | 82.5 | 84.4 | 82.1 | 76.8 | 69.9 | 53.6 | 54.7 | 55.8 | 57.4 | 62.3 | 65.1 | 68.5 | 68.8 | 68.1 | 62.2 | 56.9 | 53.7 | 68.5 | 66.7 | 68 | 69.9 | 70.9 | 73.5 | 78.7 | 79.9 | 80.7 | 77.5 | 72.2 | 66.1 | 53.2 | 54.4 | 56.3 | 57.8 | 61 | 64 | 67.8 | 68.3 | 67.6 | 62.5 | 57.1 | 53.7 | 61.3 | 61.8 | 62.8 | 63.5 | 66.3 | 69.1 | 72.6 | 72.5 | 73.1 | 70.6 | 64.2 | 62.3 | 69.9 | 70.2 | 74.9 | 76.9 | 77.2 | 80.3 | 83.4 | 83.9 | 86.7 | 80.7 | 74.9 | 69.3 | 59.4 | 59.6 | 60.6 | 61.4 | 64.4 | 67.3 | 70.6 | 70.9 | 71.1 | 68.1 | 62.5 | 59.8 | 65.9 | 67 | 69.3 | 72 | 74.1 | 78 | 79.6 | 81.5 | 83.8 | 78.3 | 71.6 | 65.6 | 58.1 | 58.2 | 59.2 | 59.9 | 62.8 | 66 | 69.4 | 69.7 | 69.9 | 66.3 | 61.3 | 58.4 | 64.8 | 65.2 | 67.1 | 69.5 | 71.4 | 75 | 78.4 | 79.6 | 80.4 | 75.9 | 69.7 | 64 | 56.7 | 56.9 | 57.9 | 58.8 | 61.7 | 64.8 | 68.4 | 68.7 | 68.7 | 64.8 | 60 | 57.1 | 63.6 | 63.6 | 64.9 | 67.3 | 69.4 | 72.3 | 76.9 | 78 | 78.3 | 73.5 | 68 | 62.8 | 18.2 | 16.3 | 14.9 | 14.3 | 12.2 | 11.5 | 12.3 | 13.2 | 14.5 | 15.7 | 17.9 | 17.6 | 27 | 25.3 | 24.5 | 24.3 | 19.6 | 15.4 | 15.8 | 17.3 | 20.8 | 26 | 26.8 | 24.5 | 11.8 | 11.3 | 10.6 | 9.7 | 7.9 | 6.2 | 5.7 | 6.2 | 7.5 | 10.2 | 11.5 | 12.5 | 18.4 | 17.5 | 16.3 | 16.9 | 15.4 | 15 | 14.2 | 15.3 | 17.8 | 18.5 | 18.5 | 16 | 10 | 9.3 | 8.4 | 7.9 | 6.7 | 6.3 | 5.4 | 6 | 7 | 8.5 | 9.5 | 9.7 | 0.323 | 0.333 | 0.357 | 0.363 | 0.362 | 0.377 | 0.383 | 0.368 | 0.353 | 0.354 | 0.312 | 0.311 | 2.537 | 2.522 | 2.43 | 2.42 | 2.454 | 2.416 | 2.466 | 2.493 | 2.526 | 2.499 | 2.609 | 2.611 | 283 | 292 | 292 | 293 | 293 | 287 | 284 | 288 | 289 | 280 | 286 | 283 | 26 | 30 | 35 | 37 | 36 | 37 | 35 | 34 | 31 | 30 | 24 | 23 | 1016 | 1295 | 1729 | 2100 | 2246 | 2357 | 2355 | 2244 | 1896 | 1440 | 1123 | 919 | 69 | 126 | 91 | 107 | 154 | 147 | 124 | 64 | 77 | 105 | 68 | 69 | 1.42 | N/A | N/A | 3.38 | N/A | N/A | N/A | -284 | 558 | 306 | 1.13 | N/A | -3.06 | 1.3 | N/A | N/A | N/A | -202 | 401 | 202 | 50
| NEEDLES_STYP20 | 15 | 4 | USA | CA | NEEDLES | 723805 | 23179 | 34.768 | -114.619 | 890 | 14.23 | -8 | NAP | 01-19 | 1B | 12 | 37.4 | 40.3 | -1.8 | 5.2 | 65.3 | 2.3 | 6.4 | 66.4 | 30.2 | 58.1 | 27 | 58.4 | 5.4 | 240 | 0.505 | 7 | 22.5 | 114.7 | 69.6 | 112.3 | 69.3 | 110.2 | 69 | 76.9 | 99.3 | 75.3 | 98.4 | 74.3 | 98.5 | 9.7 | 220 | 71 | 118 | 86.6 | 68.4 | 107.8 | 88.8 | 65.8 | 98.3 | 91.5 | 40.7 | 98.9 | 39.4 | 97.9 | 38.3 | 98.1 | 82.6 | 25.9 | 22.5 | 19.2 | 31.9 | 119 | 3.2 | 2.1 | 29.6 | 120.5 | 27.7 | 121.8 | 25.9 | 122.9 | 23.6 | 124.5 | 25 | 78.1 | 2.8 | 2.1 | 23 | 79.7 | 21.4 | 80.9 | 19.8 | 82.1 | 17.8 | 83.6 | 75.8 | 55.7 | 59 | 66.6 | 73.5 | 82.4 | 93.2 | 98.3 | 96.4 | 89.4 | 76.2 | 64 | 54 | 16.6 | 5.79 | 6.32 | 6.96 | 6.89 | 7.25 | 5.6 | 4.49 | 4.47 | 5.79 | 6.51 | 6.8 | 5.67 | 52 | 19 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 26 | 998 | 291 | 184 | 67 | 12 | 0 | 0 | 0 | 0 | 0 | 5 | 98 | 341 | 9471 | 195 | 256 | 514 | 704 | 1006 | 1296 | 1496 | 1438 | 1183 | 812 | 421 | 150 | 4943 | 2 | 15 | 116 | 266 | 541 | 846 | 1031 | 973 | 733 | 352 | 67 | 1 | 79763 | 21 | 188 | 1354 | 3344 | 8160 | 14925 | 18695 | 17090 | 11460 | 3942 | 575 | 9 | 54574 | 1 | 27 | 498 | 1612 | 5005 | 10793 | 14247 | 12687 | 7645 | 1912 | 147 | 0 | 8.1 | 8.1 | 7.9 | 8.3 | 9.2 | 9 | 8.7 | 8.1 | 7.6 | 7.2 | 7.8 | 7.6 | 7.6 | 4.6 | 0.6 | 0.6 | 0.5 | 0.2 | 0.1 | 0 | 0.3 | 0.6 | 0.5 | 0.3 | 0.4 | 0.4 | 9.6 | 3.6 | 3.6 | 3.2 | 2.8 | 0.7 | 0.5 | 2.2 | 3.4 | 4.7 | 1.7 | 1.7 | 2.6 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0.9 | 0.8 | 0.7 | 0.6 | 0.2 | 0.1 | 0.5 | 0.9 | 0.9 | 0.4 | 0.4 | 0.6 | 76.7 | 83.3 | 94.2 | 101 | 109.3 | 118.2 | 118.9 | 115.4 | 110.8 | 100.4 | 88.5 | 75.3 | 52.5 | 55 | 59.8 | 61 | 66.9 | 67 | 71.1 | 70.3 | 68.8 | 65.1 | 59 | 55.1 | 72.9 | 79.6 | 89.2 | 96.7 | 105.8 | 113.4 | 115.4 | 113.1 | 107.9 | 96.6 | 84.2 | 71.1 | 51.1 | 53.8 | 57.6 | 59.9 | 64 | 65.9 | 70.7 | 70.8 | 68.1 | 63.2 | 57 | 51.8 | 69.8 | 75.7 | 85.5 | 92.8 | 102.3 | 110.9 | 113 | 110.9 | 105.8 | 93.4 | 80.8 | 67.6 | 50 | 52.2 | 56.2 | 58.4 | 62.7 | 65.9 | 70.6 | 70.3 | 68 | 61.9 | 56.1 | 50.2 | 66.7 | 71.9 | 82 | 89 | 99 | 108.3 | 110.4 | 108.6 | 103.3 | 90.3 | 76.8 | 64.4 | 48.9 | 51 | 54.7 | 57.2 | 61.7 | 65.5 | 70.1 | 70.2 | 67.5 | 60.9 | 54.3 | 48.5 | 57.8 | 59.3 | 61.8 | 65 | 70.9 | 73.2 | 78.6 | 79.3 | 76 | 69.8 | 62.2 | 57.5 | 66.3 | 72.6 | 87.6 | 91.7 | 104 | 105.9 | 107 | 101.8 | 95.8 | 86.5 | 79.8 | 67.6 | 55.4 | 56.6 | 59.2 | 61.5 | 66.5 | 70.8 | 76.5 | 77.4 | 73.9 | 67.2 | 59.4 | 55.3 | 64.5 | 69.7 | 83.3 | 89.8 | 99.6 | 105.6 | 100.1 | 98.6 | 95.1 | 87.1 | 79.5 | 65.8 | 53.2 | 54.5 | 57.3 | 59.9 | 64.2 | 68.8 | 75.2 | 75.8 | 72.5 | 65.2 | 57.3 | 53 | 64.6 | 69.4 | 81.9 | 87.6 | 97.9 | 104.6 | 98.9 | 98.3 | 94.8 | 87.7 | 75.9 | 63.7 | 51.1 | 52.8 | 55.8 | 58.4 | 62.4 | 67.2 | 74.2 | 74.6 | 71 | 63.2 | 55.6 | 50.7 | 63 | 68.7 | 78.8 | 85.7 | 96 | 103.7 | 99.4 | 98 | 94.7 | 85.4 | 74.2 | 61.5 | 19.7 | 21.6 | 24.5 | 24.7 | 25.2 | 26 | 22.5 | 22.8 | 24.3 | 23.7 | 21.7 | 18.6 | 23 | 27.1 | 29.6 | 29.4 | 29.5 | 28.7 | 25.3 | 25.1 | 26.6 | 26.9 | 25.4 | 21.8 | 11.4 | 12.7 | 12.6 | 12.4 | 11.7 | 10.1 | 8.9 | 8.8 | 10.3 | 12 | 11.9 | 10.8 | 19.3 | 22.5 | 26.9 | 26.4 | 27.6 | 25.8 | 20.8 | 21.3 | 22 | 22.7 | 22.6 | 18.4 | 10.1 | 10.9 | 11.7 | 11.5 | 12.7 | 11.5 | 7.5 | 7.5 | 9.2 | 10.8 | 11 | 9.7 | 0.273 | 0.276 | 0.29 | 0.324 | 0.335 | 0.334 | 0.384 | 0.379 | 0.338 | 0.301 | 0.277 | 0.272 | 2.598 | 2.612 | 2.546 | 2.422 | 2.419 | 2.424 | 2.394 | 2.401 | 2.484 | 2.564 | 2.606 | 2.615 | 302 | 312 | 314 | 305 | 301 | 299 | 284 | 284 | 292 | 298 | 298 | 296 | 24 | 26 | 30 | 36 | 37 | 37 | 38 | 37 | 32 | 27 | 23 | 22 | 1039 | 1353 | 1821 | 2259 | 2552 | 2709 | 2407 | 2235 | 1978 | 1531 | 1153 | 926 | 68 | 101 | 80 | 80 | 82 | 89 | 106 | 94 | 71 | 73 | 48 | 63 | N/A | N/A | -4.75 | N/A | -1.8 | N/A | N/A | N/A | N/A | N/A | 0.7 | N/A | -3.06 | N/A | -0.74 | N/A | N/A | N/A | 257 | 144 | 12
| EDWARDS-AFB_STYP20 | 14 | 4 | USA | CA | EDWARDS AFB | 723810 | 23114 | 34.9 | -117.867 | 2311 | 13.51 | -8 | NAP | 94-19 | 3B | 12 | 21.7 | 25.3 | -6.1 | 4.3 | 39.7 | -1.3 | 5.6 | 42.8 | 30.6 | 51 | 27.4 | 51.6 | 3.1 | 0 | 0.592 | 7 | 32 | 105 | 64.6 | 102.3 | 63.7 | 100 | 63 | 68.9 | 92.8 | 67.5 | 93.5 | 66 | 93.2 | 12.2 | 240 | 61.6 | 89.2 | 76.5 | 57.6 | 77.2 | 78.3 | 54.7 | 69.2 | 77.4 | 34.3 | 92.1 | 33 | 93.7 | 31.8 | 92.8 | 75.2 | 28.2 | 25.7 | 23.5 | 14.8 | 109.6 | 4.4 | 2 | 11.6 | 111.1 | 9.1 | 112.2 | 6.6 | 113.4 | 3.4 | 114.8 | 12.5 | 71.9 | 4.3 | 1.8 | 9.4 | 73.2 | 6.9 | 74.3 | 4.4 | 75.3 | 1.3 | 76.7 | 63.1 | 45.6 | 48.6 | 54.9 | 60.3 | 67.6 | 77.6 | 83.9 | 83 | 75.3 | 62.9 | 52.1 | 43.8 | 15.21 | 5.73 | 6.13 | 6.31 | 7.46 | 7.47 | 7.09 | 4.49 | 4.31 | 6.24 | 6.44 | 6.61 | 6.27 | 551 | 158 | 91 | 27 | 9 | 0 | 0 | 0 | 0 | 0 | 2 | 54 | 210 | 2787 | 602 | 460 | 317 | 177 | 61 | 6 | 0 | 0 | 7 | 114 | 387 | 656 | 5318 | 21 | 52 | 178 | 317 | 547 | 829 | 1051 | 1022 | 760 | 404 | 118 | 19 | 2076 | 0 | 0 | 3 | 35 | 142 | 385 | 586 | 557 | 317 | 50 | 1 | 0 | 30067 | 1 | 17 | 211 | 741 | 2086 | 5453 | 8260 | 7755 | 4298 | 1130 | 114 | 1 | 17657 | 0 | 2 | 36 | 252 | 983 | 3310 | 5267 | 4940 | 2429 | 428 | 10 | 0 | 10 | 7 | 9.1 | 10.4 | 12.7 | 13.5 | 13.1 | 11.7 | 10.7 | 9 | 8.2 | 7.1 | 7.1 | 5.7 | 1.1 | 1.4 | 0.6 | 0.3 | 0.1 | 0 | 0.2 | 0.1 | 0.2 | 0.3 | 0.3 | 0.8 | 13 | 5.9 | 6 | 2.3 | 1 | 0.9 | 0.5 | 0.9 | 0.4 | 1.3 | 2 | 1.1 | 3.6 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4 | 1.5 | 1.5 | 0.6 | 0.3 | 0.2 | 0.1 | 0.2 | 0.2 | 0.4 | 0.5 | 0.3 | 0.9 | 70.3 | 76.4 | 84.2 | 90.9 | 98.8 | 107.1 | 108.9 | 107.8 | 101.5 | 93.2 | 81.4 | 70.8 | 50.7 | 51.6 | 54.5 | 57.7 | 61.6 | 64.8 | 65.6 | 65.8 | 64.2 | 58.9 | 54 | 51.3 | 66.1 | 72.3 | 79.6 | 86.5 | 93.8 | 102.7 | 105.4 | 104.2 | 98.8 | 89.1 | 77.4 | 64.9 | 47.9 | 50.3 | 53 | 55.7 | 59.2 | 62.4 | 64.9 | 64.6 | 63.3 | 58 | 52 | 48.1 | 63 | 68 | 75.5 | 82.4 | 90.1 | 99.6 | 102.5 | 101.8 | 96.3 | 85.1 | 73.1 | 61.1 | 46.9 | 49.1 | 51.7 | 54.3 | 58.3 | 61.5 | 64.1 | 63.7 | 62.3 | 56.1 | 51 | 46.6 | 59.1 | 63.3 | 71.6 | 78.1 | 85.9 | 96.2 | 99.9 | 99.4 | 93.2 | 81.1 | 68.1 | 57.1 | 46 | 47.3 | 50.8 | 53.1 | 57.2 | 60.7 | 63.5 | 62.9 | 61 | 54.9 | 49 | 45.1 | 55.7 | 55.4 | 57.1 | 60.2 | 63.8 | 67.8 | 71.4 | 70.4 | 69.3 | 64 | 57.3 | 55.5 | 62.5 | 66.5 | 73.4 | 84.1 | 93.5 | 100.2 | 91 | 93.6 | 90.7 | 80.7 | 68.4 | 61.6 | 52.6 | 52.9 | 55.1 | 57.9 | 61.2 | 65.2 | 69.3 | 68.6 | 67.5 | 60.9 | 54.5 | 52.5 | 59.6 | 64.4 | 72.8 | 80.3 | 88.4 | 95.6 | 92 | 94.1 | 87.7 | 79.4 | 71.2 | 60.1 | 50.3 | 50.9 | 53.5 | 56.1 | 59.6 | 63.5 | 67.7 | 66.9 | 65.7 | 58.7 | 52.6 | 50.1 | 57.1 | 63.4 | 71.3 | 77.6 | 85.9 | 93.8 | 94.2 | 95.1 | 87.2 | 79.2 | 68.3 | 57.1 | 48.2 | 49.2 | 51.9 | 54.4 | 58.1 | 62.1 | 66.1 | 65.2 | 63.8 | 56.7 | 50.8 | 47.6 | 55.6 | 60.7 | 68 | 74.7 | 82.6 | 91.3 | 94 | 94.7 | 86.2 | 75.9 | 65.2 | 54.7 | 26.9 | 26.3 | 28.6 | 28.6 | 29 | 32.2 | 32 | 33.2 | 32.7 | 32.6 | 31.1 | 26.6 | 33.8 | 35.3 | 36.8 | 36.3 | 35.1 | 36 | 34.7 | 35.3 | 35.6 | 39 | 37.9 | 32.4 | 19.2 | 17.6 | 16.2 | 14.7 | 12.6 | 11.5 | 11 | 12.1 | 13.4 | 17.4 | 20.2 | 18.9 | 23.3 | 27.7 | 31.2 | 31.9 | 32.9 | 33.8 | 29 | 30.6 | 29.2 | 31.4 | 31.7 | 23.5 | 14.4 | 14.6 | 14.4 | 13.1 | 12 | 11.4 | 11 | 11.8 | 11 | 14 | 17.1 | 14.8 | 0.273 | 0.283 | 0.298 | 0.32 | 0.335 | 0.33 | 0.353 | 0.34 | 0.325 | 0.302 | 0.277 | 0.276 | 2.548 | 2.538 | 2.485 | 2.424 | 2.405 | 2.432 | 2.414 | 2.429 | 2.464 | 2.515 | 2.56 | 2.556 | 301 | 309 | 311 | 306 | 301 | 300 | 293 | 296 | 297 | 297 | 296 | 293 | 25 | 28 | 32 | 36 | 37 | 36 | 37 | 36 | 33 | 29 | 24 | 23 | 986 | 1284 | 1750 | 2166 | 2445 | 2661 | 2502 | 2348 | 2003 | 1512 | 1125 | 898 | 74 | 128 | 88 | 89 | 106 | 105 | 107 | 65 | 49 | 80 | 46 | 65 | N/A | N/A | -5.47 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | N/A | -3.35 | 1.15 | N/A | N/A | N/A | -202 | 392 | 189 | 44
| BARSTOW-DAGGETT_STYP20 | 14 | 4 | USA | CA | BARSTOW-DAGGETT | 723815 | 23161 | 34.854 | -116.786 | 1917 | 13.71 | -8 | NAP | 94-19 | 2B | 12 | 29.6 | 32.5 | -1.9 | 5.3 | 49.9 | 1.3 | 6.3 | 48.8 | 34.7 | 54.7 | 32.1 | 55 | 5.5 | 270 | 0.588 | 7 | 29.2 | 108.9 | 67.9 | 106.6 | 66.9 | 104.4 | 65.9 | 72.5 | 98.5 | 70.9 | 97.2 | 69.4 | 96 | 10.8 | 280 | 65 | 99.5 | 81.7 | 62.2 | 89.9 | 84.7 | 58.5 | 78.5 | 88.5 | 37.2 | 98.8 | 35.9 | 96.5 | 34.5 | 96.3 | 91.6 | 32.1 | 27.7 | 24.7 | 23.3 | 113.4 | 3.7 | 2 | 20.6 | 114.8 | 18.5 | 116 | 16.4 | 117.1 | 13.7 | 118.5 | 18.9 | 76.3 | 3.3 | 5 | 16.5 | 79.9 | 14.6 | 82.8 | 12.7 | 85.7 | 10.3 | 89.3 | 68.5 | 49.7 | 52.9 | 59.9 | 65.6 | 74.4 | 84.2 | 90 | 88.8 | 81.3 | 68.8 | 56.8 | 48.2 | 15.95 | 5.84 | 6.47 | 6.98 | 7.66 | 7.86 | 6.75 | 4.25 | 4.06 | 6.23 | 7.07 | 7.24 | 5.74 | 250 | 77 | 40 | 6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 104 | 1925 | 476 | 339 | 188 | 85 | 16 | 1 | 0 | 0 | 1 | 42 | 256 | 521 | 6992 | 66 | 122 | 313 | 469 | 756 | 1025 | 1240 | 1203 | 939 | 584 | 227 | 48 | 3189 | 0 | 1 | 29 | 104 | 306 | 576 | 775 | 738 | 489 | 161 | 10 | 0 | 46479 | 4 | 51 | 484 | 1375 | 4016 | 8495 | 12201 | 11251 | 6508 | 1889 | 201 | 4 | 28829 | 0 | 4 | 117 | 554 | 2175 | 5485 | 8282 | 7492 | 3879 | 804 | 37 | 0 | 10.8 | 7.8 | 9.6 | 11.6 | 14.2 | 14.5 | 14 | 11.5 | 10.8 | 10.2 | 9.4 | 8.3 | 7.7 | 3.9 | 0.5 | 0.6 | 0.5 | 0.2 | 0.1 | 0.1 | 0.4 | 0.3 | 0.5 | 0.2 | 0.3 | 0.4 | 7.5 | 2.5 | 2.5 | 1.9 | 1.8 | 0.5 | 1.3 | 2 | 1.3 | 3.3 | 1 | 1.7 | 2 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6 | 0.6 | 0.7 | 0.5 | 0.4 | 0.1 | 0.2 | 0.4 | 0.4 | 0.8 | 0.2 | 0.4 | 0.5 | 72.7 | 79.2 | 88.3 | 95.1 | 103.7 | 110.9 | 112.6 | 110.2 | 104.8 | 96.3 | 83.9 | 72.7 | 52.3 | 52.9 | 57 | 60.3 | 65.4 | 65.3 | 69.4 | 69.9 | 66.2 | 62.2 | 55.2 | 53 | 69.1 | 75 | 83.1 | 90.6 | 99.3 | 106.9 | 109.7 | 107.9 | 102 | 91.8 | 79.5 | 67.5 | 49.7 | 51.7 | 55 | 58.1 | 62.9 | 65.4 | 68.5 | 67.9 | 65.5 | 60.4 | 53.7 | 49.9 | 65.8 | 70.9 | 79.4 | 86.5 | 95.7 | 104.3 | 107.4 | 105.7 | 99.6 | 88.4 | 75.3 | 63.9 | 47.9 | 50.1 | 53.5 | 56.4 | 60.6 | 64.4 | 67.7 | 66.5 | 64.9 | 58.7 | 52.4 | 47.9 | 62.4 | 66.6 | 75.6 | 82.2 | 91.7 | 101.3 | 104.7 | 103.2 | 97 | 84.4 | 71.2 | 60.3 | 46.8 | 48.4 | 52.3 | 54.8 | 59.6 | 63.4 | 66.8 | 65.6 | 63.4 | 56.9 | 50.7 | 46 | 55.5 | 56.5 | 58.9 | 62.2 | 69.2 | 72.3 | 75.2 | 74.3 | 71.5 | 65.9 | 58.2 | 55.7 | 67.7 | 71.6 | 80.1 | 90.4 | 100.8 | 104.8 | 102.3 | 100 | 92.7 | 85 | 75.7 | 67.7 | 52.7 | 53.8 | 56.6 | 59.5 | 64.4 | 68.6 | 72.9 | 72.1 | 69.8 | 62.8 | 55.7 | 52.9 | 63 | 68.8 | 77.9 | 86.6 | 94.5 | 101.9 | 98.7 | 98.2 | 92 | 85.3 | 74.7 | 63.3 | 50.6 | 51.8 | 54.8 | 57.4 | 61.9 | 66.2 | 71.2 | 70.5 | 68.3 | 60.5 | 53.6 | 50.4 | 60.6 | 66.4 | 75.9 | 82.6 | 91.5 | 99.7 | 97.6 | 97 | 91 | 83.9 | 72.2 | 60.4 | 48.5 | 50 | 53.2 | 55.6 | 60.1 | 64.2 | 69.7 | 69 | 66.3 | 58.6 | 51.9 | 47.9 | 59.2 | 63.9 | 73 | 79.4 | 88.7 | 97.3 | 96.6 | 95.8 | 90.1 | 80.8 | 68.9 | 57.2 | 23.5 | 23.9 | 26 | 26.7 | 27.9 | 30.1 | 29.2 | 29.2 | 28.4 | 27.2 | 25.6 | 22.9 | 27.7 | 29.6 | 30.6 | 31.5 | 31.7 | 32.5 | 31.5 | 30.5 | 29.9 | 30.6 | 29.6 | 26.8 | 14.2 | 13.8 | 12.5 | 12.2 | 11.4 | 11 | 11.2 | 11 | 10.9 | 12.8 | 14.1 | 14.5 | 22.1 | 25.2 | 28.3 | 29.3 | 30.5 | 31.5 | 27.2 | 27 | 26.6 | 27.7 | 26.9 | 22.6 | 12.1 | 12.2 | 12 | 11.7 | 12.3 | 12.7 | 12.2 | 12 | 10.7 | 11.8 | 13 | 12.6 | 0.273 | 0.282 | 0.294 | 0.326 | 0.336 | 0.337 | 0.371 | 0.351 | 0.33 | 0.309 | 0.275 | 0.274 | 2.546 | 2.534 | 2.492 | 2.391 | 2.391 | 2.405 | 2.376 | 2.417 | 2.456 | 2.489 | 2.576 | 2.565 | 301 | 309 | 312 | 304 | 300 | 298 | 287 | 292 | 295 | 294 | 298 | 294 | 25 | 28 | 32 | 37 | 38 | 37 | 38 | 36 | 33 | 29 | 24 | 23 | 1028 | 1343 | 1814 | 2244 | 2523 | 2700 | 2462 | 2306 | 2008 | 1544 | 1152 | 929 | 74 | 114 | 73 | 69 | 91 | 96 | 111 | 84 | 62 | 71 | 46 | 58 | N/A | N/A | -3.01 | N/A | -0.97 | N/A | N/A | N/A | N/A | N/A | 1.12 | N/A | -3.29 | 1.03 | N/A | N/A | N/A | -178 | 391 | 211 | 40
| LANCASTER-FOX_STYP20 | 14 | 4 | USA | CA | LANCASTER FOX | 723816 | 03159 | 34.741 | -118.212 | 2338 | 13.5 | -8 | NAP | 94-19 | 3B | 12 | 21.3 | 24.9 | -2.7 | 5.2 | 39.1 | 1.4 | 6.4 | 42.8 | 32.9 | 50.9 | 28.9 | 51.6 | 3 | 270 | 0.631 | 7 | 29 | 103.5 | 65.7 | 100.9 | 64.5 | 98.6 | 63.6 | 68.6 | 95.9 | 67.2 | 94.9 | 65.8 | 93.7 | 13.9 | 220 | 59 | 81.2 | 80.1 | 55.9 | 72.6 | 80.9 | 53.6 | 66.5 | 79.6 | 34 | 94.9 | 32.8 | 95 | 31.6 | 93.4 | 76.8 | 30.2 | 27.1 | 25 | 15.2 | 108.9 | 4 | 1.9 | 12.3 | 110.3 | 10 | 111.4 | 7.7 | 112.4 | 4.8 | 113.8 | 12.1 | 71.1 | 3.7 | 1.9 | 9.4 | 72.4 | 7.3 | 73.5 | 5.2 | 74.6 | 2.6 | 75.9 | 62.5 | 45.5 | 48.1 | 54 | 59.1 | 67.6 | 76.9 | 83.2 | 81.8 | 74.4 | 62.7 | 51.6 | 44.1 | 15.03 | 5.73 | 5.89 | 6.45 | 7.28 | 8.05 | 7.56 | 4.91 | 4.54 | 6.07 | 6.58 | 6.71 | 6.01 | 564 | 160 | 97 | 34 | 10 | 0 | 0 | 0 | 0 | 0 | 2 | 60 | 201 | 2883 | 604 | 475 | 343 | 204 | 69 | 9 | 0 | 0 | 7 | 122 | 402 | 648 | 5125 | 21 | 43 | 158 | 283 | 544 | 806 | 1030 | 987 | 731 | 396 | 109 | 17 | 1968 | 0 | 0 | 3 | 26 | 148 | 365 | 565 | 522 | 287 | 51 | 1 | 0 | 28071 | 1 | 14 | 177 | 567 | 1967 | 4829 | 7830 | 7312 | 4115 | 1155 | 104 | 0 | 15814 | 0 | 1 | 30 | 176 | 909 | 2744 | 4766 | 4462 | 2281 | 436 | 9 | 0 | 10.9 | 7.4 | 9.5 | 11.5 | 14.1 | 15 | 14.8 | 12.9 | 11.4 | 9.8 | 9.1 | 8.1 | 7.7 | 7.5 | 1.2 | 1.9 | 1.4 | 0.4 | 0.1 | 0 | 0.1 | 0.1 | 0.2 | 0.3 | 0.5 | 1.1 | 14.4 | 4.6 | 6.2 | 5.6 | 1.8 | 1.1 | 0.8 | 0.9 | 1 | 1.3 | 2.4 | 2.1 | 5.4 | 1.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 1.1 | 2.1 | 1.5 | 0.5 | 0.3 | 0.2 | 0.2 | 0.2 | 0.4 | 0.5 | 0.6 | 1.4 | 70.3 | 75.8 | 84.3 | 90.2 | 98.1 | 105.5 | 107.6 | 105.9 | 101.1 | 93 | 81.3 | 70.1 | 49.8 | 51.1 | 55 | 58.5 | 62.5 | 65 | 67.7 | 67.5 | 64.6 | 60.2 | 53.9 | 51.4 | 66.3 | 71.9 | 79 | 85 | 93.4 | 100.4 | 104.1 | 102.8 | 98.4 | 88.9 | 77.2 | 65.3 | 47.4 | 50 | 53.6 | 55.9 | 60.4 | 63.3 | 66.2 | 65.6 | 63.5 | 58.2 | 52.1 | 48.1 | 63.2 | 67.3 | 74.9 | 80.9 | 89.6 | 97.3 | 101.1 | 100.3 | 95.6 | 85 | 72.7 | 61.5 | 46.7 | 48.3 | 52 | 54.4 | 59.3 | 62.4 | 65 | 64.3 | 62.3 | 56.5 | 50.8 | 46 | 59.1 | 62.5 | 70.3 | 76.1 | 85.1 | 94 | 98.3 | 97.9 | 92.6 | 81 | 67.8 | 57.8 | 45.1 | 46.8 | 50.5 | 53 | 57.6 | 61.3 | 64.1 | 63.4 | 61 | 54.9 | 48.8 | 45.2 | 53.9 | 54.5 | 57.2 | 60.4 | 64.4 | 67.3 | 71 | 70.4 | 68.5 | 63.8 | 56.5 | 54.5 | 63.7 | 66.6 | 77.7 | 83.7 | 92.9 | 99.3 | 97.7 | 98.2 | 94 | 80.6 | 72.8 | 63.5 | 51.4 | 52 | 55.1 | 57.9 | 62.3 | 65.6 | 69.1 | 68.2 | 66.4 | 60.5 | 54.2 | 51.8 | 59.6 | 66.1 | 73.9 | 80.2 | 89.7 | 95.8 | 96.1 | 96.4 | 91.5 | 82.1 | 70.4 | 60.3 | 49.3 | 50.2 | 53.5 | 55.9 | 60.3 | 64.1 | 67.7 | 66.6 | 64.6 | 58.6 | 52.3 | 49.4 | 57.8 | 63.3 | 71 | 76.4 | 86.1 | 93.5 | 94.6 | 95.8 | 89.4 | 79.7 | 68.1 | 57.1 | 47.2 | 48.5 | 51.7 | 54.1 | 58.8 | 62.4 | 66.2 | 65 | 62.7 | 56.7 | 50.6 | 46.8 | 56.5 | 59.9 | 67.3 | 73.1 | 82.6 | 90.4 | 93.1 | 94.5 | 87.6 | 76.5 | 65.3 | 55.4 | 26.7 | 25.4 | 26.9 | 26.6 | 26.5 | 28.3 | 29 | 31.3 | 32.6 | 32.2 | 30 | 26.5 | 34.6 | 36.3 | 36.6 | 35.6 | 33.5 | 32.8 | 33.1 | 34.7 | 37.1 | 39.2 | 38.2 | 33.1 | 19.9 | 19 | 17.2 | 15.5 | 13.3 | 12.2 | 12.3 | 13.7 | 15.3 | 18.2 | 19.9 | 19.5 | 24.2 | 28.6 | 30.6 | 30.3 | 30.9 | 30.7 | 28.4 | 30.6 | 32.1 | 32.7 | 30.9 | 23.8 | 15 | 15.7 | 15 | 13.8 | 12.6 | 12 | 11.2 | 13.2 | 13.9 | 15.3 | 16.5 | 15.1 | 0.292 | 0.302 | 0.32 | 0.347 | 0.361 | 0.355 | 0.382 | 0.362 | 0.347 | 0.332 | 0.299 | 0.292 | 2.504 | 2.491 | 2.432 | 2.358 | 2.342 | 2.373 | 2.342 | 2.374 | 2.412 | 2.434 | 2.509 | 2.523 | 293 | 301 | 303 | 297 | 292 | 293 | 284 | 289 | 289 | 285 | 287 | 286 | 26 | 30 | 34 | 39 | 40 | 39 | 40 | 38 | 35 | 31 | 26 | 24 | 977 | 1263 | 1723 | 2128 | 2403 | 2626 | 2504 | 2353 | 1996 | 1501 | 1118 | 891 | 75 | 139 | 98 | 101 | 119 | 116 | 103 | 60 | 46 | 84 | 48 | 67 | N/A | N/A | -3.46 | N/A | N/A | 2.12 | N/A | N/A | N/A | N/A | 1.13 | N/A | -3.2 | 1.19 | N/A | N/A | N/A | -207 | 401 | 191 | 46
| PALMDALE_STYP20 | 14 | 4 | USA | CA | PALMDALE | 723820 | 23182 | 34.629 | -118.084 | 2524 | 13.4 | -8 | NAP | 94-19 | 3B | 12 | 25.3 | 28 | -1.2 | 5.7 | 48 | 2.7 | 6.9 | 47.4 | 32.2 | 48.2 | 28.2 | 48.9 | 3.6 | 200 | 0.573 | 7 | 28.6 | 102.4 | 65.2 | 100.1 | 64.8 | 98 | 64 | 69.9 | 93.8 | 68.2 | 92.7 | 66.6 | 91.8 | 14.1 | 250 | 62.7 | 93.6 | 80.1 | 59.1 | 82.1 | 80.5 | 55.6 | 72.3 | 81.3 | 35.3 | 93.2 | 33.8 | 92.5 | 32.4 | 91.7 | 85.1 | 28.3 | 25.5 | 23.4 | 20.1 | 107.4 | 2.9 | 2 | 18 | 108.8 | 16.3 | 110 | 14.7 | 111.1 | 12.6 | 112.6 | 17 | 73.1 | 2.7 | 4.5 | 15 | 76.4 | 13.4 | 79 | 11.8 | 81.5 | 9.9 | 84.8 | 62.9 | 46.5 | 48.6 | 54.3 | 59.3 | 67.3 | 76.2 | 83.1 | 82.1 | 75.2 | 63.8 | 52.8 | 45.2 | 14.69 | 5.79 | 5.98 | 6.49 | 7.42 | 7.63 | 6.99 | 4.83 | 4.63 | 6.57 | 6.43 | 6.78 | 5.92 | 494 | 138 | 91 | 33 | 11 | 0 | 0 | 0 | 0 | 0 | 2 | 47 | 172 | 2730 | 575 | 459 | 333 | 200 | 67 | 7 | 0 | 0 | 8 | 100 | 366 | 615 | 5218 | 28 | 52 | 168 | 288 | 537 | 786 | 1025 | 995 | 756 | 429 | 132 | 22 | 1979 | 0 | 0 | 2 | 28 | 139 | 343 | 560 | 530 | 314 | 62 | 1 | 0 | 27842 | 3 | 16 | 154 | 574 | 1965 | 4723 | 7832 | 7263 | 4151 | 1056 | 103 | 2 | 15444 | 0 | 1 | 23 | 175 | 902 | 2639 | 4718 | 4352 | 2260 | 365 | 9 | 0 | 9.8 | 7.2 | 9 | 10.4 | 12.3 | 12.8 | 12.3 | 11 | 10 | 8.8 | 8.6 | 7.4 | 7.5 | 7 | 1.3 | 1.3 | 1.1 | 0.4 | 0.1 | 0 | 0 | 0.2 | 0.2 | 0.2 | 1 | 1 | 15.6 | 4.7 | 6.4 | 5.2 | 2.5 | 1.7 | 0.7 | 0.5 | 1.5 | 2.1 | 2 | 5.6 | 5.3 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 1.3 | 1.6 | 1.3 | 0.6 | 0.3 | 0.2 | 0.1 | 0.4 | 0.5 | 0.5 | 1.2 | 1.3 | 71.4 | 76.1 | 83.8 | 90 | 98.2 | 103.9 | 106.8 | 105.5 | 100.4 | 91.4 | 81.2 | 71.1 | 50.3 | 51.2 | 54.7 | 57.9 | 63.7 | 63.6 | 67.5 | 68.4 | 65 | 59.4 | 53.2 | 50.6 | 66.9 | 71.6 | 78.7 | 84.8 | 93.2 | 99.6 | 103.2 | 101.8 | 97.7 | 87.9 | 77.1 | 65.7 | 47.8 | 49.3 | 53.5 | 55.6 | 60.9 | 63.4 | 65.6 | 65.4 | 64.3 | 58 | 51.7 | 48.3 | 63.7 | 66.8 | 74.7 | 81.1 | 89.9 | 96.8 | 100.3 | 99.5 | 95.2 | 84.1 | 72.7 | 62.3 | 46.6 | 48.1 | 52.1 | 54.5 | 59.6 | 62.3 | 65 | 65 | 62.3 | 56.3 | 50.5 | 46.2 | 59.7 | 62.5 | 70.4 | 76.2 | 85.6 | 93.2 | 97.9 | 97.1 | 92.1 | 80.6 | 68 | 57.8 | 45.3 | 46.5 | 50.8 | 52.8 | 57.5 | 61.4 | 64.3 | 63.8 | 61.7 | 54.9 | 48.8 | 45 | 53.8 | 54.6 | 57.6 | 60.3 | 66.4 | 69.6 | 72.5 | 72.4 | 71.2 | 64 | 56.7 | 55 | 63.4 | 64.1 | 75.8 | 82.9 | 90.3 | 93.8 | 96 | 96.1 | 91.3 | 78.1 | 72.2 | 64.1 | 51.5 | 51.7 | 55.4 | 57.8 | 63.1 | 66 | 69.9 | 69.4 | 68.1 | 60.7 | 54.1 | 52.1 | 60.3 | 65.6 | 73 | 79.2 | 90 | 93.8 | 94 | 95.1 | 89 | 80.2 | 70.1 | 60.3 | 49.6 | 50 | 53.7 | 55.8 | 60.5 | 64.1 | 68.3 | 67.6 | 66.1 | 58.7 | 52.2 | 49.5 | 58.1 | 63.1 | 70.6 | 76.5 | 85.9 | 91.9 | 93 | 93.9 | 87.5 | 78.2 | 67.7 | 57.2 | 47.5 | 48.4 | 51.9 | 54 | 58.8 | 62.4 | 66.7 | 65.8 | 64 | 56.7 | 50.6 | 47 | 57.3 | 60 | 67.8 | 73 | 82.5 | 89.4 | 92 | 93 | 85.4 | 75.7 | 65.2 | 55.6 | 25.1 | 23.9 | 25.9 | 26.6 | 27.2 | 29.3 | 28.6 | 29.6 | 30.3 | 28.8 | 27.7 | 24.4 | 31.7 | 32.7 | 33.5 | 33.9 | 33.9 | 33.3 | 31.7 | 32 | 32.8 | 34.4 | 34.1 | 30.8 | 17 | 16 | 15 | 14.2 | 13.4 | 12.5 | 11.9 | 12.9 | 12.8 | 14.7 | 16.3 | 17 | 23.2 | 26.1 | 29.3 | 29.9 | 31.8 | 31.2 | 27.4 | 29.4 | 28.8 | 28.9 | 28.2 | 23.3 | 13.6 | 13.6 | 14.1 | 13.4 | 13.1 | 12.3 | 11.8 | 13.4 | 12 | 12.5 | 14.2 | 14 | 0.286 | 0.296 | 0.314 | 0.335 | 0.346 | 0.345 | 0.365 | 0.347 | 0.334 | 0.321 | 0.288 | 0.284 | 2.521 | 2.51 | 2.447 | 2.392 | 2.388 | 2.401 | 2.393 | 2.42 | 2.453 | 2.468 | 2.543 | 2.548 | 296 | 304 | 305 | 301 | 297 | 296 | 289 | 293 | 294 | 290 | 292 | 290 | 26 | 29 | 34 | 37 | 38 | 38 | 38 | 36 | 33 | 30 | 25 | 24 | 992 | 1278 | 1740 | 2141 | 2408 | 2623 | 2496 | 2348 | 1995 | 1508 | 1128 | 904 | 75 | 137 | 95 | 97 | 115 | 116 | 105 | 62 | 47 | 84 | 49 | 65 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 362 | N/A | 1.13 | N/A | -3.2 | 1.19 | N/A | N/A | N/A | -207 | 401 | 191 | 46
| SANDBERG_STYP20 | 16 | 4 | USA | CA | SANDBERG | 723830 | 23187 | 34.744 | -118.724 | 4510 | 12.45 | -8 | NAP | 94-19 | 4A | 12 | 26.6 | 28.3 | -6.1 | 4.7 | 47 | -1.2 | 6.1 | 46.5 | 40.1 | 36.5 | 35.6 | 37.7 | 15.4 | 340 | 0.657 | 7 | 20.3 | 93.1 | 61 | 90.4 | 60.2 | 87.9 | 59.2 | 65.7 | 84.5 | 63.6 | 83.4 | 61.9 | 82.1 | 12.6 | 160 | 60.3 | 92.4 | 72 | 56.2 | 79.6 | 71.9 | 53.7 | 72.6 | 71 | 32.9 | 84.4 | 31.1 | 83.7 | 29.8 | 81.9 | 86.4 | 33.3 | 28.6 | 25.7 | 22.3 | 97.6 | 3.5 | 3 | 19.8 | 99.7 | 17.7 | 101.5 | 15.7 | 103.2 | 13.1 | 105.4 | 19.1 | 69.3 | 3.8 | 5.8 | 16.4 | 73.5 | 14.2 | 76.9 | 12.1 | 80.2 | 9.4 | 84.4 | 57.9 | 44.9 | 44.2 | 48.5 | 51.2 | 58.6 | 68.2 | 75.6 | 75.8 | 70.6 | 60.5 | 51.1 | 43.9 | 14.48 | 7.93 | 8.76 | 9.17 | 9.82 | 9.62 | 9.21 | 5.96 | 5.98 | 8.42 | 9.33 | 9.33 | 7.82 | 1027 | 197 | 207 | 144 | 105 | 30 | 3 | 0 | 0 | 1 | 22 | 98 | 220 | 3796 | 624 | 583 | 516 | 423 | 247 | 73 | 4 | 5 | 47 | 197 | 424 | 653 | 3893 | 38 | 45 | 96 | 141 | 296 | 550 | 795 | 800 | 620 | 348 | 131 | 33 | 1187 | 0 | 1 | 4 | 9 | 48 | 170 | 334 | 340 | 216 | 58 | 7 | 0 | 9865 | 0 | 3 | 13 | 50 | 345 | 1491 | 3037 | 3023 | 1599 | 292 | 12 | 0 | 3743 | 0 | 0 | 0 | 3 | 86 | 553 | 1244 | 1246 | 557 | 54 | 0 | 0 | 13.4 | 14.1 | 14.2 | 14 | 14.5 | 14.4 | 13.9 | 11.8 | 11.5 | 11.5 | 12.9 | 13.4 | 14.5 | 14.5 | 2.8 | 4 | 2.4 | 0.9 | 0.4 | 0.1 | 0.1 | 0.1 | 0.2 | 0.7 | 1.2 | 2.2 | 29.8 | 12.2 | 14.4 | 8.3 | 3 | 3.8 | 1.1 | 1.2 | 0.2 | 1 | 4.4 | 3.2 | 8 | 5.6 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 7.7 | 3.4 | 3.7 | 2 | 0.9 | 0.7 | 0.2 | 0.3 | 0 | 0.2 | 0.9 | 0.8 | 2.1 | 65.6 | 72 | 75.7 | 79.4 | 86.9 | 95.9 | 96.6 | 96.1 | 92.7 | 85.3 | 75.5 | 67.2 | 45.7 | 48.2 | 50.8 | 52.6 | 58.6 | 61.2 | 62.3 | 63 | 60.2 | 54.7 | 50.8 | 45.3 | 61.6 | 64.9 | 69.9 | 74.4 | 82.2 | 90.5 | 93 | 92.3 | 89.2 | 80.8 | 71.7 | 61.5 | 43.8 | 45.8 | 49.1 | 51.1 | 56.6 | 59.3 | 61.4 | 60.8 | 58.9 | 54.1 | 48.4 | 43.6 | 58.2 | 60.9 | 65.7 | 70.2 | 77.7 | 86.2 | 90 | 89.9 | 86.3 | 77.1 | 67.3 | 57.8 | 41.7 | 43.6 | 47.7 | 50.5 | 55.1 | 58.2 | 60.8 | 60 | 57.5 | 52.3 | 46.8 | 41.9 | 55.5 | 57 | 61.9 | 65.8 | 73.4 | 82.3 | 87 | 87.2 | 82.9 | 73.4 | 63.7 | 54.6 | 40.6 | 41.8 | 45.7 | 48.7 | 53.6 | 57.8 | 59.8 | 59 | 56.7 | 51 | 45.3 | 40.9 | 50.2 | 50.7 | 53.2 | 58.6 | 64.5 | 69.6 | 69.2 | 68.4 | 66.1 | 60.9 | 53.9 | 51.9 | 55.9 | 64.1 | 68.4 | 68 | 71.6 | 80.8 | 86.4 | 87.4 | 80.8 | 74.9 | 68.7 | 55.6 | 47.3 | 47.9 | 51 | 54.2 | 59 | 62.8 | 65.5 | 64.4 | 63 | 57.5 | 50.6 | 48.2 | 54.4 | 60 | 65.9 | 67.7 | 76.9 | 84.9 | 85.8 | 85.4 | 79.2 | 72.6 | 65.4 | 54.3 | 45.3 | 45.7 | 49.3 | 51.8 | 56.8 | 60.6 | 63.8 | 62.3 | 60.9 | 55 | 48.9 | 45.8 | 52.2 | 56.4 | 62.1 | 66.3 | 74.6 | 81.7 | 83.9 | 84.7 | 78.8 | 71.3 | 62.6 | 52.4 | 43.5 | 43.8 | 47.4 | 50 | 54.8 | 58.9 | 62 | 60.7 | 58.9 | 53 | 47.1 | 43.6 | 51 | 53.3 | 58.9 | 63.7 | 71.4 | 79.1 | 81.7 | 83 | 78.2 | 69.2 | 59.6 | 50.7 | 11.9 | 12.7 | 15.1 | 16.9 | 18.5 | 20.2 | 20.3 | 20.4 | 19.2 | 16.5 | 13.6 | 12.3 | 14.3 | 16.7 | 18.4 | 20.5 | 21.7 | 22.4 | 21.6 | 21.1 | 20.3 | 18.5 | 15.9 | 15.7 | 8.3 | 8.9 | 9.7 | 10.4 | 10.1 | 9.3 | 9 | 8.8 | 8.3 | 8.2 | 7.8 | 8.7 | 12.6 | 14.9 | 16.9 | 19 | 20.9 | 20.6 | 19.7 | 19.8 | 19.5 | 17.7 | 15.2 | 13.5 | 8.5 | 8.9 | 9.7 | 10.9 | 10.7 | 10.7 | 10.2 | 10 | 9.6 | 9.3 | 8.7 | 9.5 | 0.26 | 0.269 | 0.28 | 0.309 | 0.318 | 0.317 | 0.336 | 0.318 | 0.311 | 0.295 | 0.267 | 0.264 | 2.611 | 2.608 | 2.569 | 2.474 | 2.472 | 2.48 | 2.461 | 2.489 | 2.511 | 2.547 | 2.611 | 2.609 | 307 | 315 | 318 | 310 | 306 | 305 | 298 | 303 | 302 | 300 | 302 | 299 | 23 | 26 | 30 | 35 | 35 | 35 | 35 | 34 | 31 | 28 | 23 | 22 | 955 | 1238 | 1694 | 2102 | 2380 | 2599 | 2508 | 2355 | 1985 | 1485 | 1103 | 874 | 77 | 143 | 107 | 111 | 130 | 116 | 97 | 57 | 45 | 88 | 51 | 71 | 2.25 | N/A | -3.04 | 2.61 | N/A | N/A | -216 | -475 | 616 | 329 | 1.12 | N/A | -2.97 | 1.15 | N/A | N/A | N/A | -218 | 401 | 167 | 49
| MEADOWS-FIELD_STYP20 | 13 | 4 | USA | CA | MEADOWS FIELD | 723840 | 23155 | 35.434 | -119.054 | 489 | 14.44 | -8 | NAP | 94-19 | 3B | 12 | 33.3 | 36 | 17.7 | 13.6 | 59.7 | 22.5 | 17.2 | 55.6 | 24.6 | 60.4 | 19.7 | 58.2 | 2.6 | 130 | 0.427 | 7 | 25.7 | 103.2 | 69.8 | 100.9 | 69 | 98.6 | 68 | 73.4 | 96.8 | 71.6 | 95.4 | 70.1 | 93.7 | 11.3 | 300 | 64.9 | 93.7 | 87.5 | 62.3 | 85.4 | 85.2 | 60.3 | 79.5 | 83.8 | 37.1 | 97.1 | 35.6 | 96 | 34.2 | 93.6 | 85.1 | 18.2 | 15.5 | 12.9 | 29.2 | 108.2 | 3.3 | 1.8 | 26.8 | 109.5 | 24.8 | 110.5 | 23 | 111.5 | 20.5 | 112.9 | 27.4 | 75.4 | 3.2 | 3.9 | 25.1 | 78.2 | 23.3 | 80.4 | 21.5 | 82.6 | 19.2 | 85.4 | 66.2 | 49.8 | 53.5 | 58.7 | 63.2 | 70.8 | 78.7 | 84.9 | 83.4 | 78 | 67.3 | 56.4 | 49.2 | 13.88 | 5.53 | 5.27 | 6.15 | 7.35 | 7.34 | 7.18 | 5.32 | 5.03 | 6.44 | 6.3 | 6.05 | 5.68 | 199 | 72 | 22 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 84 | 1957 | 472 | 323 | 211 | 120 | 27 | 3 | 0 | 0 | 1 | 48 | 264 | 488 | 6122 | 65 | 119 | 275 | 397 | 644 | 860 | 1081 | 1037 | 841 | 537 | 206 | 60 | 2406 | 0 | 0 | 16 | 66 | 206 | 413 | 616 | 572 | 392 | 120 | 5 | 0 | 31099 | 3 | 22 | 245 | 817 | 2448 | 5420 | 8649 | 7596 | 4616 | 1201 | 81 | 1 | 17111 | 0 | 1 | 53 | 302 | 1122 | 3038 | 5262 | 4467 | 2427 | 427 | 12 | 0 | 5.8 | 4.6 | 5.2 | 5.7 | 6.8 | 7.1 | 7.2 | 6.9 | 6.3 | 5.8 | 5.1 | 4.3 | 4.5 | 6.1 | 1 | 1.2 | 1.1 | 0.6 | 0.2 | 0.1 | 0 | 0.1 | 0.1 | 0.3 | 0.7 | 0.7 | 13.3 | 3.9 | 5.4 | 4.3 | 2.6 | 2.4 | 0.5 | 0.3 | 1.2 | 1.1 | 1.8 | 3 | 1.8 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2 | 0.8 | 1.2 | 0.9 | 0.6 | 0.4 | 0.2 | 0 | 0.2 | 0.3 | 0.4 | 0.7 | 0.5 | 72 | 77.3 | 85.7 | 92.8 | 99.4 | 105.2 | 106.7 | 106 | 102 | 94.1 | 81.2 | 70.4 | 52.9 | 57.1 | 61.2 | 62.3 | 67.2 | 69.9 | 70.4 | 71.4 | 69 | 65.4 | 59.6 | 54.5 | 66.7 | 72 | 80.2 | 87.9 | 94.6 | 101.3 | 103.4 | 102.4 | 98.6 | 88.8 | 75.9 | 66 | 53.7 | 55.8 | 59.8 | 61 | 65.5 | 69.1 | 69.9 | 69.1 | 67.1 | 63.1 | 57.8 | 52.7 | 63.1 | 67.7 | 76 | 83.2 | 90.6 | 98 | 101.2 | 99.7 | 95.9 | 84.7 | 71.8 | 62.5 | 53 | 54.3 | 57.7 | 59.8 | 63.3 | 67.3 | 69.5 | 68.1 | 66.6 | 61.7 | 56.5 | 51.8 | 59.8 | 64.1 | 71.9 | 78.3 | 86.5 | 94.4 | 98.5 | 97 | 92.6 | 80.9 | 67.8 | 59.4 | 51.6 | 53.1 | 56.5 | 58.3 | 62.2 | 65.8 | 68.7 | 67.5 | 65.8 | 60.4 | 55.3 | 51.1 | 59.2 | 60.7 | 64.7 | 66 | 70.9 | 73.9 | 76.4 | 75.3 | 74.3 | 68.3 | 62.5 | 58.9 | 65.9 | 70.3 | 80.3 | 82.7 | 95.6 | 100.8 | 96.9 | 97.9 | 93.1 | 87.2 | 74.1 | 65.4 | 56.2 | 58.1 | 61.9 | 63.2 | 67.8 | 71.1 | 73.5 | 72.4 | 71.1 | 66 | 60.1 | 56.2 | 62 | 67.7 | 76.3 | 82.7 | 91 | 96.8 | 97.5 | 96.8 | 90.3 | 84.2 | 72.3 | 61.6 | 54.4 | 56.2 | 59.5 | 61 | 65.3 | 69.1 | 71.8 | 70.5 | 68.7 | 63.8 | 58.2 | 54.1 | 60.3 | 65 | 72.5 | 80.2 | 86.7 | 93.6 | 95.6 | 94.7 | 90 | 81.2 | 69.3 | 59.8 | 52.5 | 54.3 | 57.5 | 59.2 | 63.2 | 67.4 | 70.2 | 68.9 | 66.9 | 61.8 | 56.3 | 52 | 58.3 | 62.1 | 69.2 | 76 | 83.6 | 91.3 | 94.2 | 92.7 | 89.6 | 78.1 | 65.8 | 57.8 | 17.3 | 19.6 | 22.4 | 23.9 | 24.6 | 26.1 | 25.7 | 25.8 | 25.1 | 23.5 | 20.2 | 17.9 | 22.8 | 25.3 | 28.8 | 30.1 | 28.4 | 28 | 25.8 | 27 | 27.4 | 28.5 | 26.1 | 22 | 12.8 | 12.9 | 12.9 | 12.3 | 11.2 | 10.7 | 9.7 | 10.1 | 10.4 | 12.6 | 13.3 | 12.2 | 18 | 22.1 | 26.1 | 28.1 | 27.3 | 27.1 | 24.9 | 26.1 | 25.7 | 25.1 | 22.7 | 17.1 | 11.3 | 12.1 | 12.9 | 12.1 | 11.4 | 11.2 | 10.8 | 10.9 | 10.2 | 11.3 | 12.2 | 10.5 | 0.326 | 0.338 | 0.343 | 0.372 | 0.379 | 0.369 | 0.4 | 0.376 | 0.372 | 0.37 | 0.342 | 0.328 | 2.443 | 2.415 | 2.407 | 2.329 | 2.336 | 2.364 | 2.316 | 2.351 | 2.373 | 2.344 | 2.401 | 2.447 | 277 | 286 | 294 | 289 | 287 | 288 | 279 | 284 | 280 | 270 | 267 | 268 | 28 | 32 | 35 | 40 | 40 | 39 | 41 | 38 | 36 | 34 | 29 | 26 | 863 | 1188 | 1656 | 2091 | 2435 | 2690 | 2549 | 2371 | 2000 | 1470 | 1045 | 799 | 85 | 129 | 118 | 118 | 120 | 87 | 92 | 61 | 48 | 76 | 49 | 79 | 1.42 | N/A | -3.55 | N/A | -1.58 | -1.76 | -65 | -306 | 490 | 268 | 1.1 | N/A | -2.66 | 1.17 | N/A | N/A | N/A | -232 | 392 | 160 | 40
| FRESNO-YOSEMITE_STYP20 | 13 | 4 | USA | CA | FRESNO YOSEMITE | 723890 | 93193 | 36.78 | -119.719 | 333 | 14.52 | -8 | NAP | 94-19 | 3B | 12 | 32.5 | 34.8 | 22.9 | 17.4 | 58.8 | 26.4 | 20.6 | 56.2 | 18.5 | 52.7 | 16.5 | 52.2 | 2 | 90 | 0.446 | 7 | 29.1 | 103.8 | 69.6 | 101.3 | 68.6 | 98.8 | 67.7 | 73.1 | 96.9 | 71.4 | 94.6 | 69.9 | 92.9 | 8.1 | 300 | 65.1 | 94 | 84.7 | 62.8 | 86.6 | 83.5 | 60.8 | 80.6 | 81.5 | 36.8 | 96.6 | 35.3 | 94.7 | 34 | 92.8 | 83.3 | 18.3 | 16.4 | 14.4 | 29.3 | 108.2 | 2.6 | 1.9 | 27.5 | 109.6 | 26 | 110.7 | 24.5 | 111.8 | 22.7 | 113.2 | 28.1 | 75.6 | 2.6 | 3.6 | 26.2 | 78.2 | 24.7 | 80.3 | 23.2 | 82.4 | 21.3 | 85 | 65.2 | 48.6 | 52.2 | 57.7 | 62.4 | 70 | 77.8 | 83.8 | 82.4 | 77.1 | 66.5 | 55.5 | 47.9 | 13.8 | 5 | 4.92 | 5.93 | 7.01 | 7.11 | 6.8 | 5.11 | 4.68 | 6.06 | 6.04 | 5.87 | 5.11 | 246 | 88 | 30 | 7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 102 | 2138 | 510 | 358 | 235 | 131 | 30 | 2 | 0 | 0 | 2 | 53 | 288 | 529 | 5807 | 44 | 92 | 247 | 372 | 621 | 834 | 1048 | 1004 | 812 | 512 | 183 | 38 | 2223 | 0 | 0 | 9 | 52 | 186 | 387 | 583 | 539 | 364 | 100 | 3 | 0 | 29602 | 0 | 4 | 162 | 710 | 2381 | 5265 | 8270 | 7237 | 4414 | 1103 | 56 | 0 | 16698 | 0 | 0 | 26 | 244 | 1094 | 3005 | 5161 | 4397 | 2391 | 375 | 5 | 0 | 5.9 | 4 | 4.8 | 5.8 | 7.2 | 8.2 | 8.4 | 7.5 | 6.8 | 5.9 | 4.6 | 3.7 | 3.8 | 11 | 2.1 | 2 | 2 | 0.9 | 0.4 | 0.2 | 0 | 0 | 0.2 | 0.6 | 1.3 | 1.5 | 21.6 | 8.5 | 6.1 | 7.2 | 4.4 | 1.7 | 1.9 | 0.2 | 0.2 | 1.2 | 2.4 | 3.5 | 4.3 | 6.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9 | 1.7 | 1.7 | 1.6 | 1 | 0.5 | 0.4 | 0 | 0 | 0.4 | 0.7 | 1 | 1 | 68.3 | 73.9 | 83.5 | 91.7 | 99.3 | 105.3 | 107.4 | 106.3 | 102.5 | 94 | 79.7 | 67 | 53 | 57.3 | 60.5 | 62.8 | 66.8 | 69.9 | 70.7 | 70.8 | 68.1 | 65.5 | 59.6 | 55 | 64 | 69.2 | 78.4 | 86.6 | 94.6 | 101.6 | 104.2 | 102.7 | 98.9 | 88 | 74.9 | 63 | 53.8 | 56.9 | 59.9 | 61.7 | 65.4 | 68.4 | 69.9 | 69.2 | 67.3 | 63.3 | 58.3 | 53.3 | 60.6 | 65.5 | 74.6 | 82.1 | 90.5 | 98.1 | 101.6 | 100.1 | 96 | 84 | 70.6 | 60 | 52.7 | 54.7 | 58.2 | 60.2 | 63.6 | 66.8 | 69.1 | 67.9 | 66.5 | 61.7 | 57 | 52 | 57.7 | 62.2 | 70.8 | 77.4 | 86.3 | 94.5 | 98.8 | 97.4 | 92.7 | 80.4 | 66.8 | 57.1 | 51.8 | 53.5 | 57 | 58.9 | 62.2 | 65.8 | 68.4 | 67.4 | 65.6 | 60.4 | 55.5 | 51 | 58.9 | 60.5 | 64.3 | 66.6 | 70 | 74.1 | 75.4 | 76.4 | 72.3 | 67.9 | 62.4 | 58.9 | 63.2 | 67.7 | 77.5 | 82.9 | 92.6 | 98.3 | 100.3 | 98.7 | 94.1 | 86.1 | 74.4 | 63.6 | 55.9 | 58.3 | 62 | 63.6 | 67.6 | 71.7 | 73.3 | 72.5 | 70.2 | 65.8 | 60.2 | 55.9 | 60 | 66.2 | 74.8 | 81.3 | 90.4 | 95.4 | 98.3 | 94.7 | 91.5 | 83.2 | 71.1 | 59.6 | 54.1 | 56.4 | 59.8 | 61.6 | 65.5 | 69.4 | 71.5 | 70.5 | 68.3 | 63.7 | 58.5 | 53.9 | 58.3 | 63.6 | 71.4 | 78.8 | 86.6 | 92 | 95.4 | 93.6 | 90.5 | 80.5 | 68.1 | 57.7 | 52.2 | 54.5 | 57.9 | 59.7 | 63.4 | 67.6 | 70.1 | 68.9 | 66.9 | 61.9 | 56.6 | 51.9 | 56.7 | 60.8 | 68.4 | 75.3 | 83.1 | 90.1 | 93.6 | 92.2 | 89.2 | 77.4 | 64.8 | 55.8 | 15.8 | 18.1 | 21.2 | 23.3 | 25.6 | 28.4 | 29.1 | 29.4 | 27.7 | 24.5 | 19.8 | 16.1 | 21.3 | 23.2 | 27.4 | 30 | 30.6 | 30.9 | 30 | 30.8 | 30.7 | 29.4 | 25.9 | 20.3 | 12.5 | 12.2 | 11.6 | 10.6 | 9.9 | 9.2 | 9 | 8.8 | 9.2 | 10.5 | 12.1 | 11.8 | 15.8 | 20.2 | 24.7 | 27.3 | 28.9 | 29.4 | 28.3 | 29.2 | 28.5 | 26.5 | 22.4 | 13.7 | 10.1 | 11.3 | 11.6 | 10.4 | 10 | 9.6 | 9.7 | 9.5 | 9.2 | 9.8 | 11.3 | 9.1 | 0.359 | 0.372 | 0.395 | 0.378 | 0.368 | 0.364 | 0.383 | 0.368 | 0.371 | 0.39 | 0.38 | 0.371 | 2.324 | 2.304 | 2.239 | 2.331 | 2.387 | 2.399 | 2.374 | 2.389 | 2.391 | 2.283 | 2.253 | 2.266 | 259 | 271 | 275 | 286 | 290 | 290 | 283 | 286 | 279 | 260 | 247 | 243 | 31 | 35 | 41 | 40 | 38 | 37 | 38 | 37 | 35 | 36 | 33 | 30 | 773 | 1105 | 1572 | 2001 | 2379 | 2669 | 2570 | 2357 | 1958 | 1422 | 962 | 705 | 111 | 129 | 136 | 152 | 137 | 98 | 97 | 72 | 60 | 81 | 54 | 98 | 1.01 | N/A | -2.2 | N/A | N/A | -1.44 | -68 | -223 | 344 | 205 | 0.92 | N/A | -2.05 | 0.79 | N/A | N/A | N/A | -245 | 301 | 95 | 23
| MAMMOTH-YOSEMITE_STYP20 | 16 | 4 | USA | CA | MAMMOTH YOSEMITE | 723894 | 03181 | 37.633 | -118.85 | 7128 | 11.28 | -8 | NAP | 08-19 | 6A | 12 | -0.2 | 5.1 | -11.2 | 3.9 | 24.7 | -7.2 | 4.9 | 25.1 | 35.2 | 43.3 | 28.9 | 42 | 2.5 | 350 | 0.643 | 7 | 36.1 | 86.3 | 54.2 | 84.3 | 53.5 | 82.2 | 52.6 | 57.3 | 77.3 | 56 | 77.1 | 54.8 | 76.7 | 11.9 | 280 | 50.8 | 72 | 61.5 | 47.9 | 64.5 | 61.6 | 45.3 | 58.3 | 60.8 | 27.9 | 77.1 | 26.8 | 76.4 | 25.9 | 76.8 | 62.2 | 26.9 | 23 | 19.2 | -12.7 | 90.1 | 7.2 | 2.4 | -17.9 | 91.8 | -22.1 | 93.2 | -26.1 | 94.5 | -31.4 | 96.2 | -13.2 | 60.4 | 7.1 | 1.1 | -18.3 | 61.2 | -22.4 | 61.9 | -26.4 | 62.5 | -31.6 | 63.4 | 45.2 | 28.9 | 30.5 | 36 | 42.9 | 49.1 | 59.2 | 64.5 | 62.7 | 56.7 | 46.3 | 36.4 | 28.4 | 14.6 | 9.24 | 9.62 | 7.6 | 7.37 | 6.46 | 6.23 | 4.23 | 3.86 | 5.33 | 5.84 | 7.95 | 8.8 | 3195 | 654 | 547 | 435 | 226 | 94 | 8 | 0 | 0 | 14 | 139 | 408 | 670 | 7301 | 1119 | 966 | 900 | 664 | 492 | 190 | 59 | 90 | 251 | 578 | 857 | 1135 | 1447 | 0 | 1 | 0 | 12 | 67 | 282 | 449 | 394 | 214 | 26 | 2 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 15 | 43 | 19 | 1 | 0 | 0 | 0 | 4287 | 0 | 0 | 0 | 2 | 42 | 830 | 1636 | 1325 | 429 | 23 | 0 | 0 | 1032 | 0 | 0 | 0 | 0 | 1 | 202 | 473 | 314 | 42 | 0 | 0 | 0 | 6.6 | 4.9 | 6.4 | 7.1 | 8.5 | 8.3 | 8 | 6.5 | 6.2 | 6.1 | 5.8 | 5.5 | 5.7 | 13.6 | 2.2 | 2.1 | 1.7 | 1 | 0.8 | 0.4 | 0.5 | 0.4 | 0.4 | 0.8 | 1 | 2 | 20.7 | 6 | 7 | 6.8 | 3 | 2 | 1.7 | 1.1 | 0.8 | 1.4 | 2.9 | 3.5 | 7.4 | 6.9 | 0.2 | 0.3 | 0.1 | 0.2 | 0.2 | 0 | 0.1 | 0.1 | 0 | 0 | 0.1 | 0.2 | 3.4 | 1.7 | 1.3 | 1.6 | 0.6 | 0.5 | 0.4 | 0.3 | 0.2 | 0.3 | 0.7 | 0.8 | 1.5 | 59.3 | 63.1 | 66.1 | 72.5 | 78.6 | 88.5 | 89.9 | 88.2 | 83.6 | 77.1 | 68.4 | 59.3 | 39.3 | 41 | 43 | 47.1 | 49.2 | 55.1 | 55.3 | 54.4 | 51.5 | 47.9 | 44.1 | 38.9 | 54.4 | 58.8 | 61.4 | 68.4 | 74.6 | 85 | 87.1 | 85.6 | 81.2 | 72.5 | 63.9 | 54.8 | 36.9 | 38.8 | 39.7 | 44.6 | 47.7 | 53.4 | 54.7 | 53.5 | 51.2 | 46.3 | 42.1 | 36.7 | 50 | 54.2 | 57.4 | 65.6 | 71.7 | 82 | 84.8 | 83.7 | 79 | 68.5 | 59.8 | 50.2 | 35.6 | 36.8 | 38.4 | 43.1 | 46.8 | 51.9 | 54.2 | 52.9 | 50.3 | 44.9 | 40 | 35.6 | 45 | 48.1 | 53.9 | 61.7 | 67.9 | 79.2 | 82.3 | 81.4 | 76.6 | 64.5 | 54.8 | 45.8 | 33.7 | 34.8 | 37.5 | 41.5 | 45.3 | 51 | 53.5 | 52.1 | 49.6 | 43.2 | 37.9 | 33.9 | 40.7 | 42.1 | 43.5 | 48.6 | 51 | 57.1 | 59.5 | 58.2 | 56.3 | 50.7 | 45.7 | 41.7 | 54.4 | 59.1 | 63 | 68.3 | 73.5 | 81.9 | 76.7 | 77.4 | 73 | 66.2 | 64.4 | 53.2 | 38.3 | 39.8 | 41.2 | 46.1 | 49.3 | 55.2 | 58 | 56.4 | 53.9 | 48.6 | 43.2 | 39.1 | 49.7 | 55.5 | 58.7 | 65.1 | 70.2 | 80.1 | 76.9 | 76.9 | 74.7 | 66.5 | 60.6 | 49.9 | 36.7 | 37.4 | 39.6 | 44 | 47.9 | 53.5 | 56.7 | 55 | 52.2 | 46.4 | 41.2 | 36.9 | 46.9 | 51.3 | 55.8 | 63.2 | 67.6 | 77.9 | 76.9 | 76.4 | 74.1 | 64.1 | 57.5 | 48.4 | 34.4 | 35.3 | 37.8 | 42.2 | 46.3 | 52 | 55.5 | 53.8 | 50.7 | 44.6 | 38.9 | 34.4 | 43.3 | 47.5 | 51.2 | 60 | 65 | 75.7 | 76.8 | 76.4 | 73.2 | 61.5 | 53.7 | 45.3 | 28.1 | 27 | 27.9 | 29.9 | 30.2 | 34.5 | 36.1 | 37.7 | 37 | 34.9 | 32.9 | 28.2 | 35.6 | 35.2 | 36.1 | 37 | 37.2 | 39.3 | 38.2 | 40.6 | 40.7 | 41.5 | 40.5 | 35.2 | 20.9 | 18.8 | 18.2 | 17.5 | 16.7 | 15.8 | 14.5 | 16.2 | 17.6 | 20 | 21.5 | 20.2 | 29 | 32.2 | 33 | 34.6 | 34.7 | 36.4 | 33.4 | 35.1 | 35.7 | 35.9 | 37.6 | 30.8 | 17.9 | 17.8 | 17 | 16.8 | 15.7 | 14.5 | 12.9 | 14 | 15.4 | 17.6 | 20.2 | 18.1 | 0.245 | 0.26 | 0.261 | 0.298 | 0.303 | 0.298 | 0.314 | 0.298 | 0.282 | 0.269 | 0.244 | 0.242 | 2.427 | 2.383 | 2.436 | 2.402 | 2.466 | 2.503 | 2.503 | 2.532 | 2.582 | 2.592 | 2.599 | 2.485 | 305 | 312 | 321 | 312 | 310 | 310 | 304 | 308 | 310 | 306 | 305 | 299 | 26 | 31 | 33 | 36 | 35 | 34 | 34 | 32 | 29 | 25 | 22 | 23 | 830 | 1112 | 1528 | 1965 | 2269 | 2627 | 2485 | 2318 | 1954 | 1427 | 983 | 736 | 81 | 117 | 117 | 126 | 183 | 167 | 146 | 118 | 76 | 100 | 56 | 84 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.97 | N/A | N/A | 0.79 | N/A | N/A | -85 | -203 | 236 | 119 | 18
| PORTERVILLE_STYP20 | 13 | 4 | USA | CA | PORTERVILLE | 723895 | 23149 | 36.029 | -119.063 | 442 | 14.46 | -8 | NAP | 94-19 | 3B | 12 | 30.2 | 33.1 | 20.8 | 15.9 | 40.8 | 24.8 | 19.2 | 43.3 | 15.3 | 52.3 | 12.3 | 52.3 | 3.1 | 110 | 0.428 | 7 | 31.4 | 101.7 | 70.8 | 99.5 | 69.5 | 97.4 | 68.4 | 73.3 | 96.9 | 71.5 | 94.7 | 70.1 | 93.4 | 9.1 | 320 | 64.2 | 91.4 | 86.4 | 62.9 | 87.3 | 85.1 | 61 | 81.6 | 83.3 | 37 | 96.6 | 35.4 | 95.1 | 34.2 | 92.3 | 79.9 | 12.9 | 11.5 | 10.4 | 27.4 | 106.4 | 2.6 | 2.1 | 25.6 | 107.9 | 24.1 | 109.1 | 22.7 | 110.3 | 20.8 | 111.8 | 26.1 | 75.2 | 2.1 | 2.3 | 24.6 | 76.9 | 23.4 | 78.3 | 22.3 | 79.6 | 20.8 | 81.3 | 63.3 | 47.8 | 50.9 | 55.6 | 60.3 | 67.7 | 75.4 | 80.9 | 79.3 | 74.6 | 64.5 | 54 | 47.3 | 13.13 | 4.97 | 4.91 | 5.72 | 6.87 | 6.91 | 6.54 | 4.8 | 4.53 | 5.87 | 6.09 | 5.63 | 5.16 | 309 | 104 | 43 | 15 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 118 | 2423 | 535 | 395 | 296 | 174 | 49 | 5 | 0 | 0 | 4 | 83 | 332 | 550 | 5148 | 35 | 68 | 188 | 313 | 550 | 763 | 958 | 908 | 739 | 449 | 144 | 33 | 1786 | 0 | 0 | 4 | 33 | 134 | 318 | 493 | 443 | 293 | 67 | 1 | 0 | 25484 | 0 | 6 | 140 | 671 | 2120 | 4701 | 7035 | 5997 | 3758 | 1003 | 53 | 0 | 14120 | 0 | 0 | 23 | 227 | 981 | 2680 | 4286 | 3558 | 2027 | 334 | 4 | 0 | 5 | 3.8 | 4.3 | 4.8 | 5.5 | 6 | 6.2 | 6 | 5.7 | 5.2 | 4.6 | 3.9 | 3.8 | 10.7 | 1.9 | 1.9 | 1.8 | 1.1 | 0.4 | 0.1 | 0 | 0 | 0.2 | 0.6 | 1.5 | 1.5 | 19.4 | 7.9 | 6.5 | 5.3 | 4.8 | 2.9 | 0.5 | 0.2 | 0.3 | 1.5 | 2.6 | 3.5 | 5.6 | 5.2 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6 | 1.7 | 1.7 | 1.3 | 1.1 | 0.6 | 0.1 | 0 | 0 | 0.4 | 0.7 | 1 | 1.2 | 67.7 | 73.5 | 82.4 | 90.8 | 99.2 | 104.3 | 105.8 | 103.8 | 100.2 | 92.8 | 79.8 | 68.2 | 56 | 58.6 | 62.2 | 64 | 67.8 | 71.9 | 73 | 72.1 | 69.7 | 66 | 60.1 | 55.4 | 63.7 | 69.6 | 78.7 | 86.1 | 93.4 | 100.2 | 101.9 | 100.1 | 97.4 | 88 | 74.7 | 63.8 | 53.9 | 57.2 | 60.7 | 62.4 | 65.3 | 68.8 | 71.3 | 69.9 | 67.9 | 64 | 58.4 | 53.3 | 60.9 | 64.3 | 73.3 | 81.8 | 90.2 | 97.4 | 99.6 | 98.7 | 94.6 | 83.5 | 70.5 | 60.9 | 53 | 54.8 | 58.4 | 60.8 | 63.9 | 67.5 | 70.4 | 69.2 | 67.3 | 62 | 56.7 | 52.1 | 57.1 | 61.5 | 70.1 | 77.1 | 85.5 | 93.3 | 97.3 | 95.6 | 91.1 | 80.6 | 65.9 | 57 | 51.2 | 53.1 | 56.8 | 59.1 | 62.8 | 66.2 | 69.1 | 68 | 65.9 | 60.9 | 54.8 | 50.7 | 59.2 | 60.8 | 64.7 | 67.8 | 70.1 | 74.7 | 75.8 | 74.3 | 73.4 | 68.4 | 62.5 | 58.9 | 64 | 68.6 | 77.8 | 84.5 | 94.6 | 99.3 | 99.5 | 99.3 | 95.9 | 87.4 | 75.3 | 64.6 | 56 | 58.7 | 62.1 | 64 | 67.3 | 71.3 | 73.6 | 72.1 | 70.2 | 65.8 | 60.2 | 55.9 | 61.1 | 66.5 | 75.7 | 82.3 | 91 | 95.9 | 97.3 | 95.7 | 92.1 | 83.2 | 71.4 | 60.6 | 54 | 56.4 | 59.7 | 61.8 | 65.2 | 69.2 | 72 | 70.6 | 68.4 | 63.8 | 58.2 | 53.6 | 59 | 63.4 | 71.8 | 79.3 | 87 | 93.9 | 95.3 | 94 | 91.3 | 80 | 68 | 58.5 | 52 | 54.1 | 57.4 | 59.8 | 63.3 | 67.5 | 70.4 | 69.2 | 66.9 | 61.7 | 55.9 | 51.4 | 56.7 | 60.6 | 67.9 | 75.5 | 83.7 | 91.3 | 93.5 | 92.6 | 89.6 | 78.2 | 64.6 | 56.2 | 17.7 | 20.4 | 24.9 | 27.5 | 29.4 | 32.1 | 31.4 | 31.7 | 30.8 | 27.4 | 22.6 | 18.7 | 23.3 | 25.6 | 31.1 | 33.9 | 34.4 | 34.8 | 32.2 | 32.9 | 33 | 32.5 | 29.4 | 23.7 | 15.6 | 16.3 | 16.7 | 15.7 | 14 | 13.9 | 12.7 | 13.1 | 13.8 | 15 | 16.9 | 15.3 | 19.5 | 23.1 | 28.9 | 31.4 | 32.8 | 33.1 | 30.7 | 31.2 | 31.3 | 28.3 | 25.6 | 18.1 | 13.7 | 15.5 | 16.3 | 15.3 | 13.9 | 13.6 | 12.5 | 13 | 13.6 | 13.4 | 15.3 | 12.5 | 0.352 | 0.364 | 0.365 | 0.396 | 0.404 | 0.388 | 0.422 | 0.397 | 0.388 | 0.391 | 0.359 | 0.354 | 2.344 | 2.321 | 2.335 | 2.256 | 2.262 | 2.319 | 2.257 | 2.301 | 2.329 | 2.272 | 2.336 | 2.333 | 264 | 275 | 286 | 281 | 279 | 283 | 272 | 278 | 275 | 261 | 258 | 253 | 30 | 35 | 37 | 43 | 43 | 41 | 43 | 40 | 37 | 36 | 30 | 29 | 827 | 1146 | 1612 | 2040 | 2391 | 2679 | 2534 | 2358 | 1980 | 1449 | 1011 | 758 | 93 | 125 | 125 | 128 | 135 | 102 | 105 | 74 | 55 | 80 | 51 | 86 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.92 | N/A | -2.03 | 0.83 | N/A | N/A | N/A | -221 | 311 | 122 | 25
| VISALIA_STYP20 | 13 | 4 | USA | CA | VISALIA | 723896 | 93144 | 36.317 | -119.4 | 295 | 14.54 | -8 | NAP | 94-19 | 3B | 12 | 29.9 | 32.6 | 22.9 | 17.5 | 42 | 27 | 21.2 | 40.1 | 16.8 | 52.3 | 14 | 52.2 | 2.1 | 120 | 0.42 | 7 | 31 | 100.3 | 71.8 | 98.9 | 71 | 96.7 | 70.1 | 74.9 | 95.7 | 73.2 | 93.6 | 71.7 | 92 | 7.4 | 300 | 68.1 | 104.2 | 85.3 | 65.8 | 96.2 | 84.4 | 63.9 | 89.8 | 83.4 | 38.3 | 95.2 | 36.9 | 94.1 | 35.5 | 91.8 | 83.5 | 15.6 | 12.6 | 11 | 26.8 | 105.7 | 2.9 | 2 | 24.7 | 107.2 | 23 | 108.3 | 21.4 | 109.5 | 19.3 | 110.9 | 25.7 | 77.4 | 3.3 | 1.8 | 23.3 | 78.7 | 21.4 | 79.7 | 19.6 | 80.7 | 17.2 | 82 | 63.1 | 47.5 | 50.9 | 56.4 | 61 | 68.5 | 75.5 | 80.3 | 78.5 | 73.7 | 63.9 | 53.7 | 46.4 | 12.91 | 5.02 | 4.87 | 5.47 | 6.57 | 6.4 | 5.95 | 4.35 | 4.32 | 5.42 | 5.72 | 5.48 | 5.26 | 330 | 111 | 44 | 9 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 137 | 2413 | 544 | 396 | 271 | 154 | 37 | 4 | 0 | 0 | 4 | 87 | 341 | 575 | 5108 | 32 | 68 | 208 | 332 | 573 | 766 | 939 | 883 | 712 | 432 | 136 | 27 | 1714 | 0 | 0 | 4 | 34 | 144 | 320 | 474 | 418 | 266 | 54 | 0 | 0 | 23063 | 0 | 1 | 120 | 622 | 2052 | 4368 | 6296 | 5346 | 3339 | 889 | 30 | 0 | 12346 | 0 | 0 | 18 | 200 | 923 | 2421 | 3696 | 3063 | 1737 | 287 | 1 | 0 | 4.5 | 3.4 | 4 | 4.5 | 5.5 | 6.2 | 6.3 | 5.4 | 4.8 | 4.3 | 3.7 | 3.1 | 3.3 | 9.9 | 1.7 | 1.9 | 1.7 | 1 | 0.2 | 0.1 | 0 | 0 | 0.2 | 0.4 | 1.3 | 1.4 | 18.1 | 7.7 | 5.8 | 5 | 4.8 | 2.2 | 0.7 | 0.2 | 0.2 | 1.5 | 1.9 | 3.5 | 3.8 | 5 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5 | 1.6 | 1.7 | 1.3 | 1.1 | 0.5 | 0.2 | 0.1 | 0 | 0.4 | 0.5 | 1 | 0.9 | 66.2 | 72.7 | 82.2 | 90.5 | 99 | 103.1 | 103.8 | 102.3 | 99.4 | 92.6 | 78.1 | 66.3 | 54.6 | 59.3 | 62.6 | 63.9 | 69.2 | 72.4 | 73.5 | 73.2 | 70 | 66.6 | 59.9 | 55.5 | 63.2 | 67.9 | 77.2 | 85.2 | 93.1 | 99.6 | 100.3 | 99.4 | 96.8 | 87.6 | 73.4 | 62.9 | 54.1 | 57.9 | 60.6 | 63 | 66.4 | 70.2 | 72.7 | 71.7 | 69 | 64.4 | 58.8 | 53.6 | 60.5 | 64 | 73.1 | 81.4 | 89.9 | 96.9 | 98.7 | 97.2 | 93.2 | 82.4 | 69.8 | 59.1 | 53.6 | 55.4 | 58.7 | 60.9 | 64.8 | 68.9 | 72 | 70.7 | 68 | 62.3 | 57.6 | 52 | 56.8 | 61.2 | 70 | 76.7 | 84.7 | 92.7 | 96.3 | 93.9 | 90.5 | 79.3 | 65.5 | 55.7 | 51.7 | 53.6 | 57.6 | 59.3 | 63.1 | 67.2 | 71 | 69.6 | 67 | 61.1 | 55.7 | 50.5 | 59.5 | 61.3 | 64.9 | 67.1 | 71.3 | 75.6 | 77.9 | 76.7 | 74 | 68.8 | 62.8 | 58.7 | 63.2 | 69 | 78.5 | 84.8 | 95.3 | 98.6 | 98.6 | 97.1 | 93.1 | 86.8 | 73.2 | 63.4 | 56 | 59 | 62.3 | 64.3 | 68.3 | 72.8 | 75.3 | 74.1 | 71.2 | 66.2 | 60.6 | 55.5 | 60.2 | 65.9 | 74.7 | 81.7 | 90.2 | 95.1 | 95.9 | 94.4 | 90.7 | 83.1 | 70.5 | 59.8 | 54.1 | 56.9 | 60.1 | 62.1 | 66.2 | 70.6 | 73.6 | 72.5 | 69.4 | 64.1 | 58.5 | 53.5 | 58.1 | 63.1 | 71.3 | 78.5 | 86.4 | 91.9 | 93.9 | 92.6 | 89.8 | 80 | 67.7 | 57.6 | 52.4 | 54.5 | 58 | 60.1 | 64.2 | 68.6 | 72.1 | 71 | 68 | 62.2 | 56.5 | 51.3 | 56.6 | 60.3 | 68 | 74.9 | 83 | 89.5 | 92.2 | 91 | 88 | 76.7 | 64.3 | 55.3 | 16.7 | 19.3 | 23.2 | 25.7 | 27.6 | 30.8 | 31 | 31.8 | 31 | 28.1 | 22.4 | 17.9 | 22.4 | 24.1 | 29.2 | 32.5 | 33.7 | 34.7 | 32.5 | 33.4 | 34 | 33.3 | 28.5 | 22.6 | 15.2 | 15.5 | 15.5 | 14.4 | 12.8 | 12 | 11.2 | 11.7 | 12.5 | 14.5 | 15.8 | 14.9 | 17.6 | 22 | 26.7 | 30.5 | 32 | 32.8 | 30.5 | 31.9 | 31.9 | 29.7 | 25.1 | 16.7 | 12.7 | 14.7 | 15 | 14 | 12.7 | 12 | 11.3 | 11.9 | 12.4 | 13.4 | 14.9 | 11.8 | 0.366 | 0.377 | 0.376 | 0.386 | 0.386 | 0.377 | 0.402 | 0.377 | 0.376 | 0.395 | 0.376 | 0.364 | 2.284 | 2.278 | 2.298 | 2.295 | 2.321 | 2.348 | 2.31 | 2.355 | 2.365 | 2.256 | 2.27 | 2.293 | 256 | 270 | 282 | 284 | 285 | 286 | 278 | 284 | 278 | 259 | 250 | 248 | 32 | 36 | 39 | 41 | 41 | 40 | 41 | 38 | 36 | 36 | 32 | 30 | 776 | 1123 | 1602 | 2034 | 2402 | 2676 | 2550 | 2352 | 1966 | 1433 | 978 | 716 | 109 | 124 | 132 | 141 | 129 | 87 | 94 | 68 | 55 | 75 | 53 | 95 | 1.24 | N/A | N/A | 0.86 | N/A | N/A | N/A | N/A | N/A | N/A | 1.04 | N/A | -1.94 | 0.99 | N/A | N/A | -52 | -257 | 351 | 137 | 21
| HANFORD_STYP20 | 13 | 4 | USA | CA | HANFORD | 723898 | 53119 | 36.319 | -119.629 | 249 | 14.56 | -8 | NAP | 98-19 | 3B | 12 | 28.5 | 30.9 | 22.4 | 17 | 47.3 | 25.7 | 19.9 | 46.3 | 17.5 | 51.8 | 15.5 | 51.5 | 1.3 | 60 | 0.448 | 7 | 31.4 | 102.3 | 69.8 | 99.9 | 69.4 | 97.8 | 68.4 | 73.6 | 95.4 | 72 | 93.8 | 70.4 | 92.5 | 6.8 | 330 | 66.2 | 97.3 | 83.4 | 63.8 | 89.4 | 83.4 | 62.1 | 84.1 | 81.6 | 37.3 | 95.8 | 35.7 | 93.7 | 34.3 | 92.7 | 84.9 | 16.9 | 14.9 | 12.6 | 25 | 106.7 | 2.9 | 2.3 | 22.9 | 108.4 | 21.2 | 109.7 | 19.6 | 111 | 17.5 | 112.6 | 24.1 | 76.8 | 2.9 | 3 | 22 | 79 | 20.3 | 80.7 | 18.6 | 82.4 | 16.5 | 84.5 | 63.6 | 46.9 | 50.8 | 56.6 | 61.6 | 69.2 | 76.5 | 81.6 | 80 | 74.6 | 64.5 | 53.5 | 46.4 | 13.45 | 5.08 | 4.86 | 5.89 | 6.64 | 6.16 | 5.87 | 4.37 | 3.99 | 5.52 | 5.65 | 5.58 | 5.19 | 349 | 125 | 45 | 10 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 139 | 2405 | 563 | 397 | 268 | 141 | 28 | 3 | 0 | 0 | 4 | 76 | 347 | 578 | 5302 | 27 | 68 | 214 | 350 | 594 | 796 | 981 | 929 | 737 | 448 | 132 | 26 | 1881 | 0 | 0 | 6 | 39 | 157 | 348 | 516 | 464 | 291 | 59 | 1 | 0 | 27333 | 0 | 4 | 183 | 738 | 2300 | 5047 | 7495 | 6489 | 4004 | 1022 | 50 | 1 | 15150 | 0 | 0 | 36 | 265 | 1039 | 2846 | 4581 | 3870 | 2170 | 340 | 3 | 0 | 5.2 | 3.2 | 4 | 5.1 | 6.5 | 7.4 | 7.6 | 6.6 | 6.2 | 5.2 | 4 | 3.1 | 3.1 | 8.6 | 1.7 | 1.5 | 1.5 | 0.7 | 0.2 | 0.1 | 0 | 0 | 0.2 | 0.4 | 0.9 | 1.1 | 15.6 | 6.7 | 5 | 6.6 | 3 | 1.5 | 0.8 | 0.2 | 0.4 | 1.5 | 2.4 | 2.9 | 3.3 | 3.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1.4 | 1.4 | 1.3 | 0.7 | 0.4 | 0.2 | 0 | 0.1 | 0.4 | 0.6 | 0.8 | 0.9 | 67.4 | 73.9 | 84.3 | 92.6 | 98.9 | 104.1 | 106 | 104.3 | 101.4 | 93.2 | 79.3 | 66.3 | 53.2 | 58.2 | 61.5 | 64 | 69.3 | 70.8 | 70.8 | 69.8 | 68.2 | 66.2 | 60.3 | 55.4 | 63.3 | 69.4 | 79 | 87.3 | 93.9 | 100.3 | 102.6 | 101 | 98.1 | 87.9 | 74.4 | 63 | 53.7 | 56.8 | 60 | 62 | 65.4 | 69.2 | 70.4 | 68.9 | 67.6 | 64.2 | 59.1 | 53.7 | 60.1 | 65.4 | 74.7 | 82.2 | 90 | 97.3 | 100.1 | 98.9 | 95.3 | 83.6 | 70.1 | 59.5 | 52.7 | 55.1 | 58.6 | 60.3 | 63.9 | 67.5 | 70.3 | 68.8 | 66.5 | 61.9 | 57.2 | 52 | 56.7 | 62.2 | 70.7 | 77.5 | 86 | 93.7 | 97.7 | 96.4 | 92 | 80.2 | 65.8 | 56.5 | 51.5 | 53.8 | 57 | 58.7 | 62 | 66.5 | 69 | 67.7 | 65.9 | 60.9 | 55.4 | 50.9 | 58.6 | 61 | 64.2 | 67.3 | 72.5 | 74.9 | 76.7 | 74.5 | 72.8 | 68.7 | 63.4 | 59.3 | 62.2 | 68 | 77.6 | 86.5 | 91.8 | 97.7 | 98.3 | 95 | 92 | 85.9 | 73.5 | 63.2 | 55.8 | 58.5 | 62.1 | 63.9 | 68.1 | 72.3 | 74.1 | 72.3 | 70 | 66.3 | 60.7 | 56.1 | 60 | 66.2 | 75.5 | 82.5 | 89.7 | 94.8 | 96.2 | 94.8 | 92 | 82.3 | 71 | 59.7 | 54 | 56.6 | 60 | 61.6 | 65.6 | 70.3 | 72.3 | 70.6 | 68.3 | 64.1 | 58.5 | 54.1 | 57.7 | 63.8 | 72.2 | 78.9 | 85.7 | 92 | 94.1 | 93.3 | 90.9 | 79.8 | 67.8 | 57.8 | 51.9 | 54.6 | 57.9 | 59.6 | 63.4 | 68.3 | 70.7 | 69.2 | 66.8 | 62.2 | 56.5 | 51.6 | 56.1 | 60.9 | 68.6 | 75.4 | 83 | 89.5 | 92.6 | 91.9 | 89.2 | 77 | 64.3 | 55 | 18.2 | 21.7 | 24.3 | 26.3 | 28.1 | 30.6 | 31.4 | 32.4 | 32.6 | 29.4 | 24.6 | 19.8 | 24.6 | 28 | 31.3 | 34.4 | 34.4 | 34.9 | 33.7 | 34.9 | 36.6 | 35.5 | 31.2 | 24.4 | 15.7 | 16.3 | 14.5 | 13.2 | 12 | 10.9 | 10.6 | 10.7 | 12 | 14.3 | 16.5 | 15.4 | 18.5 | 23.8 | 28.1 | 31.8 | 31.5 | 31.4 | 30.5 | 32.3 | 33.5 | 30.5 | 27.2 | 16.9 | 12.6 | 14.5 | 13.9 | 13 | 11.9 | 11 | 11.1 | 11.4 | 11.9 | 12.9 | 15.3 | 11.7 | 0.361 | 0.371 | 0.371 | 0.371 | 0.371 | 0.364 | 0.384 | 0.363 | 0.367 | 0.391 | 0.38 | 0.357 | 2.313 | 2.304 | 2.32 | 2.346 | 2.367 | 2.386 | 2.358 | 2.393 | 2.392 | 2.272 | 2.252 | 2.329 | 259 | 272 | 284 | 289 | 289 | 290 | 283 | 288 | 281 | 260 | 248 | 251 | 31 | 36 | 38 | 39 | 39 | 38 | 39 | 37 | 35 | 36 | 33 | 29 | 774 | 1127 | 1609 | 2043 | 2417 | 2679 | 2562 | 2354 | 1967 | 1433 | 976 | 715 | 111 | 124 | 133 | 144 | 124 | 81 | 88 | 63 | 54 | 73 | 54 | 96 | 1.44 | N/A | N/A | 1.6 | N/A | N/A | -166 | -506 | 572 | 308 | 1.03 | N/A | -1.98 | 0.99 | N/A | N/A | -49 | -266 | 340 | 110 | 27
| POINT-MUGU-NAS_STYP20 | 6 | 4 | USA | CA | POINT MUGU NAS | 723910 | 93111 | 34.117 | -119.117 | 13 | 14.69 | -8 | NAP | 94-19 | 3C | 12 | 38.9 | 41.1 | 8.4 | 8.5 | 62.7 | 14 | 11.2 | 64.9 | 28.6 | 63.2 | 26.3 | 61.2 | 4.9 | 10 | 0.434 | 8 | 14.2 | 82.7 | 61.8 | 79.4 | 63.2 | 76.7 | 63.3 | 70.1 | 76.7 | 68.5 | 75.1 | 67.2 | 73.7 | 12.5 | 60 | 67.7 | 101.7 | 73.9 | 65.8 | 95.3 | 72.8 | 64.2 | 90.1 | 70.6 | 34 | 75.6 | 32.7 | 75.1 | 31.6 | 73.9 | 78.4 | 23.2 | 19.1 | 16.5 | 34.8 | 92.2 | 3 | 4.6 | 32.6 | 95.5 | 30.9 | 98.2 | 29.2 | 100.8 | 27 | 104.1 | 31.4 | 72.1 | 3.3 | 2.7 | 29 | 74 | 27.1 | 75.6 | 25.3 | 77.2 | 22.9 | 79.2 | 60.2 | 56 | 55.1 | 56.3 | 57 | 59.2 | 62.4 | 65.5 | 66.1 | 65.7 | 63.4 | 59.6 | 55.2 | 6.06 | 6.1 | 5.25 | 4.51 | 4.14 | 3.01 | 2.81 | 3.09 | 3.49 | 4.01 | 4.72 | 5.45 | 5.3 | 30 | 8 | 8 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 9 | 2033 | 292 | 283 | 273 | 243 | 181 | 87 | 30 | 27 | 37 | 87 | 182 | 311 | 3735 | 194 | 151 | 198 | 212 | 286 | 371 | 479 | 501 | 470 | 416 | 288 | 169 | 265 | 13 | 6 | 4 | 4 | 2 | 9 | 44 | 62 | 58 | 38 | 19 | 6 | 1291 | 87 | 50 | 41 | 52 | 17 | 21 | 85 | 180 | 250 | 290 | 170 | 48 | 247 | 18 | 13 | 9 | 11 | 3 | 3 | 6 | 12 | 34 | 87 | 43 | 8 | 6.9 | 7.6 | 7.5 | 7.4 | 7.8 | 7.3 | 6.6 | 6.4 | 6.1 | 5.8 | 6.3 | 6.7 | 7.5 | 11.2 | 2.4 | 3.1 | 2.1 | 0.7 | 0.1 | 0 | 0 | 0.1 | 0.1 | 0.2 | 1.9 | 1.8 | 20.6 | 11.6 | 16.6 | 7.3 | 4.2 | 1.5 | 0.3 | 0.2 | 1.2 | 0.9 | 0.8 | 6.4 | 5.3 | 3.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1 | 2.6 | 3.8 | 2 | 1 | 0.3 | 0.1 | 0 | 0.2 | 0.2 | 0.2 | 1.6 | 1.6 | 82.1 | 81.9 | 79.8 | 81.1 | 75.3 | 76.4 | 79.7 | 81.4 | 84 | 90.4 | 85.8 | 80.3 | 55.8 | 56.6 | 57.6 | 58 | 62.4 | 65.1 | 69.4 | 69.4 | 68.4 | 58.9 | 58.9 | 53.7 | 75.5 | 72.6 | 72.4 | 73 | 70.6 | 72.6 | 76.3 | 78.1 | 80 | 81.7 | 78.7 | 72.7 | 53.8 | 54.3 | 55.8 | 58.2 | 61.6 | 64.3 | 67.9 | 68 | 68.8 | 60 | 56.3 | 52.9 | 71.3 | 68 | 67.8 | 68.3 | 68.1 | 70.6 | 73.8 | 75.7 | 76.9 | 76.5 | 74 | 68.1 | 52.9 | 55.1 | 56.7 | 58 | 60.3 | 63.2 | 66.3 | 67 | 67.4 | 61.3 | 55.9 | 52.8 | 66.8 | 64 | 64.2 | 65.1 | 66.1 | 69.2 | 72.2 | 73.5 | 74.1 | 72.5 | 70 | 64.9 | 52.6 | 54.5 | 56.7 | 57.4 | 59.4 | 62.4 | 65.4 | 65.8 | 66 | 62 | 56.6 | 53.2 | 61.4 | 61.5 | 62.4 | 62.5 | 65.4 | 67.4 | 72.3 | 70.7 | 71.8 | 70.2 | 64.8 | 62.3 | 66.8 | 69.3 | 69 | 71.1 | 71.1 | 73.2 | 75 | 78.6 | 79.8 | 76.6 | 73.8 | 66.1 | 59.6 | 59.5 | 60.3 | 60.5 | 63.1 | 65.4 | 69.6 | 69 | 70 | 67.3 | 62.5 | 60.1 | 64.5 | 65.8 | 66.6 | 68 | 67.7 | 70.8 | 74.5 | 76.2 | 77.5 | 73.5 | 69.8 | 64.2 | 58.3 | 58.1 | 59.1 | 59.3 | 61.8 | 64.1 | 67.6 | 67.8 | 68.3 | 65.2 | 61 | 58.3 | 63.4 | 63.8 | 64.5 | 65.9 | 66.3 | 68.9 | 73.3 | 74.6 | 75.5 | 71.6 | 67.7 | 62.9 | 56.9 | 56.8 | 57.8 | 58.2 | 60.2 | 63 | 65.9 | 66.4 | 66.7 | 63.7 | 59.6 | 56.7 | 62.3 | 62 | 62.7 | 64.1 | 64.9 | 67.6 | 71.5 | 72.9 | 73.3 | 69.4 | 65.9 | 61.7 | 18 | 16.8 | 15.9 | 16.2 | 14 | 13.2 | 13.1 | 14.2 | 15.2 | 17.3 | 19.2 | 18.7 | 24.1 | 23.5 | 22.9 | 22.6 | 17.3 | 15.8 | 15.1 | 16.5 | 18.9 | 25 | 25.9 | 23.5 | 12.2 | 12.9 | 12.9 | 12.8 | 10.2 | 9.3 | 8.4 | 9.2 | 10.2 | 13.1 | 13.6 | 13.4 | 17.6 | 17 | 16.2 | 18.2 | 15.4 | 14.2 | 13.9 | 15.6 | 17.3 | 18.1 | 19.7 | 17.4 | 12.6 | 11.5 | 11.3 | 11.8 | 9.7 | 8.8 | 8.3 | 8.9 | 10.1 | 12.3 | 13.8 | 12.7 | 0.309 | 0.32 | 0.334 | 0.375 | 0.394 | 0.39 | 0.418 | 0.387 | 0.381 | 0.36 | 0.314 | 0.316 | 2.579 | 2.566 | 2.518 | 2.387 | 2.355 | 2.376 | 2.352 | 2.412 | 2.429 | 2.477 | 2.59 | 2.576 | 288 | 296 | 299 | 289 | 283 | 283 | 274 | 282 | 279 | 277 | 284 | 279 | 25 | 28 | 32 | 38 | 40 | 39 | 39 | 36 | 34 | 30 | 24 | 24 | 990 | 1268 | 1694 | 2096 | 2275 | 2351 | 2321 | 2198 | 1877 | 1433 | 1110 | 899 | 73 | 128 | 108 | 120 | 167 | 126 | 115 | 85 | 80 | 113 | 68 | 71 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.13 | N/A | -3.06 | 1.26 | N/A | N/A | N/A | -230 | 419 | 173 | 48
| SANTA-BARBARA_STYP20 | 6 | 4 | USA | CA | SANTA BARBARA | 723925 | 23190 | 34.426 | -119.843 | 9 | 14.69 | -8 | NAP | 94-19 | 3C | 12 | 35.4 | 37.3 | 21.5 | 16.1 | 55.7 | 25.4 | 19.4 | 53.9 | 20.8 | 58.5 | 18.7 | 58.3 | 0.7 | 60 | 0.418 | 8 | 15.6 | 83.5 | 63.5 | 80.1 | 63.4 | 77.2 | 63 | 68.8 | 77.3 | 67.3 | 75.4 | 66.1 | 73.8 | 8.8 | 250 | 65.6 | 94.6 | 72.7 | 64 | 89.4 | 70.7 | 63.1 | 86.5 | 69.5 | 32.9 | 77.1 | 31.7 | 75.3 | 30.8 | 73.7 | 76.3 | 18.8 | 16.1 | 12.9 | 30.9 | 92.8 | 2.4 | 4.3 | 29.1 | 96 | 27.7 | 98.5 | 26.4 | 100.9 | 24.6 | 104.1 | 28.5 | 70.5 | 2.4 | 1.9 | 26.8 | 71.9 | 25.4 | 73 | 24 | 74.1 | 22.2 | 75.5 | 59.6 | 53.3 | 54 | 56.2 | 58 | 60.4 | 62.7 | 65.8 | 66.3 | 65.7 | 62.4 | 57.3 | 52.8 | 6.23 | 4.29 | 4.27 | 4.15 | 4.42 | 3.97 | 3.06 | 3.13 | 3.14 | 4.03 | 4.4 | 4.4 | 4.14 | 51 | 16 | 10 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 18 | 2205 | 363 | 308 | 274 | 217 | 156 | 82 | 27 | 20 | 37 | 107 | 235 | 379 | 3555 | 118 | 123 | 195 | 241 | 322 | 381 | 488 | 505 | 472 | 384 | 221 | 105 | 231 | 0 | 0 | 2 | 7 | 12 | 13 | 50 | 60 | 58 | 26 | 3 | 0 | 1509 | 22 | 29 | 46 | 89 | 112 | 68 | 144 | 233 | 339 | 324 | 97 | 6 | 320 | 1 | 2 | 6 | 22 | 33 | 13 | 20 | 30 | 73 | 98 | 22 | 0 | 5.2 | 4.1 | 5.2 | 5.7 | 6.5 | 6.3 | 5.8 | 5.7 | 5.3 | 5 | 4.5 | 4.1 | 4.1 | 16 | 3.2 | 3.7 | 3.1 | 0.9 | 0.2 | 0 | 0 | 0.1 | 0.1 | 0.5 | 2 | 2.2 | 35.1 | 12.2 | 13.6 | 11.5 | 5.7 | 1.8 | 0.5 | 0.4 | 1.9 | 1.3 | 2.4 | 6.9 | 5.8 | 4.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7 | 3.1 | 3.3 | 2.8 | 1.4 | 0.4 | 0.1 | 0.1 | 0.3 | 0.3 | 0.6 | 2 | 1.9 | 77 | 78.5 | 79.6 | 82.7 | 84.6 | 81.5 | 82.2 | 83.8 | 86.6 | 89.3 | 82.8 | 74.5 | 54.7 | 57.1 | 59.2 | 59.9 | 60.6 | 63.6 | 67 | 68.3 | 65.3 | 61.6 | 58.6 | 55.5 | 71.7 | 71.9 | 73.1 | 75.4 | 76.2 | 75 | 77.4 | 79.3 | 81.4 | 81.9 | 76.1 | 70 | 54.2 | 55.9 | 57 | 57.5 | 60.1 | 62.9 | 66.2 | 67 | 66.8 | 61 | 57.5 | 54.6 | 67.4 | 66.8 | 69.1 | 71.2 | 71.9 | 72.3 | 74.9 | 76.3 | 77.6 | 76.9 | 71.7 | 66.3 | 54.2 | 54.5 | 55.9 | 57.1 | 59.4 | 62.1 | 65.4 | 66 | 65.5 | 60.8 | 57.3 | 54.4 | 63.8 | 63.3 | 65.4 | 67.4 | 68.4 | 70 | 72.7 | 73.7 | 74.6 | 72.9 | 68 | 63.4 | 54.8 | 53.9 | 55.2 | 56.3 | 58.7 | 61.6 | 64.5 | 65 | 64.8 | 61 | 57 | 53.8 | 62.7 | 61 | 62.2 | 63.3 | 65.3 | 66.3 | 69.7 | 69.9 | 71 | 69.3 | 63.6 | 61.5 | 65.8 | 68.6 | 72.5 | 75 | 75.6 | 75.7 | 77.4 | 80 | 79.3 | 77.5 | 72.5 | 66.5 | 59.3 | 59 | 59.9 | 60.5 | 62.8 | 64.6 | 67.5 | 68.1 | 69 | 66 | 61.7 | 59.3 | 63.6 | 64.8 | 67.2 | 69.7 | 71.3 | 72.3 | 74.9 | 77.1 | 77.1 | 74.1 | 68.6 | 64.1 | 57.7 | 57.5 | 58.5 | 59.2 | 61.3 | 63.5 | 66.2 | 66.7 | 67.2 | 64.1 | 60.3 | 57.5 | 62.2 | 62.8 | 64.8 | 67.1 | 68.7 | 70.3 | 73.5 | 74.8 | 74.8 | 71.3 | 66.9 | 62.1 | 56.3 | 56.2 | 57.3 | 57.8 | 59.9 | 62.3 | 64.9 | 65.6 | 65.8 | 62.5 | 59 | 55.8 | 61.2 | 61.4 | 63 | 65 | 66.3 | 68.5 | 71.9 | 72.9 | 72.9 | 69.3 | 65.5 | 61.1 | 21.5 | 19.5 | 18 | 18.3 | 16.4 | 14.8 | 14.7 | 15.6 | 17.5 | 20.7 | 22.4 | 22 | 29.3 | 27.5 | 25.8 | 25.8 | 23 | 19.9 | 18 | 19.9 | 23.4 | 29.4 | 29.3 | 28.1 | 16.4 | 14.9 | 13.4 | 12.8 | 11.3 | 10.3 | 8.8 | 9.6 | 11.3 | 14.6 | 15.8 | 16.8 | 19.7 | 19.5 | 19.4 | 20.9 | 18.5 | 17 | 16.4 | 18.1 | 19.7 | 21.6 | 22.2 | 20.8 | 13.8 | 12 | 11.7 | 11.7 | 10.1 | 9.2 | 8.1 | 8.9 | 9.9 | 12.4 | 14 | 14.5 | 0.304 | 0.318 | 0.326 | 0.364 | 0.379 | 0.365 | 0.395 | 0.374 | 0.363 | 0.351 | 0.309 | 0.311 | 2.592 | 2.566 | 2.543 | 2.421 | 2.396 | 2.438 | 2.409 | 2.435 | 2.474 | 2.5 | 2.599 | 2.585 | 290 | 297 | 302 | 292 | 287 | 290 | 280 | 286 | 285 | 280 | 286 | 280 | 24 | 28 | 31 | 36 | 38 | 36 | 37 | 36 | 33 | 30 | 24 | 23 | 974 | 1248 | 1685 | 2102 | 2320 | 2411 | 2332 | 2184 | 1869 | 1433 | 1099 | 882 | 74 | 131 | 109 | 119 | 152 | 111 | 92 | 82 | 75 | 105 | 60 | 71 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.1 | N/A | -2.92 | 1.22 | N/A | N/A | N/A | -229 | 396 | 149 | 37
| CAMARILLO_STYP20 | 6 | 4 | USA | CA | CAMARILLO | 723926 | 23136 | 34.217 | -119.083 | 77 | 14.66 | -8 | NAP | 94-19 | 3C | 12 | 37.7 | 40 | 5.6 | 7.3 | 65.5 | 11.3 | 9.8 | 64.1 | 33.6 | 63 | 30.2 | 64.5 | 2.7 | 70 | 0.409 | 8 | 16.7 | 87.8 | 63 | 83.7 | 62.9 | 80.9 | 63.4 | 69.6 | 80.1 | 68.4 | 78.5 | 67.2 | 76.9 | 12.9 | 70 | 65.8 | 95.4 | 75.5 | 64.2 | 90 | 73 | 63.3 | 87.2 | 71.6 | 33.7 | 80.4 | 32.6 | 78.7 | 31.7 | 76.9 | 76.1 | 24.9 | 20 | 16.3 | 33.7 | 97.9 | 2 | 4.1 | 32.3 | 100.9 | 31.1 | 103.3 | 30 | 105.6 | 28.5 | 108.6 | 29.5 | 71.9 | 2.2 | 1.8 | 27.9 | 73.2 | 26.6 | 74.2 | 25.4 | 75.2 | 23.8 | 76.5 | 61.7 | 56 | 55.6 | 57.5 | 59 | 61.7 | 64.9 | 68.3 | 68.8 | 68.1 | 64.8 | 59.9 | 55.3 | 6.81 | 6.05 | 5.36 | 4.64 | 4.62 | 3.79 | 3.09 | 3.41 | 3.34 | 4.28 | 5.36 | 5.78 | 5.25 | 28 | 8 | 7 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 9 | 1717 | 290 | 270 | 240 | 191 | 119 | 37 | 7 | 5 | 12 | 66 | 175 | 305 | 4294 | 195 | 163 | 234 | 270 | 361 | 447 | 568 | 582 | 543 | 459 | 299 | 173 | 508 | 12 | 6 | 6 | 10 | 15 | 34 | 109 | 122 | 105 | 61 | 23 | 5 | 3498 | 120 | 106 | 128 | 186 | 157 | 139 | 449 | 580 | 642 | 631 | 297 | 63 | 889 | 21 | 28 | 37 | 57 | 52 | 22 | 56 | 95 | 172 | 247 | 94 | 8 | 5.8 | 6.9 | 6.6 | 6.1 | 6.3 | 5.8 | 5.3 | 5.1 | 4.8 | 4.7 | 5.5 | 6 | 6.9 | 15 | 3.5 | 3.9 | 2.4 | 0.7 | 0.4 | 0.1 | 0 | 0 | 0.1 | 0.5 | 1.1 | 2.2 | 30 | 16.6 | 17.7 | 8.2 | 3.5 | 2 | 0.8 | 0.4 | 0.1 | 0.7 | 3.6 | 3.8 | 9.5 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9 | 3.5 | 3.7 | 2.1 | 0.8 | 0.5 | 0.2 | 0.1 | 0 | 0.1 | 0.8 | 0.9 | 2.2 | 82.8 | 84.4 | 84.9 | 87.8 | 86.1 | 83.4 | 85 | 87.3 | 90.5 | 94.7 | 89.6 | 80.9 | 54.8 | 56.5 | 57.6 | 59.8 | 60.5 | 67 | 69.2 | 69.1 | 67.4 | 61.3 | 59.8 | 54.7 | 77.2 | 76.5 | 77 | 79.2 | 77.4 | 77.6 | 81.1 | 82.2 | 84.3 | 86.6 | 81.8 | 74.6 | 52.9 | 54.5 | 55.8 | 57.9 | 61.6 | 64.7 | 67.7 | 68 | 67.2 | 60 | 57.1 | 52.9 | 72.6 | 70.6 | 71.6 | 73.3 | 73 | 74.7 | 78.8 | 79.5 | 80.8 | 80.5 | 76.4 | 69.9 | 52.6 | 53.4 | 55.7 | 57.2 | 60.7 | 63.8 | 67 | 67.2 | 66.4 | 60.4 | 55.6 | 52.2 | 67.7 | 65.6 | 67.4 | 69.3 | 70.1 | 72.4 | 76.2 | 77 | 77.1 | 75.5 | 71.4 | 65.9 | 51.4 | 53.3 | 55.9 | 56.7 | 59.9 | 62.7 | 66.1 | 66.1 | 65.3 | 60.2 | 55.5 | 51.9 | 60.5 | 60.6 | 62.1 | 62.7 | 66.1 | 68.2 | 71.5 | 70.9 | 71.4 | 68.8 | 64.2 | 61.4 | 68.6 | 69.8 | 74.2 | 77.1 | 78.4 | 80 | 80.7 | 83.2 | 83.2 | 79.6 | 76.2 | 68 | 58.7 | 58.8 | 59.9 | 60.5 | 63.7 | 66.1 | 69.3 | 69.2 | 69.3 | 66.3 | 62 | 59.2 | 65.2 | 67 | 69.7 | 72 | 73.9 | 75.9 | 78.3 | 80.1 | 79.9 | 76.6 | 72 | 65.1 | 57.2 | 57.3 | 58.5 | 59.2 | 62 | 64.7 | 68 | 68 | 67.7 | 64.5 | 60.3 | 57.4 | 63.4 | 65 | 67 | 69.6 | 70.9 | 73.3 | 77 | 77.9 | 77.9 | 73.8 | 69.1 | 63.1 | 55.7 | 55.9 | 57.2 | 57.8 | 60.4 | 63.3 | 66.5 | 66.7 | 66.3 | 62.9 | 58.9 | 55.5 | 62.9 | 62.8 | 64.6 | 66.8 | 68.3 | 71.2 | 75.2 | 75.9 | 75.6 | 71.6 | 67 | 61.6 | 20.3 | 19.7 | 19.3 | 19.5 | 16.7 | 15.1 | 15.6 | 16.7 | 17.8 | 20.1 | 21.8 | 21 | 27.3 | 28.4 | 28.6 | 28.5 | 23.1 | 19 | 18.4 | 20.3 | 23.2 | 29.9 | 30 | 26.7 | 12.8 | 14 | 14.4 | 13.6 | 11.7 | 9.8 | 8.6 | 9.9 | 11 | 13.7 | 14.4 | 14 | 18.8 | 20.5 | 20.4 | 21.4 | 18.7 | 16.9 | 16.6 | 18.1 | 19.4 | 21.1 | 22.2 | 19.3 | 12 | 12.1 | 12.1 | 11.5 | 10.1 | 9.1 | 8.3 | 9.5 | 9.7 | 12 | 13.9 | 13 | 0.311 | 0.323 | 0.337 | 0.38 | 0.4 | 0.396 | 0.425 | 0.392 | 0.386 | 0.365 | 0.317 | 0.319 | 2.562 | 2.547 | 2.496 | 2.362 | 2.328 | 2.353 | 2.324 | 2.392 | 2.405 | 2.447 | 2.573 | 2.557 | 287 | 295 | 298 | 288 | 281 | 281 | 272 | 280 | 278 | 275 | 283 | 277 | 25 | 29 | 32 | 39 | 41 | 40 | 41 | 37 | 35 | 31 | 25 | 24 | 986 | 1264 | 1696 | 2101 | 2300 | 2404 | 2367 | 2237 | 1902 | 1446 | 1112 | 898 | 74 | 132 | 108 | 118 | 159 | 124 | 110 | 77 | 71 | 107 | 64 | 70 | 1.62 | 1.3 | -4.32 | 2.47 | N/A | N/A | N/A | -454 | 693 | 319 | 1.13 | N/A | -3.06 | 1.26 | N/A | N/A | N/A | -230 | 419 | 173 | 47
| OXNARD_STYP20 | 6 | 4 | USA | CA | OXNARD | 723927 | 93110 | 34.201 | -119.207 | 36 | 14.68 | -8 | NAP | 98-19 | 3C | 12 | 40.8 | 42.9 | 7.9 | 8.3 | 63.5 | 13.6 | 11 | 61.5 | 28.4 | 61.4 | 25.9 | 62.4 | 5.8 | 50 | 0.437 | 7 | 10.7 | 82.4 | 60.1 | 78.8 | 60.6 | 75.5 | 61.9 | 68.8 | 75.4 | 67.3 | 73.6 | 66.1 | 72.1 | 12.4 | 70 | 66.1 | 96.4 | 72.9 | 64.4 | 90.6 | 70.6 | 63.4 | 87.5 | 68.9 | 33 | 75.2 | 31.7 | 73.7 | 30.7 | 72.1 | 74.7 | 23.9 | 19.3 | 16.7 | 36.6 | 93.1 | 2.2 | 5.5 | 35 | 97.1 | 33.7 | 100.4 | 32.5 | 103.5 | 30.9 | 107.5 | 31.7 | 69.7 | 2.1 | 1.9 | 30.2 | 71.1 | 29 | 72.2 | 27.8 | 73.3 | 26.3 | 74.7 | 60.6 | 56.3 | 55.5 | 56.8 | 57.8 | 60.3 | 63.1 | 66.2 | 66.1 | 65.8 | 63.5 | 59.4 | 55.6 | 5.82 | 5.68 | 4.99 | 4.36 | 4.03 | 3.07 | 2.29 | 2.99 | 2.76 | 3.92 | 4.8 | 5.03 | 4.82 | 20 | 6 | 5 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 1885 | 278 | 270 | 260 | 220 | 152 | 65 | 20 | 19 | 33 | 88 | 184 | 296 | 3876 | 201 | 159 | 212 | 236 | 318 | 394 | 503 | 500 | 473 | 418 | 283 | 179 | 268 | 9 | 5 | 5 | 5 | 6 | 9 | 58 | 54 | 56 | 41 | 17 | 3 | 1096 | 81 | 54 | 53 | 54 | 53 | 12 | 68 | 69 | 184 | 305 | 133 | 30 | 265 | 13 | 13 | 12 | 17 | 20 | 2 | 4 | 4 | 39 | 103 | 34 | 4 | 6.8 | 7 | 7.2 | 7.2 | 7.6 | 7.1 | 6.5 | 6.7 | 6.5 | 6.1 | 6.1 | 6.5 | 7.1 | 15 | 3.5 | 3.9 | 2.4 | 0.7 | 0.4 | 0.1 | 0 | 0 | 0.1 | 0.5 | 1.1 | 2.2 | 30 | 16.6 | 17.7 | 8.2 | 3.5 | 2 | 0.8 | 0.4 | 0.1 | 0.7 | 3.6 | 3.8 | 9.5 | 4.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9 | 3.5 | 3.7 | 2.1 | 0.8 | 0.5 | 0.2 | 0.1 | 0 | 0.1 | 0.8 | 0.9 | 2.2 | 81.8 | 81.7 | 80.6 | 80.6 | 80.6 | 74.9 | 79.2 | 79.8 | 84.4 | 90.6 | 84.8 | 78.4 | 54.9 | 55.8 | 56.6 | 57.9 | 57.9 | 64.4 | 68.3 | 68.1 | 66.7 | 59.5 | 57.7 | 53.2 | 75.3 | 72.8 | 72.7 | 72.6 | 71.3 | 71.7 | 75.5 | 75.5 | 78.7 | 81.5 | 77.5 | 71.7 | 52.4 | 53 | 54.9 | 56.8 | 60.1 | 63.1 | 66.9 | 66.6 | 66.8 | 59.7 | 55.8 | 52.6 | 70.3 | 67.6 | 67.2 | 67.9 | 67.8 | 69.9 | 73.4 | 73.4 | 75 | 76.1 | 72.4 | 67 | 52.3 | 53.6 | 55.4 | 56.3 | 59 | 62.1 | 65.6 | 65.4 | 65.7 | 60.5 | 55 | 52.4 | 65.8 | 63.5 | 64 | 64.8 | 66 | 68.2 | 72 | 72.1 | 72.7 | 72 | 68.2 | 63.9 | 51.8 | 53.2 | 55.5 | 56.3 | 58.4 | 61.1 | 64.7 | 64.7 | 64.8 | 60.7 | 55.8 | 52.1 | 60 | 60.2 | 60.7 | 61.2 | 63.2 | 65.9 | 70 | 69.4 | 70.8 | 69.3 | 63.1 | 61.3 | 65.8 | 66.2 | 68.7 | 70.7 | 69.5 | 73 | 76.4 | 76.7 | 78 | 76.6 | 71.4 | 66.4 | 58.5 | 58.4 | 59.2 | 59.4 | 61.7 | 64.1 | 68.2 | 67.6 | 68.8 | 66.1 | 61.4 | 59 | 64.1 | 64.3 | 65.8 | 67.2 | 67.3 | 69.8 | 74.3 | 74.1 | 75.2 | 73 | 68.1 | 63.6 | 57.3 | 57.2 | 58 | 58.3 | 60.4 | 63 | 66.5 | 66.4 | 67 | 64.2 | 60.1 | 57.3 | 63.2 | 63 | 64.1 | 65.3 | 65.9 | 68 | 72.2 | 72.4 | 73.3 | 70.6 | 66.5 | 61.8 | 55.8 | 55.8 | 56.9 | 57.2 | 59.3 | 62 | 65.5 | 65.3 | 65.6 | 62.7 | 58.8 | 55.7 | 61.6 | 61.4 | 62.5 | 63.5 | 64.8 | 66.9 | 70.8 | 70.9 | 71.7 | 68.7 | 65 | 60.7 | 17.2 | 15.9 | 14.8 | 14.4 | 12.2 | 10.5 | 10.7 | 11.3 | 12.8 | 15.5 | 17.3 | 16.9 | 24.1 | 23 | 21.8 | 20.8 | 15.8 | 12.6 | 12.4 | 13.1 | 16.1 | 24.1 | 24.2 | 21.5 | 11.8 | 12.1 | 11.7 | 11 | 8.4 | 6.8 | 6 | 6.7 | 9 | 12.8 | 13.4 | 12.6 | 16.1 | 16.3 | 15.7 | 15.9 | 13.2 | 11.4 | 11.6 | 12.6 | 13.7 | 16.8 | 17.6 | 15.6 | 11 | 10.9 | 9.7 | 9.2 | 7.4 | 6.3 | 5.7 | 6.7 | 7.7 | 11.2 | 12.5 | 11.8 | 0.308 | 0.319 | 0.331 | 0.376 | 0.397 | 0.39 | 0.42 | 0.388 | 0.382 | 0.359 | 0.313 | 0.315 | 2.578 | 2.566 | 2.522 | 2.381 | 2.343 | 2.374 | 2.342 | 2.405 | 2.422 | 2.472 | 2.588 | 2.573 | 289 | 297 | 300 | 289 | 282 | 283 | 274 | 282 | 279 | 277 | 284 | 279 | 25 | 28 | 31 | 38 | 40 | 39 | 40 | 37 | 35 | 30 | 24 | 24 | 986 | 1264 | 1694 | 2101 | 2295 | 2385 | 2348 | 2218 | 1891 | 1441 | 1111 | 897 | 73 | 130 | 109 | 120 | 163 | 121 | 110 | 81 | 75 | 110 | 65 | 70 | 1.46 | N/A | -4.79 | 3.26 | 1.44 | N/A | N/A | -414 | 569 | 169 | 1.15 | N/A | -3.13 | 1.21 | N/A | N/A | N/A | -230 | 421 | 171 | 45
| VANDENBERG-AFB_STYP20 | 5 | 4 | USA | CA | VANDENBERG AFB | 723930 | 93214 | 34.717 | -120.567 | 369 | 14.5 | -8 | NAP | 95-19 | 3C | 12 | 35.7 | 37.2 | 20.7 | 15.7 | 51.8 | 24.7 | 19 | 51 | 27.7 | 56 | 25.7 | 55.8 | 6.9 | 110 | 0.55 | 9 | 16.1 | 80.6 | 60.3 | 75.7 | 59.2 | 72.5 | 59 | 65 | 72.9 | 63.4 | 70.2 | 62.2 | 68.5 | 8.3 | 270 | 62.5 | 85.7 | 66.5 | 60.9 | 81 | 65.2 | 59.5 | 76.9 | 64.1 | 30.1 | 72.4 | 28.9 | 70.4 | 28 | 68.5 | 77.9 | 26.3 | 23.5 | 20.1 | 30.2 | 91.6 | 3.6 | 5.7 | 27.6 | 95.7 | 25.5 | 99.1 | 23.5 | 102.3 | 20.9 | 106.5 | 27.5 | 68.5 | 3.3 | 3.3 | 25.1 | 70.8 | 23.2 | 72.8 | 21.3 | 74.6 | 18.9 | 77 | 56.2 | 52.2 | 52.5 | 53.3 | 54.1 | 55.6 | 57.1 | 59.8 | 60.5 | 61.1 | 59.8 | 56.2 | 52 | 5.36 | 5.01 | 5.19 | 4.13 | 4.27 | 3.5 | 3.1 | 2.78 | 2.82 | 4.08 | 5.04 | 5.13 | 4.72 | 117 | 33 | 27 | 12 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32 | 3265 | 397 | 351 | 362 | 331 | 295 | 240 | 165 | 142 | 132 | 178 | 269 | 403 | 2385 | 102 | 98 | 116 | 130 | 173 | 213 | 303 | 327 | 333 | 304 | 192 | 94 | 56 | 0 | 1 | 1 | 2 | 2 | 3 | 3 | 4 | 16 | 18 | 6 | 0 | 607 | 10 | 25 | 19 | 37 | 43 | 38 | 10 | 26 | 123 | 200 | 71 | 5 | 172 | 0 | 4 | 3 | 10 | 16 | 19 | 2 | 5 | 36 | 62 | 15 | 0 | 8.8 | 8.9 | 9.5 | 9.6 | 10.8 | 10.5 | 9.2 | 7.5 | 7.2 | 7.2 | 7.9 | 8.2 | 9 | 16.6 | 3.6 | 3.7 | 2.7 | 1.1 | 0.4 | 0.1 | 0 | 0 | 0.1 | 0.8 | 1.3 | 2.8 | 32.6 | 16.3 | 15.7 | 12.6 | 4.3 | 2.4 | 0.7 | 0.3 | 0.1 | 0.4 | 4 | 4.5 | 9.3 | 6.2 | 0.2 | 0.1 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 6.6 | 3.5 | 3.3 | 2.8 | 1.1 | 0.6 | 0.2 | 0.1 | 0 | 0.1 | 0.9 | 1.1 | 2.2 | 75.3 | 78 | 76.5 | 79 | 79.3 | 77.3 | 74.3 | 77 | 85.1 | 87.3 | 81.4 | 73.2 | 54.4 | 57.8 | 57.9 | 58.9 | 58.5 | 61.6 | 63.6 | 64.6 | 63.8 | 61 | 58.6 | 53.4 | 69.9 | 71.1 | 69.6 | 70.3 | 69.8 | 69.3 | 70.8 | 71.8 | 77.2 | 79.4 | 74.6 | 67.9 | 53.2 | 54.7 | 54.9 | 55.7 | 58.9 | 59.8 | 62.4 | 62.5 | 63 | 59.5 | 56.6 | 53.3 | 64.9 | 65.2 | 64.7 | 64.8 | 65 | 65.8 | 68.1 | 69.2 | 72.5 | 73.5 | 69.4 | 63.7 | 53.1 | 54.2 | 54.5 | 55.7 | 57.1 | 58.7 | 61.1 | 61.6 | 62.1 | 58.5 | 55.8 | 53.1 | 61 | 61.3 | 61.5 | 61.9 | 62.6 | 63.5 | 65.9 | 66.7 | 69.4 | 69.4 | 65.4 | 60.9 | 53.1 | 53.2 | 54.1 | 54.5 | 55.9 | 57.3 | 59.9 | 60.5 | 61.3 | 58.8 | 55.5 | 53.5 | 60.1 | 60.4 | 60.2 | 60.9 | 62.3 | 63.2 | 65.5 | 65.8 | 68.2 | 66.8 | 62.1 | 60.7 | 63.6 | 67.2 | 68.6 | 70.8 | 71.2 | 75.3 | 71.7 | 74.1 | 77.9 | 75.5 | 71 | 64.2 | 57.6 | 58.3 | 58.3 | 58.4 | 60 | 60.6 | 63.1 | 63.4 | 65.3 | 63.8 | 60.1 | 58.8 | 61.2 | 64.4 | 64.9 | 66.2 | 67 | 67.3 | 69.4 | 69.6 | 72.9 | 70.2 | 67.4 | 61.8 | 56.3 | 56.5 | 56.6 | 56.7 | 58 | 59.2 | 61.5 | 62.1 | 63.4 | 62 | 58.6 | 56.8 | 60.2 | 62.4 | 62.3 | 63.4 | 64.2 | 64.7 | 66.7 | 67.7 | 70 | 68.5 | 65.1 | 59.8 | 54.7 | 54.9 | 55 | 55.2 | 56.3 | 57.9 | 60.2 | 60.9 | 61.9 | 60.2 | 57.2 | 54.8 | 58.9 | 60.4 | 60 | 60.8 | 61.7 | 62.6 | 64.9 | 65.9 | 67.9 | 66.7 | 63.2 | 58.5 | 18.7 | 18 | 17.3 | 16.6 | 14.6 | 13.4 | 12.6 | 13.4 | 16.1 | 19.2 | 19.6 | 18.5 | 25 | 25.5 | 24.2 | 23.2 | 20.7 | 18.6 | 16.2 | 16.7 | 22.5 | 27.3 | 26.3 | 23.2 | 13.7 | 13.7 | 13.1 | 12.7 | 11.8 | 10.7 | 8.6 | 8.8 | 11.6 | 14 | 14 | 14 | 17.1 | 19.1 | 18.9 | 19.7 | 18.9 | 16.3 | 15.2 | 15.8 | 19.2 | 20.9 | 20.3 | 15 | 11.4 | 11.7 | 11.7 | 11.7 | 11.1 | 9.6 | 8.3 | 8.5 | 10.6 | 11.9 | 12.4 | 11 | 0.302 | 0.316 | 0.323 | 0.339 | 0.349 | 0.349 | 0.357 | 0.342 | 0.343 | 0.335 | 0.304 | 0.306 | 2.603 | 2.571 | 2.552 | 2.493 | 2.486 | 2.479 | 2.513 | 2.528 | 2.528 | 2.553 | 2.611 | 2.603 | 290 | 297 | 302 | 300 | 296 | 295 | 292 | 296 | 292 | 286 | 287 | 282 | 24 | 28 | 30 | 34 | 35 | 35 | 34 | 32 | 31 | 28 | 23 | 23 | 955 | 1227 | 1668 | 2076 | 2294 | 2354 | 2215 | 2051 | 1789 | 1389 | 1066 | 851 | 73 | 123 | 107 | 128 | 152 | 111 | 84 | 97 | 98 | 105 | 60 | 75 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.17 | N/A | -2.45 | 1.44 | N/A | N/A | N/A | -301 | 432 | 137 | 26
| SANTA-MARIA_STYP20 | 5 | 4 | USA | CA | SANTA MARIA | 723940 | 23273 | 34.899 | -120.449 | 242 | 14.57 | -8 | NAP | 94-19 | 3C | 12 | 33.6 | 35.9 | 21.2 | 16 | 55.6 | 25 | 19.3 | 50.7 | 23.7 | 58.6 | 20.5 | 58.1 | 2.9 | 120 | 0.504 | 9 | 20.3 | 85.1 | 62.3 | 80.9 | 61.8 | 77.4 | 61.3 | 66.5 | 78.4 | 65 | 76.2 | 63.8 | 74.2 | 9.8 | 310 | 62.2 | 84.4 | 69.8 | 60.5 | 79.4 | 68.5 | 59.3 | 76.1 | 67.3 | 31.2 | 78.5 | 30 | 76 | 29.1 | 74.2 | 74.8 | 24.4 | 20.6 | 18.3 | 28.9 | 95 | 2.5 | 4.6 | 27.1 | 98.2 | 25.7 | 100.9 | 24.3 | 103.5 | 22.5 | 106.8 | 26.8 | 69.4 | 2.5 | 2.4 | 25 | 71.1 | 23.6 | 72.5 | 22.2 | 73.9 | 20.4 | 75.7 | 58.4 | 52.9 | 53.4 | 55.4 | 56.3 | 58.7 | 61 | 63.5 | 63.9 | 64.2 | 61.9 | 57 | 52.4 | 6.2 | 4.99 | 5.31 | 4.86 | 4.9 | 3.9 | 3.4 | 3.15 | 3.08 | 4.26 | 5.23 | 5.43 | 4.85 | 102 | 27 | 22 | 9 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 31 | 2554 | 374 | 327 | 301 | 265 | 203 | 127 | 67 | 58 | 65 | 127 | 248 | 392 | 3170 | 118 | 116 | 175 | 196 | 268 | 330 | 420 | 432 | 425 | 370 | 216 | 104 | 148 | 0 | 1 | 2 | 5 | 7 | 8 | 22 | 24 | 40 | 32 | 7 | 0 | 1700 | 30 | 50 | 67 | 112 | 122 | 109 | 135 | 146 | 351 | 427 | 135 | 16 | 482 | 2 | 9 | 13 | 36 | 41 | 33 | 18 | 30 | 114 | 154 | 32 | 0 | 6.6 | 5.8 | 6.6 | 7.3 | 8.1 | 8.4 | 7.6 | 6.4 | 6 | 5.8 | 5.9 | 5.6 | 5.7 | 12.6 | 2.4 | 2.8 | 2.3 | 0.9 | 0.2 | 0 | 0 | 0 | 0.2 | 0.6 | 1.3 | 1.9 | 26.8 | 11.8 | 11.6 | 9.4 | 3.9 | 2.4 | 0.9 | 0.4 | 0.9 | 1.6 | 2.4 | 4.7 | 9.8 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4 | 2.3 | 2.7 | 2 | 1.1 | 0.4 | 0.1 | 0.1 | 0.1 | 0.3 | 0.6 | 1.2 | 1.7 | 78.2 | 80.7 | 81 | 84.8 | 85.3 | 83.3 | 82.3 | 83.5 | 90.4 | 91.6 | 84.4 | 76.2 | 55.1 | 59.1 | 60.1 | 60.6 | 61.2 | 65.3 | 66.4 | 65.7 | 64.8 | 63.2 | 60.4 | 54.3 | 72.2 | 73.5 | 74.4 | 76.1 | 76.1 | 76.2 | 77.5 | 77.4 | 82.6 | 84.2 | 77.7 | 70.8 | 55 | 56.9 | 57.7 | 58.7 | 60.6 | 62.5 | 64.7 | 64.8 | 63.9 | 60.1 | 57.4 | 54.3 | 67.9 | 67.9 | 69.8 | 70.7 | 70.9 | 72.3 | 74.3 | 74.4 | 77.3 | 78.3 | 72.6 | 66.2 | 54 | 55.3 | 56.6 | 57.9 | 59 | 61.2 | 63.5 | 63.5 | 63.5 | 59.5 | 56.4 | 53.6 | 63.2 | 63.4 | 65.5 | 66.6 | 67.5 | 69.7 | 71.6 | 72.1 | 73.4 | 73.1 | 68 | 62.6 | 53.8 | 53.9 | 55.8 | 56.3 | 57.8 | 59.8 | 62 | 62.4 | 62.4 | 59.2 | 55.9 | 53.2 | 61.3 | 62.1 | 63 | 63.8 | 65 | 65.5 | 68.2 | 67.8 | 69.8 | 67.4 | 63 | 61.2 | 67.4 | 72.5 | 75 | 78.3 | 78.4 | 79.7 | 79 | 80 | 82.1 | 81.5 | 75 | 67.1 | 58.8 | 59.3 | 60.3 | 60.7 | 61.9 | 63.4 | 65.5 | 65.4 | 66.4 | 64.3 | 60.8 | 58.8 | 64.9 | 67.8 | 70 | 72.1 | 73.6 | 74.7 | 76.5 | 76.1 | 77.6 | 75.9 | 70.3 | 63.5 | 57 | 57.4 | 58.5 | 58.9 | 59.7 | 61.8 | 63.9 | 64 | 64.3 | 62.3 | 59.2 | 56.9 | 62.6 | 65 | 66.9 | 69.1 | 69.4 | 71.8 | 73.6 | 73.9 | 74.9 | 73.1 | 67.7 | 61.5 | 55.2 | 55.4 | 56.8 | 57 | 58.2 | 60.1 | 62.3 | 62.5 | 62.7 | 60.4 | 57.6 | 55 | 61.2 | 61.8 | 64.1 | 65.3 | 66.6 | 68.7 | 71 | 71.4 | 72.2 | 70.2 | 65.9 | 60.3 | 22.1 | 21 | 21.2 | 21.6 | 19.5 | 18.7 | 17.7 | 17.9 | 20.3 | 23.1 | 23.6 | 22.4 | 29.6 | 29.2 | 28.8 | 29.2 | 26.2 | 23.3 | 21.3 | 21 | 27 | 32.7 | 30.9 | 28.4 | 16.3 | 16.1 | 15.5 | 15.2 | 13.3 | 11.5 | 10.3 | 10 | 12.6 | 15.2 | 15.3 | 16 | 20.9 | 22.9 | 23.1 | 24.9 | 22.6 | 21.7 | 20.1 | 20 | 23.2 | 25.6 | 24 | 19.1 | 13.3 | 13.7 | 13.7 | 14 | 11.8 | 10.9 | 10 | 9.7 | 11.4 | 13.1 | 13.3 | 12.6 | 0.304 | 0.32 | 0.324 | 0.341 | 0.352 | 0.352 | 0.361 | 0.347 | 0.347 | 0.342 | 0.304 | 0.308 | 2.583 | 2.543 | 2.537 | 2.476 | 2.465 | 2.461 | 2.49 | 2.497 | 2.503 | 2.517 | 2.599 | 2.583 | 289 | 295 | 302 | 299 | 295 | 294 | 290 | 294 | 290 | 283 | 286 | 280 | 24 | 28 | 31 | 35 | 35 | 36 | 34 | 33 | 32 | 29 | 24 | 23 | 945 | 1219 | 1669 | 2087 | 2343 | 2447 | 2326 | 2151 | 1846 | 1411 | 1065 | 844 | 75 | 126 | 112 | 131 | 140 | 102 | 77 | 79 | 82 | 96 | 58 | 75 | 1.13 | N/A | N/A | 1.85 | N/A | N/A | N/A | -385 | 425 | 63 | 1.17 | N/A | -2.3 | 1.35 | N/A | N/A | N/A | -301 | 432 | 137 | 27
| PASO-ROBLES_STYP20 | 4 | 4 | USA | CA | PASO ROBLES | 723965 | 93209 | 35.67 | -120.628 | 810 | 14.27 | -8 | NAP | 94-19 | 3B | 12 | 27.1 | 29.6 | 16.2 | 12.8 | 49.3 | 20 | 15.5 | 47.8 | 21.2 | 54.4 | 19.1 | 53.4 | 1.7 | 80 | 0.523 | 7 | 37.3 | 102.3 | 66.6 | 99 | 65.8 | 95.4 | 64.6 | 69.3 | 95.5 | 67.7 | 93.6 | 66.1 | 91.3 | 8.8 | 210 | 60 | 79.5 | 72.7 | 57.9 | 73.8 | 71.2 | 56.5 | 70.1 | 69.9 | 33.8 | 95.7 | 32.2 | 93.7 | 31.1 | 91.3 | 81 | 20.7 | 18.9 | 17.4 | 22.5 | 108.8 | 3.6 | 2.8 | 19.9 | 110.8 | 17.8 | 112.5 | 15.8 | 114 | 13.3 | 116.1 | 21 | 73.2 | 3.6 | 3.3 | 18.4 | 75.6 | 16.3 | 77.5 | 14.3 | 79.4 | 11.7 | 81.8 | 60.6 | 48.9 | 50.5 | 54.2 | 57.6 | 63.9 | 69.8 | 74.1 | 74 | 70.4 | 62.3 | 53.6 | 47.7 | 10.92 | 4.91 | 5.07 | 5.33 | 6.11 | 6.14 | 6 | 5.57 | 5.13 | 5.7 | 5.75 | 5.78 | 5.12 | 294 | 78 | 52 | 20 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 106 | 2611 | 498 | 407 | 334 | 233 | 97 | 21 | 2 | 1 | 16 | 121 | 344 | 537 | 4173 | 45 | 65 | 152 | 236 | 430 | 593 | 746 | 742 | 611 | 383 | 137 | 33 | 1015 | 0 | 0 | 1 | 10 | 62 | 164 | 284 | 279 | 176 | 38 | 1 | 0 | 16335 | 7 | 16 | 142 | 489 | 1368 | 2727 | 3898 | 3807 | 2694 | 1055 | 131 | 1 | 8895 | 1 | 0 | 28 | 174 | 648 | 1521 | 2297 | 2265 | 1491 | 443 | 27 | 0 | 6.4 | 4.8 | 5.3 | 5.9 | 7.4 | 8.6 | 9 | 8.1 | 7.3 | 6.2 | 5.2 | 4.5 | 4.6 | 12.4 | 2.6 | 2.7 | 2.2 | 0.9 | 0.1 | 0 | 0 | 0 | 0.2 | 0.4 | 1.4 | 1.9 | 24.4 | 12.2 | 8.8 | 9 | 4.5 | 1.7 | 0.1 | 0.3 | 0.9 | 1.3 | 2.4 | 5.2 | 6.8 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 2.4 | 2.6 | 1.9 | 1 | 0.3 | 0 | 0.1 | 0.2 | 0.3 | 0.6 | 1.3 | 1.5 | 73.4 | 76.6 | 83.7 | 91.5 | 98.9 | 104.2 | 106.4 | 106.4 | 103.1 | 95.9 | 83.7 | 71.4 | 52.6 | 57.8 | 60.7 | 61.2 | 65.1 | 67.4 | 68.8 | 69 | 66.5 | 63.9 | 58.3 | 51.7 | 68.1 | 71.3 | 78 | 85.1 | 92.9 | 99 | 101.6 | 101.6 | 98.6 | 89.7 | 77.8 | 66.1 | 52.8 | 56 | 58.6 | 60.1 | 63 | 65.3 | 67 | 66.2 | 65.1 | 61.1 | 57 | 51.9 | 63.6 | 66 | 73 | 79.7 | 87.4 | 94.4 | 97.5 | 97.5 | 94.2 | 84.9 | 72.3 | 62.6 | 52.7 | 54 | 56.5 | 58.4 | 61 | 64 | 65.8 | 65.4 | 63.7 | 59.5 | 55.3 | 52.1 | 59.7 | 61.7 | 68.4 | 74.3 | 81.9 | 89.5 | 93.1 | 92.9 | 89.5 | 80 | 67.2 | 58.8 | 51.6 | 52.5 | 55.1 | 56.3 | 59.5 | 62.7 | 64.6 | 64.2 | 63 | 58.4 | 53.8 | 51 | 59.6 | 60.9 | 63.5 | 64.9 | 67.6 | 70.8 | 71.5 | 71.6 | 70.6 | 66.8 | 61.3 | 59.5 | 64.2 | 70 | 78.2 | 83.8 | 94.2 | 99.3 | 101.5 | 99.7 | 92.2 | 86.4 | 74.5 | 64.3 | 56.6 | 58.1 | 60.2 | 61.6 | 64.7 | 67.7 | 69 | 68.6 | 67.4 | 63.7 | 59.3 | 56.8 | 62.1 | 66.1 | 74.1 | 80.3 | 89.1 | 93.7 | 95.8 | 96.2 | 90.2 | 83.4 | 71.8 | 60.9 | 54.7 | 55.9 | 58 | 59.4 | 62.4 | 65.5 | 67.2 | 66.8 | 65.4 | 61.5 | 57.5 | 54.5 | 60 | 63.4 | 70.4 | 77 | 84.2 | 90.5 | 93.6 | 93.7 | 90.1 | 79.2 | 68 | 58.7 | 52.8 | 53.7 | 55.8 | 57.3 | 60.2 | 63.4 | 65.5 | 65.1 | 63.6 | 59.6 | 55.5 | 52.1 | 58.2 | 60.3 | 66.2 | 72.5 | 79.2 | 86.7 | 90.8 | 90.2 | 87.1 | 76.4 | 64.9 | 56.9 | 24.3 | 23.6 | 27 | 30.5 | 32.7 | 36.5 | 37.3 | 38.2 | 37.4 | 34.3 | 28.9 | 24.4 | 32.2 | 32.8 | 36.2 | 40.6 | 43.1 | 44.8 | 44.2 | 45.1 | 45.1 | 43.2 | 37.9 | 31 | 19.1 | 18.7 | 18.8 | 18.6 | 17.5 | 16.8 | 15.6 | 16.1 | 17.6 | 19.1 | 19.3 | 18.6 | 22.6 | 26.1 | 31.9 | 36.4 | 39.3 | 40.7 | 40 | 41.3 | 39.8 | 37.2 | 30.5 | 19.8 | 14.8 | 15.8 | 17.4 | 17.9 | 16.9 | 16.8 | 15.2 | 16 | 16.3 | 17.2 | 16.7 | 13.7 | 0.301 | 0.314 | 0.32 | 0.337 | 0.354 | 0.34 | 0.362 | 0.339 | 0.345 | 0.335 | 0.308 | 0.305 | 2.554 | 2.524 | 2.509 | 2.457 | 2.418 | 2.464 | 2.43 | 2.474 | 2.461 | 2.491 | 2.54 | 2.552 | 288 | 296 | 302 | 300 | 294 | 297 | 290 | 296 | 289 | 283 | 282 | 279 | 25 | 29 | 31 | 35 | 37 | 35 | 36 | 34 | 33 | 29 | 25 | 23 | 895 | 1178 | 1641 | 2068 | 2408 | 2608 | 2478 | 2273 | 1924 | 1427 | 1031 | 797 | 81 | 129 | 125 | 148 | 121 | 89 | 75 | 59 | 58 | 78 | 54 | 82 | N/A | N/A | -3.67 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.9 | N/A | -1.75 | 0.97 | N/A | N/A | N/A | -266 | 319 | 76 | 29
| EASTERN-SIERRA_STYP20 | 16 | 4 | USA | CA | EASTERN SIERRA | 724800 | 23157 | 37.371 | -118.358 | 4102 | 12.64 | -8 | NAP | 94-19 | 4B | 12 | 16.1 | 19.3 | -6.5 | 4.5 | 43.8 | -2.7 | 5.5 | 46.2 | 28.4 | 45.5 | 25.9 | 45 | 5.6 | 320 | 0.561 | 7 | 39.3 | 101.5 | 62 | 99.3 | 61.3 | 97.2 | 60.5 | 65.9 | 93 | 64.2 | 91.4 | 62.8 | 90.3 | 10.1 | 160 | 57.3 | 81.7 | 72.6 | 53.8 | 71.8 | 75.3 | 50.6 | 63.6 | 75 | 32.7 | 92.4 | 31.3 | 91 | 30.2 | 90.3 | 72.7 | 25.5 | 22.5 | 19.5 | 9.1 | 105.5 | 3.1 | 1.7 | 6.9 | 106.8 | 5.1 | 107.8 | 3.4 | 108.8 | 1.2 | 110 | 7.3 | 67.6 | 3.2 | 2.2 | 5 | 69.1 | 3.1 | 70.4 | 1.3 | 71.6 | -1 | 73.2 | 57.1 | 39.8 | 42.3 | 49.2 | 54.6 | 62.9 | 72.4 | 78.1 | 75.7 | 68.1 | 56.9 | 45.5 | 38.2 | 15.04 | 6.3 | 6.62 | 6.65 | 7.11 | 6.95 | 6.29 | 4.08 | 3.75 | 5.42 | 6.45 | 6.98 | 6.16 | 1230 | 318 | 225 | 97 | 37 | 3 | 0 | 0 | 0 | 0 | 18 | 164 | 368 | 4063 | 781 | 635 | 490 | 314 | 122 | 16 | 0 | 0 | 32 | 257 | 584 | 832 | 3812 | 2 | 10 | 72 | 177 | 404 | 673 | 871 | 795 | 543 | 234 | 30 | 1 | 1170 | 0 | 0 | 0 | 4 | 58 | 239 | 406 | 331 | 125 | 7 | 0 | 0 | 23725 | 1 | 4 | 71 | 390 | 1685 | 4725 | 7130 | 6124 | 2984 | 589 | 22 | 0 | 13385 | 0 | 0 | 6 | 81 | 693 | 2745 | 4500 | 3730 | 1479 | 150 | 1 | 0 | 7.9 | 7 | 8 | 9 | 9.9 | 8.8 | 8.2 | 7.9 | 7.8 | 7.5 | 7.6 | 6.9 | 6.8 | 5.4 | 0.9 | 1 | 0.4 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 | 0.6 | 0.7 | 17.1 | 8.9 | 6 | 3 | 1.6 | 1.3 | 1.3 | 0.7 | 0.6 | 1.2 | 0.8 | 2.6 | 5.8 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2 | 1.5 | 1.5 | 0.6 | 0.3 | 0.4 | 0.3 | 0.2 | 0.2 | 0.3 | 0.2 | 0.7 | 1.1 | 69.2 | 73.6 | 80.3 | 86.5 | 95.1 | 102.9 | 105.1 | 102.5 | 97 | 88.6 | 76.9 | 67.3 | 46.2 | 47.2 | 50.8 | 54.1 | 58.5 | 61.1 | 63.5 | 63.1 | 60.6 | 56.2 | 50.3 | 45.6 | 64.4 | 68.7 | 75.7 | 82.2 | 90.9 | 99.4 | 102.3 | 100.1 | 94.2 | 84.2 | 72.6 | 62.4 | 44.1 | 45.5 | 48.7 | 51.9 | 56.4 | 59.9 | 62.8 | 61.8 | 59.4 | 54.3 | 48.7 | 43 | 60.4 | 64.6 | 72.2 | 78.8 | 87.5 | 96.8 | 100.1 | 98 | 91.9 | 80.5 | 68.4 | 58.4 | 42.6 | 44.1 | 47.4 | 50.7 | 55.1 | 59.4 | 61.9 | 60.8 | 58.5 | 52.5 | 46.7 | 41.4 | 55.7 | 59.6 | 68.5 | 74.8 | 83.8 | 94.1 | 97.9 | 95.9 | 89.1 | 76.8 | 63.8 | 53.9 | 40.7 | 42 | 45.9 | 49 | 53.9 | 58.6 | 61.2 | 60.1 | 57.2 | 50.7 | 44.5 | 39.5 | 49.5 | 49.2 | 52.2 | 56.1 | 60.4 | 65.5 | 68.4 | 67.8 | 64.3 | 59.2 | 52.2 | 48.1 | 64.8 | 67.7 | 76.2 | 82.5 | 90.8 | 97.1 | 96.2 | 96.1 | 89.6 | 77 | 73.1 | 62.4 | 46.2 | 46.9 | 50 | 53.1 | 57.8 | 62.5 | 66.4 | 65.1 | 62.3 | 56.1 | 49.8 | 45.2 | 59 | 65.7 | 73 | 79.3 | 86.6 | 94.4 | 93.2 | 92.7 | 88 | 79.1 | 69.6 | 58 | 44.1 | 44.9 | 48.3 | 51.2 | 56.3 | 60.9 | 64.9 | 63.5 | 60.4 | 53.8 | 47.7 | 42.4 | 57.3 | 61.8 | 70.2 | 76.5 | 84.1 | 92.8 | 91.4 | 91.3 | 86.1 | 77.4 | 66.2 | 55.6 | 41.8 | 42.9 | 46.4 | 49.7 | 54.6 | 59.4 | 63.5 | 62 | 58.4 | 51.7 | 45.5 | 40.2 | 55.1 | 57.8 | 67 | 73.6 | 81.1 | 90.6 | 90.1 | 89.6 | 84.9 | 74.2 | 62.9 | 53 | 29.4 | 29.6 | 33 | 33.3 | 35 | 38.6 | 39.3 | 40.5 | 39.3 | 36.6 | 33.8 | 29.5 | 37.2 | 38.6 | 39.1 | 40 | 40.6 | 42.2 | 41.9 | 42.6 | 42.6 | 41.9 | 39.6 | 36.9 | 20.7 | 19.7 | 18.6 | 17.3 | 15.6 | 14.9 | 14.7 | 15.6 | 17.3 | 19.2 | 20.7 | 21.3 | 32.6 | 34.6 | 37.1 | 38 | 38.7 | 39.9 | 36.7 | 38.2 | 39.6 | 38.2 | 37.3 | 33.6 | 18.9 | 18.3 | 18 | 17 | 15.3 | 15.4 | 13.9 | 15.1 | 17.1 | 17.8 | 19.8 | 20 | 0.262 | 0.276 | 0.287 | 0.318 | 0.333 | 0.33 | 0.34 | 0.328 | 0.305 | 0.289 | 0.265 | 0.261 | 2.473 | 2.446 | 2.443 | 2.398 | 2.415 | 2.437 | 2.47 | 2.478 | 2.545 | 2.567 | 2.576 | 2.513 | 298 | 306 | 312 | 305 | 300 | 300 | 296 | 298 | 302 | 298 | 297 | 292 | 25 | 30 | 33 | 37 | 37 | 36 | 35 | 34 | 30 | 26 | 23 | 23 | 857 | 1146 | 1571 | 2014 | 2292 | 2636 | 2454 | 2307 | 1962 | 1446 | 1013 | 764 | 74 | 107 | 107 | 107 | 177 | 168 | 148 | 125 | 75 | 97 | 56 | 76 | 0.68 | N/A | -2.63 | N/A | N/A | N/A | N/A | N/A | 220 | 146 | 0.97 | N/A | N/A | 0.72 | N/A | N/A | -81 | N/A | 274 | 166 | 14
| MERCED_STYP20 | 12 | 4 | USA | CA | MERCED | 724815 | 23257 | 37.285 | -120.513 | 152 | 14.62 | -8 | NAP | 98-19 | 3B | 12 | 29.7 | 32.1 | 21.5 | 16.2 | 48.7 | 25.4 | 19.6 | 46.5 | 24.7 | 53.8 | 20.6 | 52.2 | 2.4 | 100 | 0.464 | 7 | 32.2 | 101.5 | 69.5 | 99 | 68.7 | 96.7 | 67.6 | 72.2 | 96 | 70.6 | 94.1 | 69.1 | 92.2 | 9.3 | 330 | 63.6 | 88.5 | 81.7 | 61.5 | 81.9 | 79.9 | 59.9 | 77.5 | 79.2 | 35.9 | 96.1 | 34.4 | 94 | 33.2 | 92.3 | 85.8 | 19.5 | 16.8 | 14.4 | 26 | 106.2 | 2.4 | 2 | 24.3 | 107.6 | 22.9 | 108.8 | 21.5 | 109.9 | 19.8 | 111.3 | 24.6 | 75.4 | 2.8 | 4.1 | 22.6 | 78.4 | 21 | 80.8 | 19.4 | 83.1 | 17.4 | 86.1 | 62.4 | 46.4 | 50.2 | 55.2 | 59.8 | 67.5 | 74.8 | 79.5 | 77.7 | 73.4 | 64.1 | 53.5 | 46.5 | 12.86 | 4.84 | 4.68 | 5.5 | 6.35 | 6.22 | 6 | 4.95 | 4.29 | 5.87 | 5.6 | 5.54 | 5.18 | 365 | 131 | 51 | 16 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 135 | 2533 | 575 | 413 | 305 | 181 | 43 | 4 | 0 | 0 | 7 | 84 | 346 | 575 | 4907 | 21 | 57 | 177 | 297 | 544 | 743 | 914 | 858 | 702 | 436 | 133 | 25 | 1601 | 0 | 0 | 1 | 24 | 122 | 297 | 449 | 393 | 259 | 55 | 1 | 0 | 22521 | 0 | 0 | 95 | 507 | 1920 | 4216 | 6227 | 5229 | 3421 | 873 | 33 | 0 | 12184 | 0 | 0 | 12 | 164 | 841 | 2321 | 3739 | 3016 | 1806 | 282 | 3 | 0 | 6.1 | 4.6 | 5.5 | 5.9 | 7 | 7.8 | 8 | 7.5 | 7 | 5.9 | 5.2 | 4.3 | 4.9 | 12.4 | 2.4 | 2.2 | 2 | 1 | 0.4 | 0.1 | 0 | 0 | 0.2 | 0.7 | 1.6 | 1.9 | 21.7 | 7.1 | 6.1 | 5.5 | 4.6 | 2.1 | 0.6 | 0.4 | 0.5 | 1.3 | 3.8 | 4.9 | 4.5 | 6.6 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 3.9 | 1.8 | 1.6 | 1.5 | 0.9 | 0.6 | 0.2 | 0.1 | 0.1 | 0.3 | 0.9 | 1.3 | 1.2 | 66.3 | 71.5 | 81.5 | 91.1 | 97.5 | 103.9 | 105.3 | 103.3 | 100.3 | 92.9 | 78.2 | 65 | 53.2 | 57.7 | 61.3 | 64.4 | 67.2 | 70.6 | 71.1 | 69.5 | 67.7 | 65.1 | 60.2 | 55 | 61.9 | 67.5 | 76.4 | 84.4 | 93.3 | 99.4 | 101.9 | 99.7 | 97.7 | 86.8 | 73.1 | 61.3 | 52.8 | 56.3 | 59.7 | 61.9 | 65.4 | 69.4 | 69.7 | 68.8 | 66.7 | 63.5 | 58.1 | 53 | 58.7 | 64 | 72.6 | 80.1 | 89 | 96.2 | 99.2 | 97.2 | 94.3 | 82.3 | 69.3 | 58.5 | 52 | 54.5 | 58.4 | 60.5 | 63.5 | 67.4 | 69.4 | 67.8 | 65.9 | 61.4 | 56.9 | 52.1 | 55.5 | 61.1 | 68.7 | 75.1 | 84.2 | 92.3 | 96.3 | 94.2 | 90.7 | 79 | 65.2 | 55.9 | 50.5 | 53 | 56.8 | 58.4 | 61.8 | 66 | 68.1 | 67 | 65.1 | 59.9 | 55 | 50.7 | 57.4 | 60.3 | 64.5 | 67.1 | 70.3 | 73.3 | 74.7 | 73.2 | 72.4 | 67.8 | 62.4 | 58.8 | 61.3 | 67.5 | 76.1 | 83 | 93.3 | 98.2 | 97.3 | 96.1 | 91.1 | 84.3 | 73.8 | 62.9 | 55 | 58 | 61.6 | 63.8 | 67.1 | 71 | 72.4 | 71 | 69.3 | 65.4 | 59.9 | 55.7 | 58.7 | 64.7 | 73.6 | 81.2 | 89.8 | 95.4 | 97.3 | 94.7 | 90.5 | 82.2 | 70.4 | 58.9 | 53.1 | 55.8 | 59.5 | 61.5 | 64.7 | 69.1 | 70.6 | 69.3 | 67.6 | 63.4 | 57.9 | 53.7 | 56.2 | 62.4 | 70.2 | 77.8 | 85.7 | 92 | 95 | 92.7 | 90.2 | 80.1 | 66.5 | 56.9 | 51.3 | 54 | 57.4 | 59.5 | 62.7 | 67.4 | 69.1 | 68 | 66 | 61.4 | 56.1 | 51.6 | 55.2 | 59.8 | 66.9 | 73.2 | 82.2 | 89.7 | 92.8 | 91 | 88.1 | 75.6 | 63.6 | 54.8 | 17 | 20.5 | 23.5 | 25.8 | 28.8 | 31.4 | 32.2 | 32.3 | 31.5 | 27.6 | 22.4 | 17.8 | 22.8 | 25.6 | 30.1 | 33.7 | 35.3 | 35 | 34.3 | 35.1 | 36 | 33.3 | 28.6 | 21.5 | 14.9 | 15.4 | 15.4 | 14.5 | 13.6 | 12.1 | 11.5 | 11.7 | 12.1 | 14.2 | 15.2 | 13.8 | 16.6 | 22.3 | 27.6 | 31.2 | 33.2 | 33.3 | 32 | 33.1 | 33.1 | 29.2 | 24.2 | 14.6 | 11.8 | 14.3 | 15.3 | 14.3 | 13.7 | 12.3 | 11.8 | 11.8 | 12 | 12.6 | 13.7 | 10.3 | 0.347 | 0.352 | 0.359 | 0.361 | 0.361 | 0.352 | 0.366 | 0.355 | 0.356 | 0.367 | 0.355 | 0.335 | 2.384 | 2.393 | 2.369 | 2.381 | 2.402 | 2.436 | 2.409 | 2.417 | 2.425 | 2.378 | 2.373 | 2.445 | 263 | 278 | 286 | 292 | 292 | 293 | 288 | 290 | 284 | 268 | 257 | 260 | 29 | 32 | 36 | 37 | 37 | 36 | 37 | 36 | 34 | 32 | 29 | 25 | 744 | 1093 | 1564 | 2003 | 2397 | 2663 | 2591 | 2351 | 1935 | 1404 | 935 | 683 | 119 | 121 | 140 | 160 | 121 | 84 | 80 | 66 | 61 | 80 | 56 | 99 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.72 | N/A | -2.07 | N/A | N/A | N/A | N/A | -205 | 248 | 63 | 45
| VACAVILLE-NUT-TREE_STYP20 | 12 | 4 | USA | CA | VACAVILLE NUT TREE | 724828 | 93241 | 38.378 | -121.958 | 109 | 14.64 | -8 | NAP | 01-19 | 3A | 1 | 30.5 | 33.8 | 13.6 | 11 | 57.7 | 17.9 | 13.6 | 57.2 | 22 | 51 | 18.9 | 52.3 | 0.5 | 350 | 0.455 | 7 | 33.1 | 101.9 | 68.7 | 99.1 | 67.8 | 95.8 | 67 | 71.2 | 97 | 69.7 | 94.3 | 68.4 | 92.2 | 8.3 | 220 | 61.3 | 81.4 | 80.6 | 59.8 | 76.9 | 79 | 58.3 | 73 | 77.1 | 34.9 | 97.3 | 33.6 | 94.5 | 32.5 | 92.3 | 77 | 19.9 | 17.3 | 15.3 | 26.3 | 107.7 | 3.3 | 2.9 | 23.9 | 109.8 | 22 | 111.5 | 20.2 | 113.1 | 17.8 | 115.2 | 24.8 | 73.8 | 3.2 | 2.2 | 22.5 | 75.4 | 20.6 | 76.7 | 18.8 | 77.9 | 16.5 | 79.6 | 62.6 | 48.3 | 51.7 | 56 | 59.8 | 66.1 | 73.4 | 77.8 | 76 | 73.1 | 65 | 54.8 | 48.2 | 11.73 | 4.6 | 4.92 | 5.54 | 6.13 | 5.94 | 6.18 | 5.06 | 4.57 | 5.41 | 5.53 | 5.61 | 5.03 | 246 | 86 | 36 | 11 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 94 | 2319 | 517 | 374 | 283 | 180 | 56 | 7 | 0 | 0 | 4 | 68 | 308 | 522 | 4835 | 35 | 82 | 197 | 295 | 500 | 702 | 861 | 807 | 692 | 464 | 163 | 37 | 1430 | 0 | 0 | 4 | 23 | 90 | 259 | 396 | 342 | 247 | 67 | 2 | 0 | 19751 | 2 | 9 | 121 | 461 | 1427 | 3639 | 5265 | 4368 | 3295 | 1094 | 70 | 0 | 10493 | 0 | 1 | 14 | 149 | 587 | 1976 | 3128 | 2465 | 1768 | 399 | 6 | 0 | 5.8 | 3.9 | 5.3 | 6 | 6.6 | 7.3 | 7.2 | 6.9 | 6.4 | 5.5 | 5.1 | 4.2 | 4.7 | 26.3 | 5.7 | 4.6 | 3.5 | 1.3 | 0.6 | 0.1 | 0 | 0.1 | 0.3 | 1.2 | 3.5 | 4.9 | 48.9 | 16.7 | 15.2 | 10.7 | 6.4 | 3.4 | 1.6 | 1.2 | 1.4 | 1.7 | 8.2 | 8.9 | 18.4 | 8.1 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 8.7 | 4.2 | 3.9 | 2.7 | 1.5 | 0.8 | 0.3 | 0.2 | 0.2 | 0.4 | 1.5 | 2.7 | 4.1 | 70.5 | 75.1 | 81.8 | 90.1 | 96.7 | 104.1 | 107.7 | 104.4 | 102 | 94.1 | 80 | 66.2 | 51.4 | 57.6 | 60.8 | 63.5 | 67.1 | 70.3 | 71.2 | 68.4 | 66.2 | 63.3 | 58.9 | 52.1 | 65.6 | 71.2 | 77.4 | 84.2 | 90.7 | 99.8 | 102.1 | 99.7 | 98.6 | 88.5 | 75.4 | 63.1 | 51.7 | 55.2 | 59.5 | 61.3 | 65.2 | 68.6 | 69.6 | 67.6 | 65.9 | 61.6 | 57.7 | 52.2 | 61.6 | 66.3 | 73.1 | 79.5 | 86.9 | 95.3 | 98.9 | 96.7 | 94.5 | 84.1 | 71.1 | 60.5 | 51.1 | 53.2 | 57.5 | 60 | 63.1 | 67.3 | 68.7 | 67.2 | 64.9 | 60 | 55.7 | 51.9 | 58 | 62.9 | 69.6 | 74.4 | 82 | 91 | 94.9 | 92.6 | 90.5 | 80.7 | 66.3 | 57.4 | 50.1 | 52 | 55.5 | 57.8 | 61.6 | 65.4 | 67.5 | 66.2 | 63.8 | 59 | 54 | 51.1 | 58 | 60.4 | 63.3 | 66.9 | 70.3 | 73.4 | 73.4 | 71.4 | 70.2 | 66.5 | 62.5 | 59.4 | 62.5 | 69.2 | 77.4 | 84.6 | 90.7 | 97.7 | 102.5 | 97.5 | 94.5 | 85.7 | 74.6 | 62.3 | 55.4 | 58 | 61 | 63.7 | 67.3 | 70.8 | 71.3 | 69.7 | 67.9 | 64.4 | 60.2 | 57 | 60.7 | 66.2 | 74.5 | 80.5 | 88.3 | 95.6 | 98.4 | 94.4 | 92 | 83 | 69.2 | 59.4 | 53.6 | 55.9 | 58.9 | 61.2 | 64.9 | 68.6 | 69.8 | 68.4 | 66.4 | 62.5 | 58.5 | 54.7 | 57.2 | 63.1 | 70.8 | 76.1 | 83.8 | 91.9 | 95.7 | 92.4 | 90 | 79 | 66.3 | 57.2 | 51.8 | 54 | 56.9 | 59.1 | 62.7 | 66.8 | 68.4 | 67.2 | 65 | 60.8 | 56.7 | 52.9 | 56.4 | 60.2 | 66.5 | 72.7 | 79.7 | 88.7 | 92.9 | 90.4 | 87.7 | 75.7 | 64.1 | 55.5 | 18.3 | 20.2 | 21.5 | 23.4 | 26.4 | 30.1 | 33.1 | 32.7 | 32 | 27.5 | 22.3 | 17.3 | 26.3 | 28.2 | 30 | 32.4 | 34.4 | 37.2 | 37.9 | 37.5 | 38.5 | 35.2 | 29.3 | 22.6 | 15.2 | 15.2 | 15.5 | 15.3 | 14.5 | 13.9 | 13.5 | 13.2 | 14 | 14.4 | 14.5 | 13.4 | 17.9 | 22 | 27.4 | 29.9 | 32.2 | 34.8 | 35.8 | 34.6 | 34.4 | 29.7 | 22.2 | 13 | 12 | 13.1 | 14.9 | 15.2 | 14.9 | 14.2 | 13.6 | 13 | 13.5 | 13.5 | 12.5 | 9.4 | 0.319 | 0.321 | 0.332 | 0.353 | 0.358 | 0.356 | 0.358 | 0.343 | 0.343 | 0.328 | 0.321 | 0.324 | 2.525 | 2.524 | 2.48 | 2.402 | 2.414 | 2.425 | 2.411 | 2.444 | 2.452 | 2.519 | 2.524 | 2.513 | 274 | 289 | 295 | 293 | 292 | 292 | 290 | 293 | 287 | 282 | 271 | 263 | 24 | 28 | 32 | 36 | 37 | 36 | 37 | 35 | 32 | 27 | 24 | 23 | 709 | 1029 | 1462 | 1934 | 2324 | 2583 | 2550 | 2277 | 1865 | 1323 | 866 | 628 | 123 | 133 | 149 | 163 | 138 | 106 | 73 | 70 | 62 | 88 | 61 | 103 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.72 | N/A | -2.03 | N/A | N/A | N/A | N/A | -216 | 245 | 54 | 51
| SACRAMENTO-EXECUTIVE_STYP20 | 12 | 4 | USA | CA | SACRAMENTO EXECUTIVE | 724830 | 23232 | 38.507 | -121.495 | 15 | 14.69 | -8 | NAP | 94-19 | 3A | 12 | 31.5 | 34 | 20.3 | 15.3 | 53.2 | 24.1 | 18.3 | 51.3 | 24.8 | 54.3 | 21.2 | 52 | 1.1 | 330 | 0.463 | 7 | 31.8 | 100.2 | 69.6 | 97 | 68.3 | 93.7 | 67.3 | 72.1 | 95.1 | 70.3 | 92.5 | 68.7 | 90 | 6.9 | 220 | 63.6 | 87.9 | 83.1 | 61.5 | 81.7 | 79.1 | 60.1 | 77.6 | 76.8 | 35.7 | 94.9 | 34.1 | 92.8 | 32.8 | 90 | 81 | 19.9 | 17.5 | 15.3 | 27.6 | 106.1 | 2.8 | 2.5 | 25.6 | 107.9 | 24 | 109.3 | 22.4 | 110.7 | 20.4 | 112.5 | 26.4 | 74.3 | 2.8 | 2.3 | 24.4 | 75.9 | 22.7 | 77.3 | 21.2 | 78.6 | 19.1 | 80.3 | 61.7 | 47.9 | 51.3 | 55.5 | 59.3 | 65.7 | 72 | 75.7 | 75 | 72.1 | 64 | 53.9 | 47.6 | 11.38 | 4.65 | 4.54 | 5.19 | 5.99 | 6.17 | 6.03 | 5.16 | 4.75 | 5.11 | 5.25 | 5.36 | 5.06 | 278 | 95 | 36 | 12 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 109 | 2436 | 530 | 385 | 297 | 190 | 64 | 9 | 0 | 0 | 5 | 81 | 334 | 541 | 4556 | 30 | 71 | 181 | 282 | 488 | 660 | 796 | 777 | 663 | 435 | 140 | 33 | 1238 | 0 | 0 | 1 | 20 | 86 | 219 | 331 | 312 | 218 | 50 | 1 | 0 | 15445 | 0 | 1 | 61 | 364 | 1276 | 2836 | 3973 | 3611 | 2550 | 745 | 28 | 0 | 7894 | 0 | 0 | 3 | 107 | 552 | 1474 | 2238 | 1985 | 1291 | 243 | 1 | 0 | 6 | 4.9 | 5.7 | 6.2 | 6.9 | 7.3 | 7.4 | 7.1 | 6.5 | 5.5 | 5.1 | 4.3 | 5.1 | 19.8 | 3.7 | 3.5 | 2.9 | 1.4 | 0.8 | 0.2 | 0 | 0 | 0.1 | 1.1 | 2 | 4 | 32.8 | 9.5 | 10.9 | 8.7 | 4.4 | 3.7 | 1.5 | 0.2 | 0.5 | 0.5 | 3.9 | 4.6 | 9.8 | 7.8 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0.2 | 0.2 | 5.5 | 2.9 | 2.4 | 2.5 | 1 | 0.9 | 0.4 | 0 | 0.1 | 0.2 | 0.9 | 1.2 | 2.6 | 66 | 71.9 | 79.6 | 88.5 | 96.6 | 103 | 104.2 | 104.1 | 100.2 | 92.3 | 77.7 | 64.6 | 52.3 | 57.3 | 61.3 | 63.6 | 68.1 | 70.8 | 71.6 | 70.2 | 67.6 | 64.7 | 59.6 | 54.8 | 61.8 | 67.4 | 75.2 | 82.9 | 91.2 | 97.9 | 99.9 | 98.9 | 96 | 86.1 | 72.9 | 61.2 | 53 | 55.9 | 59.4 | 61.1 | 66 | 68.9 | 70.3 | 69.2 | 66.5 | 62.4 | 57.9 | 54 | 58.9 | 63.8 | 71.4 | 78.2 | 86.5 | 93.6 | 96.1 | 95.1 | 92.2 | 81.9 | 68.1 | 58.9 | 52.5 | 53.9 | 57.7 | 60.3 | 63.2 | 67 | 68.8 | 67.8 | 65.3 | 60.3 | 56.2 | 52.8 | 56.2 | 60.6 | 67.4 | 73 | 81.4 | 88.6 | 92.2 | 91 | 88 | 77.7 | 64.2 | 56.6 | 51.2 | 52.9 | 55.9 | 57.9 | 61.7 | 65.8 | 68.1 | 66.9 | 64.4 | 59.2 | 54.7 | 51.3 | 58.5 | 60.5 | 63.9 | 67.2 | 70.6 | 73.3 | 75.3 | 75.2 | 71.6 | 67.3 | 62.5 | 59.1 | 60.9 | 66.4 | 75.9 | 81.5 | 91.3 | 97.6 | 98.4 | 97.1 | 92.6 | 85.2 | 73.1 | 62.3 | 55.6 | 58.2 | 61.3 | 63.8 | 67.7 | 70.8 | 72.1 | 71.1 | 68.5 | 64.6 | 60 | 56.8 | 58.7 | 64.3 | 72.5 | 78.8 | 88 | 93.7 | 95.6 | 94.2 | 89.1 | 81.6 | 68.6 | 59.3 | 53.6 | 56.1 | 59.2 | 61.6 | 65.3 | 68.7 | 70.3 | 69.1 | 66.9 | 62.6 | 58.2 | 54.6 | 56.4 | 61.4 | 68.8 | 75.4 | 83.6 | 90 | 92.7 | 91.2 | 87.6 | 77.3 | 65.2 | 57 | 52.1 | 54.1 | 57 | 59.4 | 63 | 66.8 | 68.6 | 67.6 | 65.4 | 60.8 | 56.3 | 52.5 | 55.2 | 58.9 | 65.4 | 70.9 | 78.6 | 86.4 | 89.9 | 88.7 | 85.6 | 73.7 | 62.3 | 55.3 | 15.4 | 17.9 | 20.7 | 23.2 | 26.4 | 29.7 | 31.8 | 31.5 | 30.2 | 26.3 | 20.3 | 16 | 20.6 | 24 | 27.9 | 31.7 | 34.5 | 36.6 | 36.4 | 36.7 | 36.6 | 33.4 | 26.9 | 19.3 | 12.6 | 14 | 14.5 | 14.1 | 13.2 | 13 | 13.1 | 12.6 | 12 | 12.5 | 13.4 | 11.9 | 13.8 | 19.3 | 24.9 | 28.7 | 32.6 | 34.2 | 34.5 | 33.8 | 32.6 | 28.6 | 21.7 | 11.5 | 9.4 | 12.2 | 13.9 | 14.2 | 13.8 | 13.7 | 13.8 | 12.8 | 11.8 | 11.6 | 12.1 | 8.3 | 0.324 | 0.326 | 0.341 | 0.356 | 0.365 | 0.362 | 0.363 | 0.347 | 0.351 | 0.345 | 0.331 | 0.333 | 2.503 | 2.504 | 2.449 | 2.399 | 2.395 | 2.413 | 2.407 | 2.442 | 2.437 | 2.463 | 2.486 | 2.473 | 271 | 286 | 292 | 292 | 290 | 290 | 289 | 292 | 284 | 275 | 266 | 258 | 25 | 28 | 33 | 37 | 37 | 37 | 37 | 35 | 33 | 29 | 25 | 24 | 685 | 1025 | 1464 | 1939 | 2352 | 2618 | 2603 | 2332 | 1892 | 1338 | 857 | 616 | 130 | 128 | 148 | 161 | 138 | 102 | 73 | 73 | 64 | 85 | 60 | 102 | N/A | N/A | N/A | N/A | -0.94 | N/A | N/A | N/A | N/A | N/A | 0.72 | N/A | -1.94 | N/A | N/A | N/A | N/A | -209 | 248 | 76 | 48
| SACRAMENTO-MATHER_STYP20 | 12 | 4 | USA | CA | SACRAMENTO MATHER | 724833 | 23206 | 38.567 | -121.3 | 99 | 14.64 | -8 | NAP | 86-19 | 3A | 12 | 28.2 | 30.9 | 17.8 | 13.5 | 45 | 22.2 | 16.7 | 45.3 | 29.7 | 52.1 | 26.7 | 51 | 2.4 | 110 | 0.458 | 7 | 35.2 | 101.2 | 68.7 | 98.3 | 67.4 | 94.8 | 66.5 | 70.9 | 96.6 | 69.3 | 93.6 | 68 | 91.3 | 5.9 | 260 | 61.4 | 81.5 | 75.7 | 60 | 77.5 | 75.9 | 58.6 | 73.7 | 74.6 | 34.5 | 96.9 | 33.3 | 93.9 | 32.2 | 91.3 | 76.3 | 20.6 | 17 | 13.8 | 24.3 | 107.7 | 4.3 | 2.8 | 21.2 | 109.7 | 18.7 | 111.3 | 16.3 | 112.9 | 13.2 | 114.9 | 22.6 | 74.4 | 3.8 | 1.5 | 19.9 | 75.5 | 17.7 | 76.4 | 15.6 | 77.2 | 12.8 | 78.3 | 60.7 | 45.4 | 50.3 | 54.4 | 58.1 | 64.2 | 70.7 | 76.4 | 74.6 | 71.2 | 64.3 | 52.5 | 45.2 | 12.16 | 4.92 | 5.43 | 5.1 | 6.22 | 7.36 | 6.39 | 5.19 | 5.23 | 5.7 | 6.14 | 5.25 | 5.6 | 448 | 159 | 59 | 17 | 9 | 4 | 0 | 0 | 0 | 0 | 1 | 34 | 165 | 2774 | 608 | 410 | 329 | 219 | 102 | 20 | 0 | 1 | 12 | 85 | 376 | 612 | 4345 | 16 | 69 | 154 | 253 | 444 | 623 | 818 | 763 | 636 | 444 | 108 | 17 | 1197 | 0 | 0 | 0 | 13 | 78 | 192 | 353 | 299 | 199 | 63 | 0 | 0 | 17082 | 0 | 1 | 48 | 373 | 1438 | 2886 | 4707 | 3919 | 2671 | 1026 | 13 | 0 | 9098 | 0 | 0 | 4 | 116 | 632 | 1498 | 2814 | 2239 | 1400 | 395 | 0 | 0 | 5.3 | 4.2 | 5.2 | 6 | 5.8 | 5.9 | 6.3 | 6 | 5.6 | 4.8 | 4.3 | 4.3 | 5.4 | 16.5 | 3.3 | 2.9 | 2.5 | 1.1 | 0.4 | 0.2 | 0 | 0.1 | 0.3 | 0.9 | 2.3 | 2.4 | 33.5 | 9.1 | 8.6 | 7.1 | 4.2 | 2.1 | 1.3 | 0.8 | 0.6 | 2.8 | 6.9 | 7.4 | 6.3 | 6.3 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3 | 2.5 | 2.3 | 1.9 | 1.1 | 0.5 | 0.2 | 0.2 | 0.2 | 0.6 | 1.2 | 2 | 1.7 | 63.8 | 71.7 | 79.2 | 88.4 | 95.3 | 101.8 | 106.9 | 104.4 | 100.7 | 94.8 | 75.7 | 63.9 | 53.3 | 56.6 | 61.6 | 64 | 66.6 | 67.9 | 71.4 | 68.9 | 68.3 | 65 | 59 | 53.3 | 59.6 | 68.2 | 74.3 | 83.6 | 91.3 | 97.4 | 101.7 | 100.1 | 96.6 | 89.2 | 71.4 | 60.6 | 51.1 | 56 | 59.5 | 61.6 | 65.6 | 67.1 | 69.8 | 67.5 | 65.5 | 62.4 | 57.2 | 51.4 | 56.8 | 64.3 | 70.3 | 78 | 87.9 | 93.2 | 98.6 | 96.7 | 92.6 | 84 | 67.9 | 57.2 | 51.1 | 54.1 | 57.6 | 59.2 | 64.3 | 65.7 | 68.4 | 66.7 | 64.4 | 61.1 | 54.9 | 50.8 | 54.3 | 61 | 66.2 | 73.1 | 82.4 | 89.3 | 94.4 | 92.2 | 89.1 | 79.9 | 64 | 54.6 | 49.5 | 52.3 | 56.2 | 57.6 | 61.6 | 64.7 | 67.2 | 65.8 | 63.5 | 59.9 | 53.8 | 49.7 | 56.8 | 60.1 | 64 | 67.7 | 69.4 | 71.5 | 73.3 | 71.8 | 70.7 | 66.2 | 62.2 | 57.4 | 60 | 67.7 | 75.6 | 84.1 | 89.6 | 96.7 | 101.4 | 99.1 | 96.2 | 88.8 | 72.1 | 61.2 | 54.5 | 57.3 | 60.8 | 63.4 | 67.8 | 69.4 | 71.3 | 69.6 | 67.9 | 64.1 | 59.1 | 54.3 | 57.2 | 64.4 | 71.2 | 78.7 | 88.2 | 92.1 | 98.1 | 95.1 | 91 | 84.8 | 66.1 | 56.4 | 52.2 | 55.4 | 59.1 | 60.9 | 65.5 | 67.6 | 69.5 | 68.2 | 65.7 | 62.6 | 57.1 | 52.5 | 55.8 | 61.7 | 68.5 | 74.8 | 84.1 | 89.6 | 95.1 | 92.6 | 88.1 | 80.9 | 63.9 | 55.5 | 50.2 | 53.9 | 57.3 | 58.8 | 63 | 65.9 | 68.1 | 66.7 | 64.2 | 61.1 | 55.4 | 50.4 | 54.1 | 59.5 | 64.7 | 71.1 | 79.3 | 86.5 | 92.2 | 89.6 | 85.8 | 76.7 | 61.4 | 54.7 | 15.7 | 20 | 21.9 | 26.8 | 31.3 | 33.6 | 35.2 | 34.4 | 32.2 | 28.1 | 21.8 | 16.4 | 20.3 | 24.5 | 30.4 | 35.5 | 38.1 | 40.9 | 38.7 | 39.3 | 37.8 | 35.5 | 28 | 20.8 | 13.8 | 14.2 | 17.1 | 16.9 | 15.8 | 16.5 | 13.8 | 13.6 | 14.2 | 14.7 | 15 | 13.2 | 17.3 | 20.5 | 25.4 | 31.7 | 35.5 | 37.5 | 37.1 | 36.3 | 35 | 31.4 | 22.9 | 16 | 12.4 | 12.8 | 14.9 | 16.7 | 15.2 | 15.6 | 14 | 13.3 | 13.7 | 13.6 | 13.2 | 10.9 | 0.324 | 0.326 | 0.347 | 0.356 | 0.369 | 0.364 | 0.364 | 0.348 | 0.355 | 0.351 | 0.333 | 0.336 | 2.501 | 2.504 | 2.43 | 2.402 | 2.384 | 2.409 | 2.41 | 2.445 | 2.431 | 2.443 | 2.477 | 2.454 | 271 | 286 | 290 | 292 | 289 | 289 | 288 | 291 | 283 | 272 | 264 | 256 | 25 | 28 | 33 | 36 | 38 | 37 | 37 | 35 | 33 | 30 | 25 | 24 | 694 | 1017 | 1450 | 1919 | 2336 | 2622 | 2609 | 2340 | 1895 | 1340 | 859 | 619 | 126 | 133 | 157 | 169 | 148 | 108 | 78 | 74 | 67 | 89 | 62 | 103 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.72 | N/A | -1.94 | N/A | N/A | N/A | N/A | -209 | 248 | 76 | 47
| BEALE-AFB_STYP20 | 11 | 4 | USA | CA | BEALE AFB | 724837 | 93216 | 39.133 | -121.433 | 113 | 14.64 | -8 | NAP | 94-19 | 3A | 12 | 31.1 | 33.8 | 20.6 | 15.5 | 48.1 | 24.2 | 18.4 | 47.2 | 29.9 | 53 | 25.9 | 53.8 | 3.6 | 90 | 0.457 | 7 | 31.5 | 101.2 | 70.1 | 98.4 | 69.3 | 95.4 | 68.1 | 73.1 | 95.7 | 71.3 | 93.3 | 69.9 | 91.4 | 7 | 200 | 65 | 92.9 | 82.8 | 63.3 | 87.3 | 80 | 61.4 | 81.8 | 78.7 | 36.6 | 95.6 | 35.1 | 93.8 | 33.8 | 91.4 | 79.5 | 23.5 | 19.5 | 17 | 25.9 | 105.8 | 3.6 | 1.5 | 23.4 | 106.9 | 21.3 | 107.7 | 19.3 | 108.6 | 16.7 | 109.7 | 25.3 | 76.2 | 3.6 | 2.1 | 22.7 | 77.7 | 20.6 | 78.9 | 18.6 | 80.1 | 15.9 | 81.6 | 62.6 | 48 | 51.4 | 55.3 | 59.9 | 66.5 | 74 | 78.6 | 77.3 | 73.7 | 64 | 54.2 | 47 | 12.3 | 4.84 | 4.85 | 5.1 | 6.05 | 6.49 | 6.61 | 4.67 | 4.69 | 5.44 | 5.05 | 5.56 | 5.36 | 294 | 94 | 38 | 12 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 125 | 2413 | 526 | 380 | 302 | 174 | 57 | 7 | 0 | 0 | 5 | 78 | 325 | 559 | 4877 | 33 | 78 | 176 | 301 | 511 | 720 | 887 | 847 | 712 | 435 | 147 | 30 | 1523 | 0 | 0 | 2 | 21 | 103 | 278 | 422 | 382 | 266 | 48 | 1 | 0 | 20536 | 0 | 1 | 56 | 434 | 1481 | 3789 | 5646 | 4972 | 3331 | 795 | 31 | 0 | 10742 | 0 | 0 | 5 | 115 | 610 | 2046 | 3259 | 2772 | 1691 | 242 | 2 | 0 | 6.8 | 6.5 | 7.5 | 7.7 | 7.6 | 7.6 | 7.3 | 6.7 | 6.2 | 6.1 | 6 | 5.9 | 6.7 | 26.9 | 5.3 | 4.5 | 4.2 | 1.8 | 1.3 | 0.4 | 0 | 0.1 | 0.2 | 1.3 | 2.3 | 5.4 | 44 | 14.2 | 12.2 | 13.4 | 6.2 | 4.7 | 1.6 | 0.2 | 0.9 | 0.7 | 4.1 | 5.6 | 12.2 | 8.9 | 0.5 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 8 | 3.6 | 3.2 | 3.7 | 1.5 | 1.3 | 0.5 | 0 | 0.2 | 0.2 | 1.1 | 1.6 | 3.5 | 66.5 | 71.9 | 80.3 | 88.1 | 96.8 | 104.3 | 104.3 | 104.1 | 100.6 | 91.5 | 77.5 | 64.2 | 52.8 | 57.8 | 61.6 | 63.8 | 69.4 | 71.8 | 71.3 | 70 | 70 | 63.8 | 59.3 | 53.8 | 62.1 | 68 | 74.8 | 83.4 | 91 | 99.8 | 100.8 | 99.9 | 96.5 | 86.1 | 73.4 | 61 | 53 | 56.7 | 59.2 | 63 | 65.5 | 70 | 70 | 69.6 | 67.2 | 62.4 | 58 | 53.3 | 59.3 | 64.1 | 71.3 | 79.4 | 87.1 | 95.5 | 98 | 96.5 | 93.3 | 82 | 69.3 | 58.6 | 53.1 | 54.7 | 57.6 | 61.1 | 64.6 | 67.8 | 69.4 | 68.3 | 66.3 | 60.4 | 56.2 | 52.6 | 56.9 | 61.1 | 67.5 | 74.8 | 82.2 | 91.2 | 94.8 | 93.3 | 90.1 | 78.6 | 64.6 | 56.1 | 51.9 | 53.7 | 55.9 | 59.4 | 62.8 | 66.4 | 68.9 | 67.5 | 65.3 | 59.2 | 55 | 51.1 | 59.2 | 61.1 | 63.8 | 68.1 | 71.9 | 75.4 | 75.6 | 73.5 | 72.4 | 67 | 62.6 | 59.2 | 60.3 | 67.2 | 74.5 | 82.2 | 90.5 | 98.3 | 97.4 | 98.5 | 95.7 | 83.7 | 69.9 | 60.6 | 56.5 | 58.9 | 61.1 | 64.4 | 68.8 | 72.5 | 73.2 | 71.5 | 69.7 | 64.4 | 60.5 | 56.8 | 59.3 | 64.2 | 71.2 | 79.4 | 86.8 | 93.8 | 96 | 95.2 | 90.7 | 80.3 | 68.2 | 58.6 | 54.5 | 57 | 59.1 | 62.3 | 66.2 | 70.3 | 71.4 | 70 | 68 | 62.7 | 58.8 | 54.6 | 57 | 62 | 67.9 | 76.3 | 83.6 | 90.8 | 93.3 | 92.7 | 89.2 | 76.9 | 65.7 | 56.6 | 52.9 | 55.1 | 57.2 | 60.4 | 63.9 | 68.2 | 69.8 | 68.5 | 66.3 | 61.1 | 56.9 | 52.7 | 55.4 | 59.6 | 65 | 72.6 | 79.5 | 88.2 | 91.7 | 90.4 | 86.9 | 74 | 63.1 | 54.7 | 15.6 | 17.9 | 20.6 | 24.3 | 25.9 | 29.4 | 31.5 | 31.2 | 29.6 | 26.6 | 20.1 | 16.1 | 20.5 | 23.8 | 28.4 | 32.3 | 32.8 | 34.5 | 34.2 | 34.2 | 34.5 | 32.8 | 27.2 | 19.3 | 13.1 | 14.1 | 15.2 | 15.1 | 13 | 12.7 | 13.6 | 13.8 | 13.7 | 14.2 | 13.7 | 12 | 13.4 | 19.2 | 24.2 | 28.9 | 30.2 | 32.3 | 32 | 32.3 | 31.5 | 27.1 | 20.6 | 11.8 | 9.9 | 12.3 | 14.2 | 14.9 | 13.2 | 12.2 | 13.6 | 13.6 | 13.1 | 12.5 | 11.6 | 8.9 | 0.323 | 0.326 | 0.35 | 0.358 | 0.371 | 0.363 | 0.361 | 0.345 | 0.353 | 0.345 | 0.324 | 0.335 | 2.505 | 2.505 | 2.429 | 2.401 | 2.391 | 2.421 | 2.415 | 2.454 | 2.44 | 2.462 | 2.51 | 2.454 | 270 | 285 | 288 | 291 | 288 | 289 | 289 | 292 | 283 | 274 | 267 | 254 | 25 | 28 | 33 | 36 | 38 | 36 | 36 | 34 | 33 | 29 | 24 | 24 | 679 | 987 | 1407 | 1885 | 2314 | 2612 | 2616 | 2336 | 1880 | 1307 | 821 | 595 | 123 | 134 | 164 | 178 | 154 | 114 | 81 | 78 | 70 | 96 | 68 | 103 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.74 | N/A | -2.03 | N/A | N/A | N/A | N/A | -193 | 247 | 79 | 41
| YUBA-COUNTY-AP_STYP20 | 11 | 4 | USA | CA | YUBA COUNTY AP | 724838 | 93205 | 39.102 | -121.568 | 62 | 14.66 | -8 | NAP | 00-19 | 3A | 1 | 30.2 | 33.3 | 19.1 | 14.4 | 51.5 | 22.9 | 17.3 | 50.1 | 27.8 | 51.2 | 24.4 | 52.8 | 1.7 | 340 | 0.471 | 7 | 33.3 | 101.8 | 69.6 | 99.1 | 69.1 | 96.5 | 68 | 72.5 | 96 | 70.9 | 94.1 | 69.4 | 92.3 | 6.8 | 210 | 63.7 | 88.6 | 83.4 | 62.3 | 84 | 81.5 | 60.7 | 79.5 | 79.7 | 36.1 | 96.1 | 34.6 | 94.3 | 33.5 | 92.6 | 85.3 | 22.4 | 18.9 | 16.7 | 25.8 | 107.4 | 3.1 | 2 | 23.5 | 108.9 | 21.7 | 110.1 | 20 | 111.2 | 17.8 | 112.7 | 24.6 | 75.7 | 3.1 | 2.8 | 22.4 | 77.7 | 20.6 | 79.4 | 18.8 | 80.9 | 16.6 | 83 | 62.4 | 47.3 | 50.8 | 55.5 | 59.4 | 67.4 | 74.6 | 78.8 | 76.9 | 72.8 | 63.9 | 53.3 | 47.1 | 12.42 | 4.63 | 4.64 | 5.42 | 6.28 | 6.21 | 6.23 | 4.85 | 4.22 | 5.36 | 5.43 | 5.68 | 5.09 | 316 | 109 | 42 | 12 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 119 | 2481 | 550 | 397 | 297 | 189 | 44 | 6 | 0 | 0 | 6 | 84 | 353 | 555 | 4838 | 24 | 66 | 182 | 286 | 539 | 739 | 894 | 834 | 683 | 432 | 130 | 29 | 1525 | 0 | 0 | 3 | 22 | 117 | 295 | 429 | 369 | 238 | 51 | 1 | 0 | 20920 | 0 | 1 | 86 | 440 | 1790 | 4058 | 5812 | 4764 | 3079 | 862 | 28 | 0 | 11378 | 0 | 0 | 6 | 136 | 789 | 2269 | 3512 | 2756 | 1629 | 280 | 1 | 0 | 6.6 | 5.6 | 7 | 7.4 | 7.5 | 7.8 | 7.5 | 6.8 | 6.3 | 5.8 | 5.8 | 5.3 | 6.3 | 21.2 | 4.3 | 3.5 | 3.2 | 1.6 | 0.7 | 0.2 | 0 | 0.1 | 0.3 | 1.3 | 3.1 | 3.7 | 46.3 | 12 | 9.5 | 11.2 | 4.7 | 3.8 | 1.7 | 1.7 | 1 | 1.9 | 9.3 | 7.4 | 14.1 | 7.4 | 0.5 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.2 | 2.8 | 2.7 | 2.4 | 1.3 | 0.9 | 0.4 | 0.2 | 0.2 | 0.4 | 1.6 | 2 | 2.7 | 68.1 | 72.4 | 80.9 | 89.2 | 97.5 | 105.1 | 106.2 | 104 | 100.9 | 92.7 | 77.4 | 64 | 50.8 | 57.1 | 61 | 64.2 | 68.2 | 70.9 | 71.6 | 68.7 | 67 | 64.1 | 59.4 | 53.7 | 62.8 | 68.2 | 76.3 | 83.9 | 92.6 | 100.2 | 102 | 99.7 | 97.2 | 86.6 | 73.1 | 61.1 | 51.5 | 55.5 | 59.3 | 62.1 | 66.2 | 69.3 | 70.4 | 69.2 | 66.5 | 61.9 | 57.5 | 52.9 | 59 | 64.2 | 72.4 | 79.3 | 88.8 | 96.6 | 99.1 | 96.9 | 93.4 | 82.4 | 68.7 | 58.7 | 51.3 | 52.9 | 57.4 | 60.3 | 63.7 | 67.5 | 69.8 | 68.3 | 65.9 | 60.3 | 55.2 | 52.1 | 55.9 | 61.2 | 68.1 | 73.8 | 84 | 92.3 | 96 | 93.3 | 90.1 | 79 | 64.2 | 56.2 | 50.3 | 52.2 | 55.5 | 58.2 | 62.5 | 66.1 | 68.8 | 67.3 | 64.9 | 59.2 | 54.2 | 50.8 | 57.1 | 59.8 | 63.3 | 67 | 71 | 74.1 | 75.4 | 72.9 | 71.2 | 66.8 | 62.1 | 58.8 | 61.2 | 67.2 | 77 | 84.3 | 90.7 | 97 | 99.2 | 96.8 | 93.2 | 85.4 | 72.6 | 61.8 | 54.4 | 57.4 | 60.9 | 63.9 | 68.1 | 71.4 | 73.1 | 71.1 | 68.9 | 64.4 | 59.7 | 56.2 | 57.9 | 64.6 | 73.1 | 80.3 | 88.8 | 94.3 | 97.2 | 94.8 | 91.8 | 82.1 | 68.3 | 58.8 | 53 | 55.4 | 59 | 61.7 | 65.9 | 69.4 | 71.3 | 69.5 | 67.3 | 62.5 | 57.7 | 54.1 | 56.4 | 62.1 | 69.4 | 76.3 | 84.8 | 92 | 95 | 92.9 | 89.7 | 78.2 | 64.8 | 56.4 | 51.2 | 53.5 | 56.9 | 59.4 | 63.8 | 67.7 | 69.7 | 68.3 | 65.7 | 60.6 | 56 | 52.4 | 55.3 | 58.8 | 65.8 | 71.9 | 81.2 | 89.2 | 92.8 | 90.8 | 87.1 | 74.4 | 62.3 | 54.7 | 17 | 19.3 | 21.3 | 24.2 | 28 | 31.2 | 33.3 | 33.3 | 31.9 | 27.5 | 21.2 | 16.4 | 24.4 | 26.1 | 29.3 | 33 | 34.9 | 36.1 | 35.9 | 36.7 | 37.5 | 34.4 | 28 | 20 | 14.8 | 14.9 | 15 | 14.6 | 13 | 12.1 | 12.7 | 13.5 | 13.9 | 14.1 | 14.2 | 12.3 | 16.6 | 21.4 | 25.7 | 30.3 | 33 | 34 | 33.9 | 34 | 34.4 | 29.5 | 22.6 | 11.2 | 11.3 | 13.1 | 14 | 14.3 | 13.4 | 12.7 | 13.5 | 13.4 | 13.6 | 12.7 | 12.8 | 8.2 | 0.322 | 0.325 | 0.342 | 0.355 | 0.365 | 0.359 | 0.358 | 0.342 | 0.348 | 0.34 | 0.322 | 0.33 | 2.511 | 2.51 | 2.456 | 2.409 | 2.41 | 2.431 | 2.416 | 2.457 | 2.449 | 2.476 | 2.517 | 2.48 | 271 | 286 | 291 | 292 | 290 | 291 | 290 | 293 | 285 | 276 | 268 | 257 | 24 | 28 | 32 | 36 | 37 | 36 | 36 | 34 | 32 | 28 | 24 | 24 | 677 | 989 | 1412 | 1891 | 2319 | 2609 | 2613 | 2332 | 1879 | 1307 | 822 | 595 | 124 | 134 | 162 | 176 | 150 | 112 | 78 | 77 | 69 | 95 | 68 | 103 | 0.7 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.74 | N/A | -2.03 | N/A | N/A | N/A | N/A | -198 | 250 | 81 | 43
| SACRAMENTO-INTL_STYP20 | 12 | 4 | USA | CA | SACRAMENTO INTL | 724839 | 93225 | 38.696 | -121.59 | 23 | 14.68 | -8 | NAP | 94-19 | 3A | 12 | 30.8 | 33.6 | 20.7 | 15.5 | 50.8 | 24.8 | 18.9 | 50.8 | 29.5 | 54.3 | 26.5 | 54.2 | 3 | 320 | 0.494 | 7 | 32.6 | 100.3 | 70.1 | 97.5 | 69.1 | 94.6 | 67.8 | 72.6 | 95.7 | 71 | 93.4 | 69.4 | 90.9 | 6.9 | 200 | 63.8 | 88.8 | 84.1 | 62.4 | 84.5 | 82.3 | 60.8 | 79.8 | 79.8 | 36.2 | 95.4 | 34.6 | 93.7 | 33.4 | 91 | 80.1 | 23.8 | 19.7 | 17.3 | 26.8 | 105.9 | 3.5 | 2.2 | 24.3 | 107.5 | 22.3 | 108.8 | 20.3 | 110 | 17.8 | 111.6 | 25.8 | 75.5 | 3.7 | 2.4 | 23.1 | 77.2 | 20.9 | 78.6 | 18.8 | 79.9 | 16.1 | 81.7 | 61.9 | 47.5 | 50.8 | 55.3 | 59.4 | 66.5 | 73.1 | 76.8 | 75.8 | 72.4 | 63.9 | 53.6 | 47.3 | 11.84 | 4.74 | 4.61 | 5.21 | 6.01 | 6.28 | 5.95 | 4.91 | 4.61 | 5.09 | 5.36 | 5.57 | 5.38 | 309 | 105 | 42 | 13 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 119 | 2475 | 541 | 398 | 304 | 187 | 56 | 6 | 0 | 0 | 6 | 85 | 342 | 550 | 4657 | 28 | 64 | 175 | 285 | 511 | 693 | 830 | 800 | 671 | 431 | 135 | 34 | 1348 | 0 | 0 | 1 | 18 | 102 | 249 | 365 | 335 | 227 | 50 | 1 | 0 | 17645 | 0 | 0 | 63 | 406 | 1520 | 3280 | 4557 | 4080 | 2854 | 854 | 31 | 0 | 9195 | 0 | 0 | 4 | 118 | 661 | 1737 | 2630 | 2295 | 1461 | 288 | 1 | 0 | 7.5 | 6.5 | 7.6 | 7.7 | 8.2 | 8.6 | 8.7 | 8.6 | 8.1 | 7 | 6.7 | 6 | 6.9 | 17.6 | 2.9 | 2.9 | 2.4 | 1.3 | 0.6 | 0.2 | 0 | 0 | 0.1 | 0.9 | 1.7 | 3.9 | 24.4 | 8.7 | 6.2 | 7.4 | 3.7 | 1.6 | 1.4 | 0 | 0.7 | 0.6 | 3.5 | 3.9 | 9.4 | 6.2 | 0 | 0.1 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 2.2 | 1.8 | 2 | 1 | 0.5 | 0.4 | 0 | 0.2 | 0.2 | 1.1 | 0.9 | 2.8 | 66.1 | 71.4 | 79.7 | 89 | 97.1 | 103.1 | 104.7 | 103.7 | 99.7 | 93 | 78 | 65.1 | 53.1 | 57.3 | 62.1 | 63.5 | 68.5 | 71 | 72.2 | 70 | 68.2 | 64.5 | 59.5 | 55.5 | 61.9 | 66.8 | 75.1 | 83.3 | 91.9 | 98.8 | 100.3 | 99.4 | 96.3 | 86.8 | 73.1 | 61.5 | 53.4 | 56.5 | 59.6 | 61.1 | 65.7 | 69.7 | 70.8 | 69.8 | 66.9 | 62.5 | 58.2 | 54.4 | 58.8 | 63.3 | 71.8 | 78.9 | 87.8 | 94.3 | 97.1 | 95.7 | 92.6 | 82.5 | 68.7 | 59 | 52.5 | 54.5 | 58 | 60 | 63.8 | 67.5 | 69.7 | 68.4 | 66 | 60.7 | 56.1 | 52.9 | 56 | 60.3 | 67.5 | 73.6 | 82.4 | 90.1 | 93.3 | 91.9 | 89.3 | 78.8 | 64.2 | 56.6 | 51.2 | 53.3 | 56.1 | 58.1 | 62.2 | 66.4 | 68.6 | 67.3 | 65 | 59.3 | 55 | 51.5 | 59 | 60.8 | 64.9 | 66.5 | 70.9 | 74 | 75.4 | 74.1 | 71.8 | 67.8 | 63.1 | 59.6 | 62.1 | 66.5 | 75.7 | 82.9 | 90.2 | 97 | 99.4 | 98.3 | 94.1 | 86.9 | 74.1 | 62.6 | 55.9 | 58.6 | 61.7 | 63.6 | 68 | 71.4 | 73 | 71.3 | 69 | 64.8 | 60.4 | 57 | 59.2 | 64.3 | 72 | 78.8 | 88.3 | 94.1 | 96.1 | 95.4 | 90.7 | 81.8 | 68.8 | 59.9 | 53.7 | 56.3 | 59.4 | 61.5 | 65.8 | 69.4 | 71.2 | 69.6 | 67.4 | 62.7 | 58.5 | 54.8 | 56.4 | 61.4 | 68.7 | 75.5 | 84.8 | 90.4 | 93.6 | 92 | 88.7 | 78.1 | 65.4 | 57.2 | 52.1 | 54.3 | 57.3 | 59.6 | 63.5 | 67.6 | 69.5 | 68.3 | 65.9 | 60.9 | 56.6 | 52.6 | 55.2 | 58.7 | 65.3 | 72 | 80.4 | 87.8 | 90.8 | 89.7 | 86.3 | 74.8 | 62.7 | 55.2 | 15.6 | 17.8 | 21.3 | 24.3 | 27.1 | 30.3 | 32.6 | 32.5 | 31.3 | 27.9 | 20.7 | 16 | 21.6 | 23.7 | 29.2 | 33.1 | 34.9 | 36.1 | 36.1 | 36.8 | 36.8 | 34.9 | 27.9 | 19.1 | 13.8 | 14.5 | 15.8 | 15.1 | 13.7 | 13.3 | 13.7 | 13.2 | 13.4 | 14.7 | 14.6 | 12.1 | 14.1 | 19.4 | 25.7 | 29.7 | 32.7 | 33.9 | 34.5 | 34.4 | 33.8 | 30.3 | 22 | 11.1 | 10.2 | 12.7 | 14.9 | 14.7 | 14.1 | 13.8 | 14.2 | 13.1 | 13.2 | 13.7 | 13 | 8.2 | 0.322 | 0.325 | 0.338 | 0.354 | 0.364 | 0.36 | 0.361 | 0.344 | 0.349 | 0.343 | 0.327 | 0.331 | 2.511 | 2.509 | 2.461 | 2.405 | 2.402 | 2.42 | 2.406 | 2.446 | 2.442 | 2.468 | 2.5 | 2.479 | 272 | 287 | 293 | 293 | 290 | 290 | 289 | 292 | 285 | 275 | 267 | 258 | 25 | 28 | 32 | 36 | 37 | 36 | 37 | 35 | 33 | 29 | 25 | 24 | 685 | 1014 | 1446 | 1923 | 2339 | 2611 | 2602 | 2327 | 1885 | 1326 | 846 | 610 | 128 | 131 | 153 | 166 | 141 | 106 | 75 | 74 | 65 | 89 | 62 | 103 | N/A | N/A | -2.09 | N/A | -1.03 | -1.15 | N/A | N/A | N/A | N/A | 0.72 | N/A | -1.94 | N/A | N/A | N/A | N/A | -209 | 248 | 76 | 47
| MONTEREY_STYP20 | 3 | 4 | USA | CA | MONTEREY | 724915 | 23259 | 36.588 | -121.845 | 165 | 14.61 | -8 | NAP | 98-19 | 3C | 12 | 36.8 | 38.9 | 21 | 15.9 | 48.7 | 25.1 | 19.3 | 49.3 | 20.5 | 54.7 | 17.9 | 55.7 | 4.9 | 100 | 0.473 | 9 | 14.1 | 79.2 | 60 | 74.5 | 59.4 | 71.6 | 59.2 | 63.4 | 72.5 | 62.2 | 70.6 | 61.2 | 68.8 | 5.7 | 310 | 60.3 | 78.6 | 65.8 | 58.7 | 74.2 | 64.7 | 57.4 | 70.8 | 63.7 | 28.8 | 72.2 | 27.9 | 70.5 | 27.1 | 68.8 | 82.2 | 16.9 | 14.8 | 12.6 | 32.7 | 90 | 2.3 | 5.1 | 31 | 93.7 | 29.7 | 96.6 | 28.4 | 99.5 | 26.8 | 103.2 | 29.4 | 67.4 | 2.4 | 4.4 | 27.6 | 70.6 | 26.2 | 73.2 | 24.8 | 75.7 | 23.1 | 78.9 | 56.7 | 52.1 | 52.7 | 53.7 | 54.7 | 56.8 | 59.4 | 60.6 | 61.5 | 61.8 | 59.5 | 55.2 | 51.6 | 5.43 | 4.64 | 4.57 | 4.05 | 4.09 | 3.39 | 3.35 | 2.88 | 3.05 | 4.2 | 4.71 | 4.43 | 4.42 | 103 | 31 | 20 | 9 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 34 | 3113 | 402 | 346 | 351 | 314 | 257 | 175 | 139 | 116 | 117 | 185 | 296 | 415 | 2530 | 94 | 95 | 124 | 143 | 211 | 281 | 330 | 357 | 353 | 296 | 163 | 83 | 64 | 0 | 0 | 1 | 4 | 4 | 5 | 4 | 9 | 20 | 15 | 2 | 0 | 462 | 7 | 8 | 10 | 43 | 34 | 53 | 11 | 31 | 122 | 120 | 23 | 0 | 126 | 1 | 1 | 1 | 12 | 11 | 20 | 0 | 4 | 39 | 33 | 4 | 0 | 5.8 | 4.9 | 5.7 | 6 | 6.8 | 7 | 6.9 | 6.4 | 5.9 | 5.1 | 4.8 | 4.7 | 5.1 | 17.9 | 3.6 | 3.5 | 2.7 | 1.3 | 0.5 | 0.2 | 0 | 0 | 0 | 0.9 | 1.8 | 3.3 | 35.8 | 11.8 | 14.1 | 8.4 | 3.8 | 2.4 | 1.1 | 0.1 | 0.2 | 0.4 | 3.5 | 6.4 | 8.5 | 7.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 3.1 | 2.8 | 2.3 | 1.1 | 0.6 | 0.2 | 0 | 0 | 0.1 | 1.1 | 1.5 | 2.2 | 73.7 | 74.5 | 74.1 | 80.1 | 78.6 | 81.1 | 75.2 | 78 | 85.2 | 84.1 | 77.2 | 69.5 | 54.3 | 57 | 56.5 | 59 | 58.9 | 60.9 | 62.7 | 62.9 | 63.7 | 60.2 | 58.3 | 53.5 | 67 | 67.9 | 67.3 | 69.7 | 69.2 | 72.3 | 71.5 | 72.5 | 76.5 | 76.6 | 69.9 | 64.5 | 52.7 | 55.2 | 55.3 | 56.4 | 57.6 | 60.2 | 61.2 | 61.6 | 61.4 | 58.3 | 56 | 54.5 | 63.1 | 63.6 | 63.7 | 64.2 | 65.2 | 68.3 | 68.5 | 69.8 | 72.2 | 71 | 65.8 | 62.2 | 53.4 | 54.1 | 54.7 | 54.9 | 56.3 | 58.9 | 60.1 | 60.9 | 60.6 | 57.9 | 55.5 | 54.5 | 59.8 | 60.5 | 61.1 | 61.4 | 63 | 65.5 | 65.9 | 67.1 | 69.3 | 67.3 | 63.1 | 59.7 | 53.1 | 53.4 | 54 | 53.6 | 55.5 | 57.5 | 58.9 | 59.9 | 60 | 57.2 | 55.3 | 53.2 | 58.7 | 60.3 | 60 | 60.8 | 61.9 | 63.8 | 63.8 | 64.5 | 66.2 | 63.7 | 61.9 | 60.1 | 62.9 | 66.2 | 69.1 | 74.4 | 72.5 | 76.5 | 73.2 | 73.3 | 77.6 | 73 | 67.5 | 63.5 | 57 | 57.8 | 57.9 | 57.8 | 59 | 61.1 | 61.9 | 62.7 | 63.4 | 61.9 | 59.5 | 58.1 | 61.3 | 64.1 | 64.2 | 66.4 | 66.6 | 70.1 | 70 | 70.3 | 72.6 | 70 | 65.6 | 61.7 | 55.3 | 55.9 | 56.3 | 56.1 | 57.2 | 59.4 | 60.5 | 61.4 | 62 | 60.2 | 57.9 | 56.4 | 60.2 | 61.6 | 61.9 | 63.1 | 64.1 | 66.9 | 67.1 | 68.7 | 70.3 | 67.8 | 63.7 | 60 | 53.7 | 54.2 | 54.6 | 54.4 | 55.8 | 58.1 | 59.3 | 60.2 | 60.5 | 58.7 | 56.4 | 54.5 | 58.8 | 59.3 | 59.8 | 60.5 | 62.1 | 64.6 | 64.9 | 66.3 | 67.8 | 65.8 | 61.7 | 58.2 | 16.3 | 14.8 | 14.3 | 13.3 | 12.3 | 12.9 | 11.8 | 11.9 | 14.1 | 16 | 16.2 | 15.8 | 21.9 | 21 | 19.6 | 19.5 | 17.8 | 18.8 | 15.4 | 15.5 | 20.8 | 23.6 | 21.3 | 19 | 13.1 | 12.2 | 11.4 | 10.9 | 9.4 | 9.5 | 7.4 | 7.8 | 10.6 | 12.9 | 12.4 | 11.7 | 16.5 | 17.1 | 16.8 | 17.1 | 16.3 | 17.2 | 14.7 | 14.6 | 18.3 | 18.8 | 16.8 | 13.4 | 10.8 | 10.7 | 10.5 | 10.1 | 9.1 | 9 | 7.1 | 7.5 | 9.5 | 11.1 | 10.8 | 9.5 | 0.317 | 0.321 | 0.326 | 0.349 | 0.359 | 0.349 | 0.353 | 0.336 | 0.345 | 0.323 | 0.31 | 0.314 | 2.567 | 2.562 | 2.545 | 2.461 | 2.447 | 2.487 | 2.496 | 2.536 | 2.504 | 2.591 | 2.593 | 2.587 | 280 | 292 | 299 | 296 | 292 | 294 | 292 | 296 | 289 | 287 | 281 | 274 | 24 | 27 | 30 | 35 | 36 | 35 | 34 | 32 | 31 | 26 | 23 | 23 | 836 | 1109 | 1558 | 1967 | 2245 | 2422 | 2234 | 2018 | 1761 | 1333 | 958 | 735 | 89 | 119 | 124 | 164 | 136 | 106 | 75 | 93 | 74 | 80 | 51 | 90 | 0.86 | N/A | -2.84 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.72 | N/A | -2.18 | N/A | N/A | N/A | N/A | -223 | 263 | 63 | 37
| STOCKTON_STYP20 | 12 | 4 | USA | CA | STOCKTON | 724920 | 23237 | 37.889 | -121.226 | 26 | 14.68 | -8 | NAP | 94-19 | 3A | 12 | 30.7 | 33.1 | 21.8 | 16.4 | 51 | 25.3 | 19.3 | 48.8 | 26.6 | 54.6 | 24.1 | 53.3 | 2.9 | 130 | 0.495 | 7 | 32.8 | 101.5 | 69.7 | 98.3 | 68.8 | 95.3 | 68 | 73.1 | 96 | 70.8 | 94.2 | 69.1 | 91.9 | 10 | 310 | 64.5 | 91 | 84.5 | 61.7 | 82.2 | 80 | 59.9 | 77.2 | 77.7 | 36.6 | 96 | 34.5 | 94.5 | 33.1 | 92 | 88.9 | 22.6 | 19.3 | 17.2 | 26.8 | 107 | 3.2 | 2.5 | 24.5 | 108.8 | 22.6 | 110.3 | 20.8 | 111.7 | 18.4 | 113.5 | 25.5 | 76.4 | 3.5 | 5.5 | 23 | 80.4 | 20.9 | 83.6 | 19 | 86.7 | 16.5 | 90.7 | 62.4 | 47.7 | 51.3 | 55.7 | 60 | 66.7 | 73.4 | 77.4 | 76.4 | 73 | 64.5 | 54.2 | 47.5 | 11.9 | 4.9 | 4.55 | 5.13 | 5.89 | 6.07 | 6.02 | 5.13 | 4.63 | 5.07 | 5.15 | 5.45 | 5.28 | 286 | 102 | 36 | 10 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 114 | 2377 | 535 | 385 | 288 | 170 | 50 | 5 | 0 | 0 | 3 | 71 | 326 | 544 | 4802 | 32 | 71 | 188 | 302 | 518 | 701 | 850 | 820 | 690 | 449 | 146 | 35 | 1419 | 0 | 0 | 1 | 20 | 103 | 256 | 385 | 355 | 244 | 54 | 1 | 0 | 19026 | 0 | 1 | 77 | 459 | 1586 | 3474 | 5061 | 4452 | 3008 | 871 | 37 | 0 | 9999 | 0 | 0 | 6 | 140 | 703 | 1881 | 2955 | 2497 | 1532 | 284 | 1 | 0 | 7.5 | 6.1 | 7 | 7.3 | 8.6 | 9.5 | 9.6 | 8.5 | 8 | 7.2 | 6.1 | 5.4 | 6.4 | 14 | 2.8 | 2.4 | 2 | 1 | 0.4 | 0.1 | 0 | 0 | 0.3 | 0.7 | 2 | 2 | 26.7 | 7 | 8.2 | 6.5 | 3.1 | 3.7 | 0.7 | 0.6 | 0.8 | 2.5 | 2.7 | 6.2 | 5.3 | 5.6 | 0.2 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4 | 2 | 1.9 | 1.5 | 0.8 | 0.7 | 0.1 | 0.1 | 0.2 | 0.6 | 0.7 | 1.6 | 1.4 | 66.1 | 72.2 | 80.2 | 90.3 | 98.2 | 104 | 105.5 | 103.8 | 100.4 | 92.7 | 78.2 | 65.2 | 54.9 | 58 | 62 | 65 | 68.3 | 70.7 | 71.9 | 70.6 | 69.1 | 65.5 | 60 | 56.4 | 62.4 | 67.7 | 76 | 83.9 | 92.4 | 99.5 | 101.5 | 99.8 | 96.6 | 86.8 | 73.9 | 61.9 | 54.1 | 56.5 | 59.9 | 62.4 | 66 | 69.3 | 70 | 69.2 | 68.4 | 63.4 | 58.6 | 54.4 | 59.3 | 64.3 | 72.5 | 79.5 | 87.9 | 95.1 | 97.8 | 96.4 | 93.1 | 82.7 | 69.5 | 59.2 | 52.9 | 54.5 | 58 | 60.3 | 63.7 | 67.1 | 69.2 | 68.2 | 66.8 | 61.1 | 57.1 | 53.3 | 56.6 | 61.1 | 68.5 | 74.9 | 83 | 90.7 | 94.4 | 92.7 | 89.3 | 78.8 | 65.4 | 56.8 | 51.6 | 53.5 | 56.5 | 58.5 | 62 | 65.7 | 68.6 | 67.3 | 65.4 | 60.1 | 54.9 | 51.7 | 59.1 | 61 | 64.4 | 67.3 | 71.7 | 73.6 | 78.8 | 75.2 | 78.4 | 67.8 | 63.3 | 59.8 | 62.6 | 67.5 | 76.5 | 83.2 | 90.7 | 100.2 | 95.9 | 97.1 | 92.3 | 86.9 | 74 | 63.3 | 56.1 | 58.6 | 61.7 | 64.1 | 67.6 | 70.7 | 73 | 71.5 | 70.7 | 65.2 | 60.5 | 57.1 | 59.5 | 64.9 | 73.1 | 80.4 | 89.3 | 95.3 | 96.5 | 95.7 | 90.4 | 83 | 70.1 | 59.9 | 54 | 56.5 | 59.5 | 61.8 | 65.2 | 68.7 | 70.6 | 69.4 | 68 | 63.3 | 58.6 | 54.8 | 57.3 | 62.3 | 69.6 | 76.9 | 85.4 | 91.7 | 94.7 | 92.4 | 88.5 | 79.1 | 66.5 | 57.3 | 52.3 | 54.5 | 57.4 | 59.5 | 63 | 66.8 | 68.9 | 67.9 | 66.2 | 61.4 | 56.8 | 52.6 | 55.6 | 59.8 | 66.5 | 72.2 | 80.8 | 88.4 | 92.4 | 90.2 | 86.7 | 75.6 | 63.6 | 55.6 | 16.1 | 19.4 | 22.7 | 25.1 | 28 | 31.1 | 32.8 | 32.2 | 30.9 | 27.6 | 21.7 | 16.9 | 21.3 | 25.1 | 29.3 | 33.7 | 35.8 | 37.1 | 36.5 | 36.1 | 36.3 | 34 | 28 | 20 | 13.5 | 14.7 | 15.3 | 15.1 | 14.5 | 14 | 13.8 | 13.6 | 14.4 | 14.8 | 15 | 12.7 | 15.3 | 21.1 | 26.2 | 30.5 | 33.7 | 34.6 | 34.6 | 33.7 | 32.7 | 30.1 | 23.3 | 12.8 | 10.5 | 13.2 | 14.6 | 15 | 15.4 | 14.1 | 15.1 | 13.9 | 14.7 | 14.2 | 13.3 | 8.9 | 0.333 | 0.331 | 0.343 | 0.362 | 0.365 | 0.362 | 0.368 | 0.352 | 0.355 | 0.353 | 0.342 | 0.332 | 2.469 | 2.486 | 2.439 | 2.38 | 2.391 | 2.411 | 2.402 | 2.431 | 2.425 | 2.439 | 2.445 | 2.478 | 268 | 285 | 292 | 291 | 290 | 290 | 287 | 290 | 284 | 273 | 262 | 260 | 26 | 29 | 33 | 37 | 38 | 37 | 37 | 35 | 33 | 30 | 26 | 24 | 729 | 1051 | 1499 | 1953 | 2355 | 2636 | 2601 | 2342 | 1910 | 1368 | 896 | 656 | 117 | 129 | 150 | 170 | 137 | 98 | 70 | 64 | 62 | 84 | 57 | 101 | N/A | N/A | N/A | N/A | -1.12 | N/A | N/A | N/A | N/A | N/A | 0.72 | N/A | -2.02 | N/A | N/A | N/A | N/A | -211 | 239 | 54 | 49
| MODESTO-CITY_STYP20 | 12 | 4 | USA | CA | MODESTO CITY | 724926 | 23258 | 37.624 | -120.951 | 73 | 14.66 | -8 | NAP | 98-19 | 3B | 12 | 31.2 | 33.7 | 21 | 15.8 | 55.6 | 24.7 | 18.9 | 54.4 | 22.5 | 53.7 | 19.6 | 52.3 | 2.3 | 120 | 0.464 | 7 | 30.2 | 101.7 | 69.4 | 98.6 | 68.3 | 95.8 | 67.2 | 71.6 | 96.3 | 70 | 94.3 | 68.7 | 92.3 | 9.9 | 330 | 62.4 | 84.5 | 82.6 | 60.5 | 78.8 | 79.6 | 58.8 | 74.3 | 77.6 | 35.3 | 96.4 | 33.9 | 94.4 | 32.8 | 92.4 | 79 | 19 | 17 | 15.4 | 27.4 | 106.6 | 2.2 | 2.5 | 25.8 | 108.4 | 24.5 | 109.8 | 23.3 | 111.2 | 21.7 | 113 | 26.6 | 73.8 | 2.3 | 2 | 25 | 75.2 | 23.6 | 76.4 | 22.3 | 77.6 | 20.7 | 79.1 | 63.4 | 47.7 | 51.8 | 56.9 | 61.3 | 68.5 | 75.3 | 79.6 | 78.1 | 74 | 64.9 | 54.6 | 47.7 | 12.5 | 4.7 | 4.61 | 5.43 | 6.28 | 6.51 | 6.46 | 5.5 | 4.67 | 5.49 | 5.22 | 5.33 | 4.97 | 261 | 100 | 31 | 7 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 104 | 2260 | 535 | 368 | 255 | 144 | 36 | 5 | 0 | 0 | 3 | 64 | 314 | 536 | 5166 | 29 | 83 | 220 | 340 | 574 | 760 | 918 | 871 | 721 | 462 | 154 | 34 | 1691 | 0 | 0 | 4 | 32 | 145 | 314 | 453 | 406 | 275 | 61 | 1 | 0 | 21782 | 0 | 1 | 113 | 544 | 1930 | 4102 | 5979 | 5041 | 3238 | 807 | 27 | 0 | 11481 | 0 | 0 | 13 | 174 | 857 | 2236 | 3515 | 2819 | 1627 | 240 | 0 | 0 | 6.5 | 4.4 | 5.5 | 6.4 | 7.6 | 8.6 | 8.8 | 8.2 | 7.7 | 6.5 | 5.5 | 4.4 | 4.9 | 12.4 | 2.2 | 1.9 | 2.1 | 1 | 0.2 | 0.1 | 0 | 0.1 | 0.3 | 0.7 | 2 | 1.7 | 27.4 | 5.7 | 5.9 | 6.5 | 3 | 1.1 | 0.5 | 0.7 | 0.7 | 2.2 | 2.4 | 6 | 3.9 | 6.4 | 0.2 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8 | 1.6 | 1.6 | 1.7 | 0.9 | 0.2 | 0.1 | 0.2 | 0.2 | 0.6 | 0.7 | 1.5 | 1 | 66.7 | 72.9 | 81.9 | 91 | 98.2 | 104.3 | 105.9 | 103.5 | 100.4 | 91.6 | 77.4 | 65 | 53.4 | 58 | 60.8 | 64.6 | 67.6 | 70.5 | 71.2 | 69.2 | 67.5 | 64.1 | 60.5 | 55.2 | 62.6 | 69 | 77.1 | 84.8 | 93.6 | 100 | 102 | 99.6 | 96.6 | 85.9 | 73.4 | 61.6 | 53.4 | 56.4 | 59.6 | 61.6 | 65.4 | 68.6 | 69.8 | 68.6 | 66.6 | 62.5 | 58.3 | 53.3 | 59.5 | 65.2 | 73.5 | 80.5 | 89.2 | 95.9 | 98.7 | 96.4 | 93.1 | 82.1 | 69.1 | 59.1 | 52.1 | 54.4 | 58 | 59.8 | 63.2 | 66.9 | 68.8 | 67.6 | 65.9 | 60.8 | 56.7 | 52.5 | 56.7 | 62.1 | 69.4 | 75.7 | 84.4 | 91.9 | 95.5 | 93.3 | 89.6 | 78.6 | 65.2 | 56.8 | 51 | 53.2 | 56.4 | 58.2 | 61.6 | 65.5 | 67.5 | 66.9 | 64.7 | 59.7 | 54.8 | 51 | 58.3 | 60.3 | 63.8 | 66.4 | 70.1 | 73 | 74.7 | 72.7 | 72.2 | 66.7 | 63 | 59.2 | 62.1 | 67.8 | 77 | 86 | 94.5 | 100.4 | 100.5 | 98.1 | 91.7 | 84.6 | 73.7 | 62.6 | 55.2 | 58.1 | 61.3 | 63.5 | 67 | 70.3 | 71.9 | 70.5 | 69 | 64.5 | 60.3 | 56.3 | 59 | 66 | 73.9 | 81.9 | 90.1 | 95.6 | 97.4 | 94.9 | 90.3 | 81.5 | 69.7 | 59.3 | 53.4 | 56.1 | 59.4 | 61.3 | 64.8 | 68.4 | 70.2 | 69 | 67.3 | 62.8 | 58.3 | 54.1 | 57.3 | 63.4 | 70.9 | 77.2 | 86.1 | 92.4 | 94.9 | 92.9 | 89.1 | 78.2 | 66.2 | 57.2 | 51.6 | 54.2 | 57.3 | 59.3 | 62.6 | 66.7 | 68.6 | 67.7 | 65.8 | 61.1 | 56.5 | 52 | 55.6 | 60.8 | 67.5 | 73.1 | 81.6 | 89.3 | 92.8 | 90.8 | 87.2 | 75.3 | 63.3 | 55.5 | 16.3 | 19.1 | 21.4 | 23.6 | 26.7 | 29.1 | 30.2 | 29.7 | 28.4 | 25.6 | 20.7 | 16.7 | 21.9 | 24.6 | 27.7 | 31.3 | 32.7 | 33.2 | 32 | 32.4 | 33 | 31.7 | 26.5 | 20 | 13.3 | 13.8 | 12.9 | 12.5 | 11.7 | 11.4 | 11.3 | 11.3 | 10.7 | 12.1 | 13.2 | 12.2 | 15.8 | 21.5 | 25.3 | 28.6 | 30.9 | 31.6 | 30.3 | 30.5 | 30.2 | 27.5 | 22.2 | 12.8 | 10.4 | 13 | 12.6 | 12.6 | 12 | 11.8 | 11.8 | 11.4 | 10.7 | 11.1 | 11.8 | 8.8 | 0.339 | 0.335 | 0.341 | 0.358 | 0.362 | 0.355 | 0.366 | 0.35 | 0.352 | 0.353 | 0.343 | 0.326 | 2.434 | 2.465 | 2.44 | 2.393 | 2.4 | 2.43 | 2.412 | 2.437 | 2.436 | 2.436 | 2.435 | 2.492 | 266 | 284 | 293 | 292 | 291 | 292 | 288 | 291 | 285 | 273 | 262 | 264 | 27 | 30 | 33 | 37 | 37 | 36 | 37 | 35 | 33 | 30 | 27 | 24 | 736 | 1065 | 1524 | 1969 | 2366 | 2646 | 2596 | 2344 | 1918 | 1382 | 912 | 667 | 117 | 126 | 147 | 168 | 131 | 92 | 72 | 62 | 61 | 82 | 56 | 100 | 1.53 | N/A | N/A | N/A | N/A | N/A | N/A | -256 | 319 | N/A | 0.74 | N/A | N/A | N/A | N/A | N/A | N/A | -216 | 248 | 58 | 47
| LIVERMORE_STYP20 | 12 | 4 | USA | CA | LIVERMORE | 724927 | 23285 | 37.693 | -121.814 | 393 | 14.49 | -8 | NAP | 98-19 | 3A | 1 | 30.9 | 33.4 | 16.2 | 12.7 | 51.8 | 20.7 | 15.7 | 52 | 20 | 51.1 | 17.7 | 53.3 | 1.6 | 70 | 0.494 | 7 | 29.2 | 99 | 67.4 | 95 | 65.9 | 91.1 | 64.9 | 69.4 | 93.3 | 67.8 | 90.4 | 66.2 | 87.5 | 9.9 | 280 | 60.9 | 81 | 75.9 | 59.2 | 76.1 | 72.5 | 57.8 | 72.4 | 70.5 | 33.6 | 93.4 | 32.1 | 90.2 | 31 | 87.9 | 78.8 | 19.2 | 17.7 | 16.2 | 26.9 | 105.5 | 2 | 2.9 | 25.5 | 107.6 | 24.3 | 109.3 | 23.2 | 110.9 | 21.7 | 113 | 24.9 | 72.2 | 2.2 | 2.8 | 23.3 | 74.2 | 22 | 75.9 | 20.8 | 77.4 | 19.1 | 79.5 | 60.3 | 48.3 | 50.7 | 54.2 | 57.4 | 62.5 | 68.6 | 72.5 | 72.3 | 70.4 | 63.7 | 54.3 | 48.4 | 10.41 | 4.88 | 4.87 | 5.22 | 5.71 | 5.88 | 6.41 | 5.85 | 5.02 | 5.75 | 5.35 | 5.48 | 5.08 | 271 | 91 | 46 | 18 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 91 | 2587 | 517 | 400 | 334 | 239 | 122 | 28 | 5 | 3 | 14 | 88 | 322 | 515 | 4044 | 39 | 66 | 149 | 226 | 387 | 558 | 698 | 692 | 612 | 426 | 150 | 41 | 884 | 0 | 0 | 1 | 10 | 44 | 136 | 237 | 230 | 176 | 49 | 1 | 0 | 10910 | 0 | 2 | 57 | 269 | 742 | 1827 | 2703 | 2451 | 2058 | 761 | 40 | 0 | 5288 | 0 | 0 | 3 | 79 | 316 | 922 | 1412 | 1236 | 1052 | 266 | 2 | 0 | 6.2 | 4.6 | 5 | 5.5 | 6.6 | 8.1 | 8.5 | 8.6 | 7.9 | 6.3 | 5 | 4.1 | 4.6 | 14.9 | 2.9 | 2.6 | 2.2 | 1.1 | 0.4 | 0.1 | 0 | 0.1 | 0.2 | 0.8 | 2 | 2.4 | 32.4 | 6.7 | 7.3 | 6.7 | 4.6 | 2 | 0.7 | 0.7 | 0.9 | 1.5 | 3.6 | 5.4 | 7 | 6.4 | 0.3 | 0.1 | 0.1 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 5.2 | 2 | 1.9 | 1.7 | 1 | 0.5 | 0.2 | 0.1 | 0.2 | 0.4 | 0.9 | 1.6 | 1.7 | 68.8 | 72.8 | 79.5 | 87.9 | 95 | 102 | 103.7 | 101.9 | 100.6 | 92.7 | 78.6 | 67.2 | 51.9 | 56.4 | 60.5 | 62.8 | 65.9 | 68.8 | 69.3 | 68.1 | 66.5 | 63.7 | 58.5 | 54.9 | 64.2 | 68.5 | 74.9 | 81.5 | 88.4 | 95.8 | 97.8 | 96.7 | 96.2 | 86.5 | 73.9 | 63.4 | 52.2 | 55.2 | 58.7 | 61.5 | 63.5 | 66.6 | 67.6 | 66.4 | 65.2 | 61.1 | 57.5 | 53 | 60.9 | 64.4 | 70.5 | 75.8 | 82.4 | 90.7 | 93 | 91.8 | 91.4 | 82.2 | 69 | 60.8 | 52.2 | 54 | 56.7 | 58.7 | 60.9 | 64.9 | 66.4 | 65.6 | 63.8 | 59.3 | 55.4 | 52.8 | 57.6 | 61 | 66.2 | 70.5 | 76.4 | 84.7 | 88.2 | 87 | 86.4 | 77.8 | 65.2 | 58.3 | 50.9 | 52.2 | 54.7 | 56.4 | 59.1 | 62.9 | 65.3 | 64.6 | 62.5 | 58.1 | 53.8 | 51.5 | 57.9 | 59.7 | 63 | 65.5 | 68.2 | 70.9 | 72.7 | 71.2 | 70.9 | 66 | 62 | 59.6 | 62 | 67.2 | 76.3 | 81.9 | 91.1 | 97 | 99.2 | 96.7 | 89.6 | 85 | 72.9 | 63.4 | 55.4 | 57.4 | 60.1 | 62.4 | 64.9 | 68.2 | 69.3 | 68.4 | 67.3 | 63.5 | 59.7 | 57.2 | 59.8 | 65 | 71.7 | 78.7 | 85.2 | 92.5 | 92.9 | 91.7 | 89.7 | 81.1 | 69 | 60.8 | 53.6 | 55.3 | 58 | 59.6 | 62.2 | 66 | 67.4 | 66.6 | 65.5 | 61.7 | 57.9 | 55.1 | 57.5 | 62.5 | 68.2 | 73.4 | 79.7 | 87.9 | 89.8 | 87.6 | 87 | 77.3 | 65.4 | 58.5 | 51.8 | 53.5 | 55.8 | 57.3 | 59.8 | 63.9 | 65.8 | 65.2 | 63.9 | 59.9 | 56.2 | 52.8 | 56.5 | 59.7 | 64.2 | 68.8 | 74.1 | 82.8 | 86.6 | 84.8 | 83.4 | 73.3 | 63 | 56.2 | 18.1 | 19.2 | 21.5 | 22.6 | 23.9 | 27.4 | 29.2 | 28.9 | 28.5 | 25.9 | 21.4 | 18.3 | 23 | 25.5 | 29.4 | 32.9 | 35.1 | 37.1 | 36.1 | 36.7 | 37.6 | 34.2 | 27.1 | 22 | 13.8 | 14.9 | 15.9 | 15.8 | 15 | 14.5 | 13.2 | 13.4 | 14.6 | 14.8 | 13.9 | 13.3 | 16.7 | 21.1 | 26.5 | 29.3 | 32.1 | 34.3 | 33.6 | 32.9 | 32.6 | 28.6 | 22 | 14.3 | 11.3 | 13.2 | 15.3 | 15 | 14.6 | 14.1 | 13.2 | 12.6 | 13.2 | 13.2 | 12.6 | 9.8 | 0.32 | 0.325 | 0.339 | 0.359 | 0.365 | 0.36 | 0.365 | 0.35 | 0.35 | 0.333 | 0.325 | 0.324 | 2.527 | 2.518 | 2.459 | 2.383 | 2.388 | 2.41 | 2.398 | 2.431 | 2.426 | 2.507 | 2.51 | 2.52 | 275 | 289 | 293 | 292 | 290 | 291 | 288 | 291 | 285 | 281 | 270 | 265 | 25 | 28 | 33 | 37 | 38 | 37 | 37 | 35 | 33 | 28 | 25 | 23 | 749 | 1059 | 1503 | 1959 | 2312 | 2558 | 2480 | 2224 | 1843 | 1338 | 901 | 666 | 109 | 128 | 140 | 164 | 138 | 99 | 69 | 71 | 63 | 81 | 56 | 98 | 0.99 | N/A | N/A | N/A | N/A | N/A | -50 | -234 | 356 | 108 | N/A | N/A | -2.11 | N/A | N/A | N/A | N/A | -198 | 243 | N/A | 44
| OAKLAND-INTL_STYP20 | 3 | 4 | USA | CA | OAKLAND INTL | 724930 | 23230 | 37.7444 | -122.2236 | 8 | 14.69 | -8 | NAP | 94-19 | 3C | 1 | 36.9 | 39.2 | 20.1 | 15.1 | 53 | 25.8 | 19.8 | 51.6 | 26.5 | 53.1 | 23.4 | 53.3 | 3.1 | 50 | 0.521 | 9 | 16.6 | 83.9 | 64.4 | 79.5 | 63.1 | 75.4 | 62.1 | 66.5 | 78.6 | 65 | 75.8 | 63.8 | 73.4 | 10.7 | 310 | 62.7 | 85.1 | 69 | 61.1 | 80.4 | 67.9 | 59.7 | 76.4 | 66.8 | 31.1 | 78.6 | 29.9 | 75.9 | 29 | 73.5 | 73.6 | 23.5 | 20 | 18.2 | 32.5 | 93.7 | 2.4 | 3.7 | 30.8 | 96.4 | 29.3 | 98.6 | 28 | 100.7 | 26.2 | 103.4 | 30 | 69.7 | 2.7 | 2.2 | 28 | 71.3 | 26.4 | 72.6 | 24.9 | 73.8 | 22.9 | 75.4 | 58.4 | 50.6 | 52.7 | 55.4 | 57.4 | 59.9 | 62.6 | 63.8 | 64.6 | 65 | 61.9 | 55.5 | 50.7 | 6.6 | 4.07 | 4.1 | 4.13 | 4.33 | 4.12 | 4.12 | 3.38 | 3.61 | 4.52 | 4.42 | 4.55 | 4.45 | 119 | 42 | 18 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 44 | 2602 | 447 | 344 | 299 | 232 | 171 | 96 | 64 | 50 | 52 | 117 | 287 | 443 | 3176 | 60 | 94 | 172 | 224 | 308 | 377 | 427 | 453 | 451 | 370 | 173 | 67 | 184 | 0 | 0 | 1 | 6 | 13 | 24 | 26 | 38 | 53 | 22 | 1 | 0 | 1207 | 0 | 1 | 11 | 53 | 108 | 193 | 125 | 170 | 360 | 178 | 8 | 0 | 346 | 0 | 0 | 1 | 9 | 31 | 63 | 31 | 49 | 120 | 42 | 0 | 0 | 8.5 | 6.6 | 7.9 | 8.7 | 9.9 | 10.4 | 10.1 | 10 | 9.4 | 8.3 | 7.1 | 6.3 | 6.9 | 17.9 | 3.7 | 2.8 | 2.8 | 1.2 | 0.2 | 0.1 | 0 | 0 | 0.2 | 1.3 | 2.7 | 2.6 | 35.5 | 9.1 | 7.2 | 8 | 5.4 | 2.4 | 1.2 | 0.7 | 0.9 | 1.5 | 8.2 | 7.9 | 6.1 | 7.2 | 0.3 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 6.9 | 2.6 | 2.1 | 2 | 1.3 | 0.4 | 0.3 | 0.2 | 0.2 | 0.4 | 1.6 | 2 | 1.5 | 66.5 | 69.6 | 75 | 80.8 | 84.1 | 87.9 | 84.1 | 86.5 | 89.9 | 84.9 | 74.1 | 65.6 | 51.3 | 57.3 | 58.2 | 61.5 | 63 | 65.3 | 66.7 | 66.2 | 65.5 | 62.1 | 59 | 53.1 | 61.7 | 65 | 69.7 | 73.2 | 75.9 | 79.3 | 77.3 | 78.5 | 82.9 | 79 | 69.3 | 62.5 | 53.9 | 54.8 | 57.4 | 58.8 | 61 | 63.4 | 64.6 | 64.6 | 64.5 | 60.4 | 57.2 | 53.9 | 59.1 | 62.2 | 65.6 | 68.3 | 70.4 | 73.6 | 72.8 | 73.6 | 77.5 | 74 | 65.4 | 60.1 | 53.1 | 53.8 | 55.8 | 57.4 | 59.5 | 61.6 | 62.6 | 63.3 | 63.2 | 59.6 | 56.5 | 53.9 | 57.1 | 59.7 | 62.9 | 64.5 | 66.5 | 70.2 | 70.3 | 71.5 | 72.9 | 70.4 | 63.2 | 57.9 | 52.3 | 53.7 | 54.9 | 55.9 | 57.8 | 60.5 | 61.4 | 62.4 | 62.4 | 59.1 | 56 | 52.9 | 58.4 | 59.8 | 61.5 | 63.7 | 66 | 68.1 | 68 | 67.9 | 68.4 | 65.7 | 62.5 | 59.8 | 60.5 | 63.8 | 71.5 | 75.6 | 78.9 | 80.7 | 81.4 | 81.6 | 81.8 | 77 | 70.1 | 62 | 56.4 | 57.7 | 59.2 | 60.5 | 62.7 | 64.7 | 64.9 | 65.6 | 66.2 | 63.5 | 60.2 | 57.9 | 58.8 | 62.2 | 65.6 | 69.3 | 72.5 | 76.3 | 76.1 | 75.5 | 78.1 | 72.9 | 65.5 | 60.1 | 54.8 | 56.2 | 57.5 | 58.9 | 60.4 | 62.6 | 63.2 | 64.1 | 64.6 | 62 | 58.9 | 56.1 | 57.2 | 60.5 | 62.9 | 66.2 | 68.5 | 72.7 | 72.1 | 73 | 74.8 | 70.7 | 63.4 | 58.5 | 53.4 | 54.6 | 56.1 | 57.2 | 58.7 | 60.8 | 61.9 | 62.6 | 63.2 | 60.4 | 57.4 | 54.2 | 55.9 | 58.5 | 61.3 | 63.5 | 65.8 | 69.3 | 69.7 | 70.3 | 72 | 68.1 | 61.7 | 56.7 | 13.2 | 13.5 | 14.8 | 14.9 | 13.9 | 15 | 13.8 | 14 | 16.6 | 17.3 | 15 | 13.3 | 16 | 17.4 | 20.6 | 22 | 21.7 | 22.9 | 18.8 | 18.9 | 27.2 | 25.1 | 19.2 | 15 | 9.5 | 10.1 | 11.2 | 11.4 | 10.3 | 10.4 | 8.7 | 8.8 | 11.6 | 12.1 | 10.9 | 9.3 | 10.8 | 14.2 | 16.3 | 19.1 | 19.1 | 20.7 | 17.8 | 18.7 | 22.2 | 20 | 14.7 | 9.4 | 7.8 | 9 | 9.8 | 10.7 | 9.7 | 10 | 8.5 | 8.9 | 10.3 | 10.4 | 9.6 | 7.2 | 0.324 | 0.33 | 0.342 | 0.36 | 0.364 | 0.36 | 0.369 | 0.349 | 0.348 | 0.34 | 0.324 | 0.325 | 2.549 | 2.532 | 2.484 | 2.401 | 2.417 | 2.435 | 2.413 | 2.465 | 2.454 | 2.521 | 2.548 | 2.551 | 274 | 287 | 292 | 292 | 291 | 291 | 287 | 292 | 286 | 279 | 272 | 265 | 24 | 28 | 32 | 37 | 37 | 36 | 37 | 34 | 32 | 28 | 24 | 23 | 754 | 1054 | 1491 | 1950 | 2253 | 2466 | 2339 | 2086 | 1763 | 1297 | 892 | 662 | 107 | 128 | 134 | 155 | 145 | 104 | 77 | 88 | 66 | 82 | 57 | 97 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | -2.14 | N/A | N/A | N/A | N/A | -198 | 243 | N/A | 44
; | PALO-ALTO-AP_STYP20 | 4 |  |  |  | PALO-ALTO-AP | 724937
; | SAN-CARLOS-AP_STYP20 | 3 |  |  |  | SAN-CARLOS-AP | 724938
| SAN-FRANCISCO-INTL_STYP20 | 3 | 4 | USA | CA | SAN FRANCISCO INTL | 724940 | 23234 | 37.62 | -122.365 | 8 | 14.69 | -8 | NAP | 94-19 | 3C | 1 | 40.3 | 42.2 | 26.2 | 20.2 | 52.1 | 29.8 | 23.9 | 51.5 | 31.4 | 56.3 | 26.5 | 55.3 | 3.5 | 150 | 0.583 | 9 | 16 | 82.9 | 62.8 | 78.1 | 62 | 74.5 | 61.5 | 65.9 | 77.4 | 64.2 | 74.4 | 63 | 72.1 | 12.6 | 290 | 61.6 | 81.9 | 68.9 | 60.2 | 77.9 | 67.5 | 59 | 74.6 | 66.3 | 30.5 | 77.4 | 29.3 | 74.5 | 28.4 | 72 | 78.1 | 28.5 | 25.5 | 23.3 | 36.2 | 92.9 | 2.1 | 3.6 | 34.7 | 95.5 | 33.5 | 97.6 | 32.3 | 99.6 | 30.8 | 102.2 | 33.3 | 69.4 | 2.4 | 2.4 | 31.5 | 71.1 | 30.1 | 72.5 | 28.7 | 73.8 | 27 | 75.5 | 58.3 | 51.3 | 53 | 55.2 | 56.8 | 59.2 | 62 | 63.3 | 64.2 | 64.8 | 62.2 | 56.2 | 51.4 | 6.29 | 3.78 | 3.99 | 4.17 | 4.34 | 4.25 | 4.22 | 3.29 | 3.44 | 4.65 | 4.55 | 4.2 | 4.11 | 84 | 29 | 14 | 4 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 31 | 2606 | 424 | 336 | 305 | 251 | 191 | 112 | 74 | 56 | 57 | 113 | 266 | 421 | 3128 | 70 | 98 | 166 | 206 | 287 | 359 | 413 | 441 | 445 | 378 | 190 | 75 | 173 | 0 | 0 | 1 | 5 | 12 | 21 | 22 | 32 | 52 | 27 | 1 | 0 | 945 | 0 | 0 | 10 | 46 | 90 | 154 | 97 | 125 | 278 | 140 | 5 | 0 | 267 | 0 | 0 | 0 | 10 | 26 | 52 | 22 | 34 | 89 | 34 | 0 | 0 | 10.3 | 6.6 | 8.3 | 10 | 12.4 | 13.5 | 13.7 | 12.7 | 12.2 | 10.9 | 9 | 7 | 7 | 21.9 | 4.2 | 4.1 | 3 | 1.5 | 0.7 | 0.2 | 0 | 0.1 | 0.1 | 1.1 | 2.3 | 4.6 | 38 | 10.4 | 14.3 | 8.7 | 5 | 3.3 | 1.6 | 0.1 | 0.9 | 0.5 | 3.7 | 7.2 | 11.8 | 8.1 | 0.3 | 0 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.4 | 6.3 | 3.1 | 3 | 2.4 | 1.2 | 0.8 | 0.4 | 0 | 0.2 | 0.1 | 1.1 | 1.8 | 3.2 | 65.1 | 70 | 74.6 | 80.1 | 83.5 | 86.8 | 82.5 | 85.1 | 88.9 | 84.5 | 73 | 64.5 | 53.1 | 56.8 | 59 | 60.7 | 61.7 | 63.6 | 65.2 | 64.7 | 64.4 | 61 | 59.3 | 57.3 | 61.4 | 64.6 | 68.4 | 72.2 | 74.7 | 77.8 | 76 | 76.6 | 81.5 | 77.5 | 68 | 61.6 | 54.1 | 55.9 | 56.6 | 57.9 | 59.6 | 61.7 | 63.2 | 63.7 | 63.3 | 59.5 | 57.3 | 56.3 | 59.1 | 61.6 | 64.2 | 66.6 | 69.3 | 72.3 | 72.3 | 73 | 76 | 73 | 65.1 | 59.8 | 53.5 | 55.1 | 55.6 | 56.2 | 58.6 | 60.6 | 61.8 | 62.5 | 62.6 | 59.2 | 56.7 | 55.2 | 57.2 | 59.1 | 61.5 | 63.3 | 65.7 | 69.1 | 69.8 | 70.5 | 72.1 | 69.5 | 62.7 | 58 | 52.7 | 53.7 | 54.7 | 54.9 | 56.7 | 59.1 | 60.7 | 61.4 | 61.8 | 59 | 56.2 | 53.8 | 58.9 | 60.3 | 61.6 | 62.7 | 65.3 | 66.2 | 66.3 | 66.9 | 68.4 | 65.6 | 62.4 | 60.8 | 60.8 | 64.1 | 70.1 | 75 | 77.1 | 81.8 | 79.5 | 78.5 | 79.4 | 75.2 | 68.4 | 62.7 | 56.4 | 58 | 59.1 | 59.7 | 62 | 63.2 | 63.9 | 64.6 | 65.9 | 63.3 | 60.4 | 58.9 | 58.7 | 62.2 | 65.2 | 68.5 | 71.4 | 75.3 | 74.3 | 74.3 | 76.8 | 71.9 | 65.1 | 60.5 | 54.9 | 56.4 | 57.3 | 57.7 | 59.4 | 61.3 | 62.4 | 63.2 | 64 | 61.8 | 59 | 56.8 | 57.3 | 60.2 | 62.1 | 64.8 | 67.3 | 71.5 | 71.4 | 71.9 | 73.9 | 70 | 63.3 | 58.7 | 53.4 | 54.8 | 55.8 | 55.8 | 57.6 | 59.6 | 61 | 61.9 | 62.3 | 60.1 | 57.4 | 54.6 | 55.9 | 58.2 | 60.3 | 62.1 | 64.6 | 68.2 | 69.1 | 70.1 | 71.1 | 67.5 | 61.4 | 56.9 | 10.6 | 11.6 | 13.1 | 13.8 | 13.8 | 15.2 | 14.6 | 14.5 | 16 | 15.4 | 12.5 | 10.5 | 13.3 | 15.7 | 18.2 | 20.6 | 21.2 | 22.2 | 18.8 | 18.8 | 23.9 | 22.1 | 16 | 11.5 | 8.1 | 9.1 | 10.2 | 10.6 | 10.3 | 10.4 | 8.8 | 8.5 | 11.1 | 10.7 | 8.8 | 7.7 | 9.5 | 13.1 | 15.5 | 18.3 | 18.9 | 20.9 | 18.1 | 18.2 | 21.6 | 19 | 13.1 | 8.2 | 7.1 | 8.3 | 9.6 | 10.3 | 9.8 | 10.1 | 8.7 | 8.4 | 10.4 | 10 | 8.4 | 7 | 0.324 | 0.332 | 0.341 | 0.358 | 0.365 | 0.359 | 0.367 | 0.345 | 0.348 | 0.338 | 0.322 | 0.324 | 2.562 | 2.537 | 2.504 | 2.421 | 2.426 | 2.449 | 2.432 | 2.494 | 2.47 | 2.54 | 2.568 | 2.566 | 275 | 286 | 293 | 292 | 290 | 291 | 288 | 293 | 287 | 280 | 273 | 266 | 24 | 28 | 31 | 36 | 36 | 36 | 36 | 33 | 32 | 27 | 23 | 23 | 764 | 1058 | 1494 | 1952 | 2220 | 2410 | 2246 | 2000 | 1715 | 1279 | 895 | 667 | 102 | 127 | 129 | 150 | 148 | 105 | 82 | 98 | 69 | 81 | 57 | 95 | N/A | N/A | -2.02 | N/A | N/A | N/A | N/A | N/A | 245 | 40 | N/A | N/A | -2.14 | N/A | N/A | N/A | N/A | -198 | 243 | N/A | 44
| SAN-JOSE-INTL_STYP20 | 4 | 4 | USA | CA | SAN JOSE INTL | 724945 | 23293 | 37.359 | -121.924 | 51 | 14.67 | -8 | NAP | 94-19 | 3C | 12 | 36 | 38.3 | 19.6 | 14.7 | 52.8 | 24.3 | 18.5 | 53.7 | 24.8 | 54.5 | 21.7 | 54.5 | 2.4 | 150 | 0.456 | 8 | 20.8 | 91.4 | 66.1 | 87.7 | 65.2 | 83.9 | 64.2 | 68.9 | 85.6 | 67.4 | 82.9 | 66.1 | 80.7 | 10.3 | 330 | 62.9 | 86 | 74.8 | 61.3 | 81.1 | 73.2 | 60.3 | 78.2 | 71.9 | 33 | 85.5 | 31.7 | 82.5 | 30.7 | 80.8 | 78.8 | 19.7 | 17.9 | 16.3 | 32.1 | 98.9 | 3.1 | 3.4 | 29.9 | 101.3 | 28.1 | 103.3 | 26.4 | 105.3 | 24.1 | 107.7 | 29.5 | 71.5 | 2.9 | 2.6 | 27.4 | 73.4 | 25.7 | 75 | 24.1 | 76.5 | 22 | 78.4 | 60.9 | 51.6 | 53.5 | 56.6 | 58.8 | 62.9 | 67.1 | 69.5 | 69.8 | 68.9 | 64.1 | 56.6 | 51.3 | 8.27 | 4.6 | 4.8 | 4.93 | 5.37 | 5.15 | 5.02 | 4.07 | 3.86 | 4.95 | 4.75 | 4.96 | 4.71 | 106 | 36 | 18 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 39 | 2102 | 416 | 321 | 262 | 199 | 104 | 27 | 4 | 2 | 11 | 75 | 256 | 425 | 4097 | 85 | 117 | 211 | 266 | 399 | 514 | 606 | 613 | 568 | 436 | 204 | 78 | 619 | 0 | 0 | 3 | 14 | 38 | 91 | 145 | 150 | 129 | 46 | 3 | 0 | 5261 | 0 | 6 | 51 | 193 | 403 | 863 | 1103 | 1062 | 1077 | 469 | 34 | 0 | 1765 | 0 | 0 | 4 | 52 | 140 | 321 | 342 | 337 | 431 | 134 | 4 | 0 | 6.5 | 5 | 6.2 | 6.7 | 7.5 | 7.8 | 7.9 | 7.4 | 7 | 6.2 | 5.5 | 4.9 | 5.3 | 14.1 | 2.8 | 2.2 | 2.3 | 1.2 | 0.2 | 0 | 0 | 0.1 | 0.2 | 0.9 | 2.2 | 2 | 32.6 | 7.4 | 6.6 | 6.4 | 3.9 | 1.7 | 0.6 | 0.7 | 0.7 | 1 | 4.6 | 6.2 | 5 | 7.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 5.4 | 2 | 2 | 1.5 | 1.1 | 0.4 | 0.1 | 0.2 | 0.2 | 0.4 | 1 | 1.7 | 1.2 | 69.8 | 74.9 | 79.8 | 86.4 | 91.1 | 95 | 94.7 | 93.9 | 95.2 | 88.7 | 79 | 67.7 | 53.6 | 58.1 | 60.2 | 62.9 | 65.3 | 67.6 | 69.2 | 66.7 | 65.1 | 62.5 | 59.8 | 55.2 | 65.2 | 69.5 | 74.2 | 79.6 | 83.7 | 88.4 | 88.2 | 88.4 | 90.3 | 83.8 | 72.8 | 64.2 | 54.6 | 56.1 | 57.6 | 60.4 | 62.2 | 65.9 | 67.6 | 66.5 | 64.6 | 60.6 | 57.6 | 54 | 62.8 | 65.3 | 70.3 | 74.1 | 78.3 | 83.1 | 83.5 | 83.4 | 84.9 | 79.3 | 69.2 | 62.1 | 53.9 | 54.8 | 56.6 | 58.6 | 61.3 | 64.6 | 66.3 | 65.6 | 63.4 | 59.1 | 56.5 | 53.8 | 60.4 | 62.4 | 66.5 | 69.6 | 73.4 | 78.7 | 80.1 | 79.8 | 79.8 | 74.8 | 65.6 | 60 | 52.9 | 53.7 | 55.1 | 56.9 | 59.6 | 63.2 | 65.4 | 65 | 63.1 | 58.8 | 55.3 | 53 | 59.9 | 61.2 | 62.3 | 65.2 | 67.9 | 70.6 | 71 | 70.3 | 70.1 | 65.9 | 62.9 | 60.2 | 63.9 | 69.1 | 75.7 | 81.4 | 87 | 89.3 | 90.4 | 86.8 | 87.2 | 80.3 | 73 | 64.5 | 57.4 | 58.7 | 60 | 62.1 | 64.8 | 67.7 | 68.6 | 68.1 | 66.7 | 63.6 | 60.5 | 58.2 | 61.7 | 65.9 | 70.3 | 76.4 | 79.7 | 84.7 | 84.9 | 83.5 | 82.1 | 77.3 | 68.2 | 61.7 | 55.5 | 56.7 | 58.2 | 59.7 | 62.5 | 65.8 | 67.2 | 66.6 | 65.2 | 62 | 59 | 56.3 | 60 | 63.4 | 67.4 | 71.6 | 75.6 | 81.2 | 81.8 | 80.9 | 80.9 | 74.3 | 66 | 59.8 | 53.8 | 54.9 | 56.4 | 57.8 | 60.4 | 63.8 | 65.8 | 65.3 | 63.9 | 60.4 | 57.4 | 54.2 | 58.6 | 60.9 | 64.8 | 67.8 | 71.7 | 77 | 79.2 | 78.5 | 78 | 71.1 | 63.9 | 58.3 | 16 | 16.3 | 18.2 | 19 | 19.4 | 21.3 | 21.1 | 20.8 | 21.6 | 21 | 17.8 | 15.6 | 19.9 | 21.9 | 24.7 | 27.3 | 27.7 | 28.6 | 26.6 | 27.2 | 29.8 | 28.2 | 22.9 | 18.3 | 11.2 | 11.6 | 12.3 | 12.9 | 11.9 | 11.7 | 10.7 | 10.4 | 10.9 | 11.4 | 11.1 | 10.2 | 13.4 | 17.4 | 20.8 | 23.3 | 23.6 | 25.2 | 23.6 | 23.4 | 24.2 | 22.5 | 17.8 | 11 | 8.9 | 10.2 | 11.3 | 12.1 | 11.4 | 11.7 | 10.5 | 9.9 | 10 | 10 | 9.7 | 7.6 | 0.324 | 0.332 | 0.337 | 0.36 | 0.372 | 0.363 | 0.367 | 0.35 | 0.356 | 0.333 | 0.322 | 0.323 | 2.533 | 2.511 | 2.489 | 2.398 | 2.385 | 2.418 | 2.418 | 2.459 | 2.432 | 2.534 | 2.542 | 2.546 | 275 | 286 | 295 | 292 | 288 | 290 | 288 | 292 | 284 | 282 | 273 | 267 | 25 | 29 | 32 | 37 | 38 | 37 | 36 | 34 | 33 | 27 | 24 | 23 | 774 | 1073 | 1518 | 1964 | 2277 | 2496 | 2371 | 2127 | 1796 | 1327 | 915 | 685 | 102 | 125 | 134 | 161 | 141 | 101 | 72 | 82 | 67 | 80 | 54 | 95 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | -241 | 337 | 108 | N/A | N/A | -2.11 | N/A | N/A | N/A | N/A | -194 | 239 | N/A | 44
| SAN-JOSE-REID-HILLV_STYP20 | 4 | 4 | USA | CA | SAN-JOSE-REID-HILLV | 724946 | 99999 | 37.33 | -121.82 | 134 | 14.62 | -8 | NAP | N/A | 3C | 12 | 35.42 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 8 | 21.06 | 91.4 | 66.02 | N/A | N/A | N/A | N/A | 68.9 | 85.82 | N/A | N/A | N/A | N/A | N/A | N/A | 62.78 | N/A | 75.56 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 7.8293 | 7.3819 | 6.9345 | 6.0397 | 5.3687 | 4.6976 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 95.18 | 95 | 94.28 | 94.28 | 90.14 | 79.52 | N/A | N/A | N/A | N/A | N/A | N/A | 67.28 | 69.62 | 67.1 | 65.48 | 62.78 | 59.36 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 21.24 | 21.06 | 21.06 | 21.6 | 20.88 | 18.18 | N/A | N/A | N/A | N/A | N/A | N/A | 28.6 | 26.6 | 27.5 | 29.7 | 28.4 | 23.8 | N/A | N/A | N/A | N/A | N/A | N/A | 11.9 | 11.2 | 10.8 | 11 | 11.5 | 11.5 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.363 | 0.367 | 0.35 | 0.356 | 0.333 | 0.322 | N/A | N/A | N/A | N/A | N/A | N/A | 2.418 | 2.418 | 2.459 | 2.432 | 2.534 | 2.542 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
| BUCHANAN-FIELD_STYP20 | 12 | 4 | USA | CA | BUCHANAN FIELD | 724950 | 23254 | 37.992 | -122.055 | 18 | 14.69 | -8 | NAP | 99-19 | 3A | 1 | 33.1 | 35.5 | 18.7 | 14.1 | 54.8 | 22.9 | 17.3 | 54.2 | 19.6 | 55.5 | 17.2 | 53.5 | 1.9 | 160 | 0.491 | 7 | 28.6 | 97.9 | 66.9 | 94.2 | 65.8 | 90.6 | 64.9 | 69 | 92.8 | 67.5 | 89.9 | 66.2 | 87.1 | 10.1 | 300 | 60.3 | 78.3 | 73.6 | 59 | 74.6 | 71.8 | 57.9 | 71.5 | 70.5 | 33 | 92.7 | 31.8 | 89.9 | 30.7 | 87.1 | 76.5 | 19.8 | 18.1 | 16.6 | 29.8 | 104.8 | 2.1 | 3.1 | 28.3 | 107 | 27.1 | 108.8 | 26 | 110.5 | 24.4 | 112.7 | 27.7 | 71.6 | 2.3 | 2 | 26 | 73.1 | 24.7 | 74.3 | 23.4 | 75.4 | 21.7 | 76.9 | 61.4 | 49.2 | 52.3 | 56.3 | 59.3 | 64.7 | 70.3 | 72.7 | 72.4 | 70.7 | 64.3 | 55.2 | 49.2 | 10 | 4.44 | 4.59 | 5 | 5.45 | 5.45 | 5.88 | 5.15 | 4.47 | 5.28 | 5.04 | 5.23 | 4.86 | 190 | 69 | 26 | 6 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 73 | 2263 | 490 | 356 | 273 | 187 | 72 | 12 | 3 | 2 | 8 | 74 | 295 | 491 | 4367 | 44 | 90 | 201 | 280 | 457 | 610 | 705 | 696 | 622 | 444 | 171 | 47 | 967 | 0 | 0 | 3 | 16 | 64 | 173 | 243 | 233 | 180 | 54 | 1 | 0 | 11188 | 0 | 7 | 74 | 297 | 918 | 2110 | 2664 | 2346 | 2012 | 725 | 35 | 0 | 5178 | 0 | 0 | 6 | 87 | 366 | 1035 | 1354 | 1116 | 976 | 235 | 3 | 0 | 7.2 | 4.5 | 5.6 | 6.6 | 7.9 | 9.4 | 10.2 | 10.4 | 9.5 | 7.4 | 5.6 | 4.5 | 4.7 | 20.1 | 4.3 | 3.6 | 2.6 | 1.4 | 0.7 | 0.2 | 0 | 0 | 0.1 | 1.1 | 2.3 | 4 | 30.5 | 10.5 | 12.9 | 8.3 | 4.6 | 3 | 1.9 | 0.1 | 0.8 | 0.6 | 4.3 | 6.8 | 10.2 | 8.7 | 0.2 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 5.3 | 2.9 | 2.6 | 2.3 | 1.1 | 0.8 | 0.4 | 0 | 0.2 | 0.1 | 1.1 | 1.7 | 2.9 | 68.2 | 74.3 | 80.5 | 87.8 | 95.3 | 101.8 | 102.5 | 100.2 | 99.7 | 91 | 78.2 | 66 | 51.9 | 56.8 | 61.1 | 63.7 | 66.1 | 68.4 | 68.5 | 67.6 | 66.3 | 62.9 | 58.8 | 53.9 | 63.6 | 69.1 | 75.8 | 82 | 88.9 | 96.1 | 96.8 | 95.2 | 95.1 | 86.2 | 73.5 | 63 | 52.9 | 55.4 | 59.3 | 61.2 | 63.7 | 66.5 | 67 | 66.3 | 64.9 | 61.2 | 57.3 | 53.2 | 60.9 | 65.1 | 71.7 | 76.6 | 83.7 | 91 | 92.2 | 90.7 | 90.6 | 81.9 | 69.3 | 60.5 | 52.2 | 53.8 | 57.1 | 59 | 61.6 | 64.9 | 66.2 | 65.2 | 64 | 59.4 | 55.6 | 53 | 58.1 | 61.9 | 67.6 | 71.7 | 78.7 | 85.9 | 88 | 86.3 | 85.6 | 77.6 | 65.7 | 58.3 | 51.3 | 53 | 55.4 | 57.1 | 60 | 63 | 65.1 | 64.4 | 62.7 | 58.6 | 54.7 | 52 | 58 | 60.3 | 63.4 | 65.7 | 68.7 | 70.8 | 71.9 | 69.7 | 69.5 | 65.9 | 62.3 | 59.5 | 61.8 | 68.1 | 76 | 83.1 | 90.7 | 97.3 | 98.4 | 93.6 | 95.4 | 83.9 | 72.9 | 62.7 | 55.9 | 58.1 | 60.7 | 62.5 | 65.4 | 68 | 68.8 | 68 | 67.1 | 63.7 | 60.2 | 57.4 | 60 | 64.8 | 72.9 | 79 | 86.4 | 92 | 92.5 | 90.4 | 88.6 | 80.3 | 68.6 | 60 | 54.1 | 56.2 | 58.6 | 60.2 | 62.9 | 66 | 67.2 | 66.4 | 65.4 | 62.1 | 58.6 | 55.4 | 57.8 | 62.7 | 68.7 | 74.5 | 80.5 | 88.1 | 89.3 | 87.2 | 85.2 | 76.8 | 65.9 | 58.3 | 52.4 | 54.3 | 56.6 | 57.9 | 60.8 | 64.1 | 65.6 | 65.1 | 63.9 | 60.3 | 56.9 | 53.4 | 56.4 | 60.4 | 65.2 | 69.8 | 76.5 | 83.8 | 86.3 | 84.3 | 82.7 | 72.9 | 63.6 | 56.4 | 16.5 | 17.9 | 19.6 | 21.1 | 23.5 | 26.8 | 28.6 | 27.5 | 27.1 | 24.2 | 19.8 | 16.3 | 21.8 | 24.6 | 27.2 | 30.6 | 33.3 | 36.1 | 36 | 35.2 | 36.2 | 32.2 | 25.5 | 19.7 | 12.7 | 13.4 | 13.5 | 14 | 12.9 | 12.3 | 11.9 | 11.4 | 11.9 | 12.3 | 12.3 | 11.5 | 15 | 19 | 23.3 | 27.6 | 30.3 | 33.3 | 34.3 | 31.7 | 31.3 | 26.8 | 20.1 | 11.8 | 10.2 | 11.4 | 12.6 | 13.4 | 12.8 | 12.3 | 12.1 | 11.1 | 11.1 | 11.3 | 11.1 | 8.5 | 0.323 | 0.326 | 0.34 | 0.359 | 0.364 | 0.361 | 0.366 | 0.35 | 0.348 | 0.333 | 0.325 | 0.326 | 2.536 | 2.529 | 2.475 | 2.394 | 2.407 | 2.421 | 2.406 | 2.444 | 2.446 | 2.525 | 2.53 | 2.529 | 273 | 288 | 293 | 292 | 291 | 290 | 288 | 291 | 286 | 281 | 270 | 263 | 24 | 28 | 32 | 37 | 37 | 37 | 37 | 35 | 33 | 27 | 24 | 23 | 736 | 1045 | 1481 | 1945 | 2293 | 2532 | 2454 | 2192 | 1821 | 1316 | 883 | 649 | 114 | 130 | 142 | 161 | 141 | 104 | 74 | 76 | 64 | 85 | 58 | 100 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.67 | N/A | -2.07 | N/A | N/A | N/A | N/A | -207 | 239 | N/A | 47
| NAPA-COUNTY-AP_STYP20 | 2 | 4 | USA | CA | NAPA COUNTY AP | 724955 | 93227 | 38.21 | -122.285 | 14 | 14.69 | -8 | NAP | 98-19 | 3C | 12 | 29.6 | 32.1 | 17.5 | 13.3 | 51.7 | 22.2 | 16.7 | 49.2 | 25 | 55.9 | 21.7 | 55.2 | 2.1 | 0 | 0.54 | 8 | 24 | 91.1 | 65.9 | 86.4 | 64.9 | 82.4 | 64 | 68.4 | 86.1 | 66.8 | 82.9 | 65.4 | 79.7 | 10 | 200 | 61.5 | 81.6 | 74.3 | 60.4 | 78.5 | 72.7 | 59.2 | 75.2 | 71 | 32.6 | 86.2 | 31.2 | 82.9 | 30.2 | 79.9 | 75.9 | 21.3 | 19.1 | 17.5 | 23.8 | 99.7 | 2.4 | 3.6 | 22 | 102.2 | 20.6 | 104.3 | 19.3 | 106.3 | 17.6 | 108.9 | 22.5 | 71.5 | 2.5 | 1.5 | 20.7 | 72.6 | 19.3 | 73.4 | 17.8 | 74.3 | 16 | 75.3 | 57.3 | 47.5 | 49.9 | 52.8 | 55.2 | 59.8 | 64.5 | 65.9 | 66.1 | 65.1 | 60.1 | 52.6 | 47.3 | 8.36 | 4.5 | 4.64 | 4.77 | 5.02 | 4.65 | 4.7 | 3.79 | 3.62 | 4.74 | 4.67 | 5.21 | 5.15 | 338 | 103 | 54 | 25 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 115 | 3076 | 543 | 423 | 380 | 296 | 176 | 62 | 30 | 26 | 54 | 165 | 371 | 550 | 2994 | 25 | 51 | 111 | 166 | 303 | 436 | 493 | 500 | 454 | 314 | 110 | 31 | 254 | 0 | 0 | 1 | 2 | 13 | 48 | 59 | 60 | 58 | 13 | 0 | 0 | 4025 | 1 | 4 | 34 | 128 | 332 | 758 | 666 | 713 | 926 | 436 | 26 | 1 | 1438 | 0 | 0 | 3 | 29 | 117 | 292 | 220 | 240 | 398 | 137 | 2 | 0 | 7.5 | 6.3 | 6.4 | 6.9 | 8.1 | 9.1 | 9.8 | 10 | 9.1 | 7.3 | 5.8 | 5.3 | 6.2 | 26.4 | 5.4 | 4.6 | 3.7 | 1.5 | 0.7 | 0.2 | 0 | 0.1 | 0.3 | 1.5 | 3.7 | 4.8 | 51.3 | 13.8 | 15.3 | 12 | 5.7 | 3.7 | 2 | 1.1 | 1.3 | 2.3 | 10.4 | 10.5 | 15.5 | 10.5 | 0.4 | 0.2 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 0 | 8.7 | 3.6 | 3.7 | 2.9 | 1.5 | 1 | 0.4 | 0.2 | 0.3 | 0.5 | 1.8 | 2.7 | 3.6 | 67.1 | 72.2 | 78.2 | 83.9 | 90.1 | 95.1 | 93 | 94 | 96.3 | 89.9 | 77.3 | 65 | 50.8 | 58.1 | 62.1 | 63.8 | 65.5 | 68.1 | 68.3 | 66.9 | 65.4 | 61.7 | 59.7 | 49.6 | 62.4 | 67.2 | 72.7 | 77.5 | 82.6 | 88 | 85.6 | 86.2 | 90.5 | 83.8 | 72.4 | 61.8 | 52.1 | 55.5 | 59.1 | 61.3 | 63.1 | 65.6 | 67 | 66.5 | 64.7 | 60.1 | 57 | 52.6 | 59.1 | 63.3 | 68 | 71.9 | 76.6 | 82.1 | 80.8 | 81.4 | 84.4 | 78.9 | 67.6 | 59.3 | 51.9 | 53.4 | 56.5 | 58.8 | 61.2 | 64.1 | 65.4 | 65.3 | 63.6 | 58.7 | 55.5 | 53.1 | 56.4 | 60.1 | 64 | 67.1 | 72 | 77.4 | 76.8 | 77.2 | 78.6 | 73.9 | 63.7 | 57.1 | 51.4 | 52.8 | 55 | 57 | 59.8 | 62.6 | 63.9 | 64 | 62.9 | 58.1 | 54.6 | 51.9 | 57.3 | 60.1 | 64 | 66.3 | 68.7 | 70.2 | 70.2 | 69.6 | 69.1 | 65.9 | 62.9 | 59 | 60.4 | 67.4 | 75.5 | 80.4 | 86.3 | 91.2 | 89.3 | 87.8 | 87.3 | 80.9 | 73.5 | 60.8 | 55.3 | 57.8 | 60.5 | 63.1 | 64.6 | 67.3 | 67.6 | 67.4 | 66.8 | 63.5 | 60.1 | 57 | 58.4 | 64.1 | 70.2 | 75.8 | 79 | 84.5 | 84.2 | 83.8 | 84.3 | 76.4 | 67.3 | 58.9 | 53.8 | 55.9 | 58.2 | 60.2 | 62.4 | 65.1 | 65.8 | 65.8 | 65.3 | 61.8 | 58.3 | 55.2 | 56.4 | 61 | 65.4 | 69.7 | 74.5 | 79.6 | 79.9 | 80 | 80.6 | 73.3 | 63.9 | 57.1 | 52.4 | 54.1 | 56.1 | 57.8 | 60.3 | 63.2 | 64.2 | 64.3 | 63.7 | 60 | 56.5 | 53.1 | 55.3 | 58.5 | 62.1 | 65.3 | 70.8 | 76.1 | 76.4 | 76.6 | 77.3 | 70.3 | 61.8 | 55.4 | 18.1 | 20 | 21.8 | 23.3 | 24.2 | 25.3 | 23.3 | 24 | 27.9 | 27.5 | 22.7 | 18.8 | 23.8 | 27.3 | 29.8 | 32.8 | 34.2 | 35 | 31.1 | 32.7 | 39.1 | 37.4 | 29.8 | 21.7 | 15.2 | 16.9 | 18.1 | 18.9 | 17.6 | 16 | 14.5 | 15.2 | 16.8 | 17.5 | 16.5 | 13.9 | 16 | 21.4 | 25.7 | 28.6 | 29.6 | 30.6 | 28.7 | 29.5 | 33.2 | 29.4 | 22 | 12.7 | 11.6 | 14.2 | 16.7 | 17.6 | 16.5 | 14.7 | 13.7 | 14 | 15.3 | 15.4 | 14.1 | 9.9 | 0.32 | 0.321 | 0.334 | 0.356 | 0.36 | 0.357 | 0.361 | 0.345 | 0.343 | 0.321 | 0.318 | 0.321 | 2.548 | 2.548 | 2.501 | 2.411 | 2.43 | 2.444 | 2.429 | 2.468 | 2.477 | 2.576 | 2.56 | 2.546 | 274 | 290 | 295 | 292 | 292 | 292 | 289 | 292 | 288 | 285 | 273 | 265 | 24 | 27 | 31 | 36 | 36 | 36 | 36 | 34 | 32 | 26 | 23 | 23 | 729 | 1034 | 1464 | 1932 | 2287 | 2528 | 2461 | 2192 | 1819 | 1304 | 874 | 639 | 116 | 134 | 146 | 161 | 141 | 108 | 75 | 75 | 63 | 89 | 61 | 102 | 0.74 | N/A | -3.01 | N/A | N/A | N/A | N/A | N/A | 254 | N/A | 0.67 | N/A | -2.07 | N/A | N/A | N/A | N/A | -207 | 239 | N/A | 47
| SONOMA-COUNTY-AP_STYP20 | 2 | 4 | USA | CA | SONOMA COUNTY AP | 724957 | 23213 | 38.504 | -122.81 | 114 | 14.64 | -8 | NAP | 98-19 | 3C | 12 | 29.3 | 31.5 | 18.9 | 14.3 | 57.3 | 24.3 | 18.5 | 51 | 21.1 | 55.2 | 18.2 | 54.3 | 1.6 | 300 | 0.486 | 7 | 29.9 | 94.9 | 66.5 | 91 | 65.7 | 87.3 | 64.5 | 69 | 89.9 | 67.4 | 87.3 | 65.9 | 84.3 | 8.6 | 180 | 61 | 80.3 | 74.7 | 59.3 | 75.6 | 72.6 | 58 | 72.2 | 71 | 33.1 | 90.5 | 31.7 | 87.5 | 30.6 | 84.4 | 86.7 | 17.1 | 15 | 12.6 | 25.3 | 101.7 | 2.3 | 3.3 | 23.6 | 104 | 22.3 | 105.9 | 21 | 107.7 | 19.4 | 110.1 | 24.4 | 72.9 | 2.5 | 3.6 | 22.6 | 75.5 | 21.1 | 77.6 | 19.8 | 79.6 | 18 | 82.2 | 58.1 | 47.8 | 50.3 | 53.3 | 56 | 60.8 | 65.8 | 67.4 | 67.6 | 66.2 | 61.1 | 53 | 47.5 | 8.86 | 4.41 | 4.86 | 5.16 | 5.49 | 5.02 | 5.18 | 4.09 | 3.86 | 4.92 | 5.08 | 5.27 | 5.04 | 319 | 97 | 50 | 25 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 110 | 2901 | 535 | 412 | 364 | 274 | 150 | 48 | 17 | 15 | 39 | 144 | 360 | 543 | 3279 | 27 | 58 | 126 | 190 | 336 | 475 | 541 | 545 | 487 | 343 | 119 | 32 | 386 | 0 | 0 | 1 | 5 | 20 | 73 | 93 | 95 | 76 | 22 | 1 | 0 | 7287 | 3 | 11 | 69 | 214 | 572 | 1421 | 1464 | 1447 | 1401 | 640 | 44 | 1 | 3069 | 0 | 1 | 11 | 60 | 203 | 633 | 621 | 639 | 659 | 237 | 5 | 0 | 4.6 | 3.3 | 4.5 | 5 | 5.5 | 5.8 | 5.7 | 5.4 | 4.9 | 4.3 | 3.9 | 3.3 | 3.6 | 45.4 | 9.8 | 8.4 | 5.4 | 3 | 1.9 | 0.4 | 0 | 0.1 | 0.1 | 2.2 | 4.2 | 10.2 | 71.9 | 30 | 25.3 | 18.8 | 9.3 | 6.9 | 1.4 | 0.1 | 1.2 | 0.4 | 6 | 11.1 | 23.1 | 24.8 | 0.9 | 0.4 | 0.2 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 2.4 | 13.6 | 6.9 | 5.7 | 5.3 | 2.3 | 2.1 | 0.4 | 0 | 0.3 | 0.1 | 1.5 | 3.1 | 6.5 | 69.2 | 75.5 | 81.1 | 87.1 | 92.1 | 98.2 | 98.7 | 97.6 | 98.3 | 93 | 79.2 | 67.8 | 52.5 | 58.9 | 61.8 | 63.8 | 65.9 | 68.2 | 70.1 | 67.8 | 66.7 | 62.5 | 60.6 | 52.4 | 64 | 69.3 | 74.9 | 80.3 | 85.6 | 92.4 | 91.6 | 92.2 | 93.5 | 86.4 | 73.8 | 62.9 | 52.5 | 56.2 | 58.8 | 61.5 | 62.9 | 66.4 | 67.4 | 66.6 | 65.2 | 60.9 | 57.5 | 52.1 | 60.1 | 64.7 | 70.2 | 74.4 | 80.5 | 87.5 | 86.8 | 87.2 | 88.2 | 81.3 | 68.7 | 59.8 | 51.9 | 53.1 | 56.1 | 58.7 | 61.6 | 64.9 | 66.2 | 65.7 | 63.9 | 59.1 | 55.7 | 53.1 | 56.9 | 60.5 | 65.4 | 69.2 | 75.3 | 82.2 | 82.2 | 82.2 | 82.2 | 75.9 | 64 | 57.3 | 51.4 | 51.8 | 54.1 | 56.2 | 59.2 | 63.2 | 64.8 | 64.6 | 62.7 | 58.1 | 54.3 | 52.2 | 58 | 60.3 | 63.6 | 66.3 | 68.4 | 71.1 | 71.3 | 70.5 | 69.8 | 66 | 63.3 | 59.2 | 62.1 | 71.3 | 78.1 | 82.3 | 87.5 | 93.7 | 94.5 | 92.5 | 91.4 | 82.5 | 75.6 | 61.4 | 55.7 | 57.8 | 60.2 | 62.5 | 65.1 | 68.2 | 68.4 | 67.9 | 67.1 | 63.5 | 60.3 | 57.3 | 59.4 | 65.8 | 72.6 | 77.6 | 82.5 | 89.1 | 89.1 | 88.5 | 88.1 | 80.9 | 68.5 | 59.2 | 54.2 | 55.5 | 57.8 | 59.8 | 62.5 | 65.9 | 66.6 | 66.2 | 65.2 | 61.6 | 58.2 | 55.3 | 57.1 | 61.4 | 67.1 | 72.4 | 77.7 | 84.7 | 85.2 | 85.1 | 84.2 | 75.1 | 64.4 | 57.5 | 52.6 | 53.7 | 55.4 | 57.2 | 60.1 | 63.8 | 65 | 64.7 | 63.5 | 59.7 | 56.3 | 53.5 | 55.6 | 58.2 | 62.1 | 67.3 | 73.5 | 80.6 | 81.9 | 81.6 | 80.8 | 71.7 | 61.7 | 55.6 | 19.7 | 20.6 | 22.4 | 24.1 | 26.7 | 29.7 | 29.9 | 30 | 31.6 | 29.2 | 23.3 | 19.3 | 27.2 | 29.9 | 32.3 | 34.2 | 36.9 | 39.5 | 38.9 | 40 | 42.9 | 40.2 | 31.6 | 24.7 | 16.8 | 17.3 | 17.6 | 17.6 | 17.5 | 17 | 17 | 16.8 | 17.5 | 17.2 | 17 | 15.6 | 18.4 | 23.8 | 28.4 | 30.8 | 33.2 | 36 | 35.4 | 35.3 | 36.5 | 32.5 | 24 | 14.3 | 12.9 | 14.9 | 16.5 | 16.8 | 17 | 17 | 16.2 | 15.6 | 16.1 | 15.4 | 14.4 | 10.6 | 0.319 | 0.323 | 0.33 | 0.349 | 0.35 | 0.349 | 0.352 | 0.335 | 0.334 | 0.32 | 0.315 | 0.32 | 2.556 | 2.545 | 2.528 | 2.437 | 2.468 | 2.477 | 2.468 | 2.515 | 2.509 | 2.591 | 2.578 | 2.553 | 274 | 288 | 296 | 295 | 295 | 294 | 292 | 295 | 291 | 285 | 274 | 265 | 24 | 27 | 30 | 35 | 35 | 35 | 35 | 32 | 30 | 25 | 23 | 22 | 717 | 1014 | 1438 | 1908 | 2268 | 2505 | 2405 | 2123 | 1777 | 1273 | 854 | 619 | 116 | 139 | 145 | 155 | 142 | 115 | 91 | 80 | 74 | 93 | 65 | 103 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 212 | N/A | N/A | N/A | -2.14 | N/A | N/A | N/A | N/A | -187 | 248 | N/A | 39
| BLUE-CANYON_STYP20 | 16 | 4 | USA | CA | BLUE CANYON | 725845 | 23225 | 39.277 | -120.71 | 5276 | 12.1 | -8 | NAP | 94-19 | 4C | 2 | 21.1 | 23.6 | -6.9 | 4.6 | 42.8 | -1.6 | 6.1 | 42.6 | 25.6 | 34.5 | 22 | 35.8 | 5.7 | 60 | 0.447 | 7 | 12.9 | 83.8 | 58.7 | 81.3 | 57.8 | 79.2 | 56.4 | 62.5 | 78.3 | 60.5 | 76.8 | 59 | 75.3 | 6.4 | 270 | 56.1 | 81.6 | 70.8 | 53.6 | 74.3 | 70 | 51.3 | 68.3 | 69.1 | 30.7 | 78.3 | 29.2 | 76.9 | 27.9 | 75.2 | 80.1 | 18.8 | 16.2 | 13.1 | 17 | 87.7 | 3.2 | 2.3 | 14.7 | 89.3 | 12.8 | 90.6 | 11 | 91.9 | 8.7 | 93.6 | 14.6 | 65.5 | 3.2 | 3.6 | 12.3 | 68.1 | 10.4 | 70.2 | 8.7 | 72.2 | 6.4 | 74.9 | 51.9 | 40.5 | 38.6 | 41.5 | 44.5 | 52.8 | 62 | 70.2 | 69.4 | 64.2 | 54.5 | 44.8 | 38.9 | 14.37 | 8.91 | 8.97 | 8.93 | 9.72 | 9.83 | 8.92 | 5.77 | 5.64 | 8.53 | 9.15 | 9.38 | 8.29 | 1907 | 315 | 334 | 292 | 224 | 89 | 16 | 0 | 0 | 9 | 63 | 211 | 354 | 5301 | 760 | 738 | 729 | 616 | 390 | 155 | 21 | 24 | 114 | 339 | 607 | 808 | 2606 | 20 | 16 | 28 | 58 | 176 | 375 | 626 | 603 | 436 | 201 | 55 | 12 | 522 | 0 | 0 | 0 | 0 | 12 | 64 | 182 | 161 | 91 | 12 | 0 | 0 | 2362 | 0 | 0 | 0 | 0 | 36 | 294 | 911 | 740 | 352 | 29 | 0 | 0 | 346 | 0 | 0 | 0 | 0 | 1 | 44 | 147 | 110 | 43 | 1 | 0 | 0 | 5.5 | 5.7 | 6.2 | 6.3 | 6 | 5.4 | 5.2 | 4.5 | 4.6 | 5.1 | 5.3 | 5.4 | 6.3 | 70.4 | 12.2 | 10.3 | 9.4 | 5.2 | 2.1 | 0.8 | 0.1 | 0.6 | 1.3 | 4.3 | 10.7 | 11.5 | 121.7 | 33.9 | 37.7 | 22.2 | 14.2 | 5.3 | 2.7 | 1 | 3.7 | 7 | 22.3 | 28.3 | 41.6 | 23.5 | 0.7 | 0.8 | 1.7 | 0.7 | 0.1 | 0 | 0 | 0 | 0 | 0 | 1 | 0.4 | 20.7 | 8.2 | 8.2 | 5.6 | 3.8 | 1.5 | 0.8 | 0.3 | 1 | 1.9 | 4.6 | 7 | 9.1 | 62.7 | 62.7 | 65.5 | 70.4 | 78.5 | 85.2 | 86.9 | 86.2 | 85 | 78.1 | 68.7 | 61.6 | 42.3 | 44.1 | 46.1 | 50.4 | 55.9 | 61.2 | 60.1 | 58.5 | 54.6 | 52.2 | 48.4 | 42.3 | 58.5 | 58.6 | 61.3 | 66.4 | 73.6 | 80.4 | 83.9 | 83 | 80.4 | 72.8 | 64.7 | 57.1 | 40.7 | 42.5 | 45 | 48.5 | 54.2 | 58.1 | 59.9 | 57.7 | 54.8 | 50.4 | 46.6 | 40.2 | 55.6 | 55.2 | 57.9 | 63 | 70.4 | 77.2 | 81.2 | 80.7 | 78 | 69.7 | 61 | 53.8 | 39.7 | 40.7 | 43.4 | 46.9 | 52.3 | 56.7 | 58.9 | 56.7 | 54 | 49.1 | 44.5 | 38.2 | 52.7 | 52 | 54.3 | 59.2 | 66.9 | 74.6 | 79 | 78.4 | 75.5 | 66.5 | 57.9 | 50.7 | 38.5 | 38.9 | 41.6 | 45 | 50.4 | 55.1 | 57.5 | 55.6 | 53.3 | 47.6 | 42.9 | 37.4 | 46.7 | 47.2 | 49.4 | 53.3 | 59.4 | 63.9 | 65.1 | 62.8 | 68.6 | 55.1 | 51 | 46.2 | 52.6 | 56.8 | 60.7 | 64.7 | 72.3 | 80 | 81.8 | 80.5 | 70.8 | 70 | 64.4 | 51.8 | 44.1 | 44.5 | 46.9 | 50.5 | 56.2 | 60.9 | 62.6 | 60.3 | 60 | 52.9 | 48.3 | 43.8 | 51.3 | 53.8 | 57.5 | 62.9 | 69.9 | 76.8 | 79.4 | 77.8 | 72 | 67.8 | 60.8 | 49.1 | 42.3 | 42.5 | 44.9 | 48.4 | 54.1 | 58.6 | 60.9 | 58.8 | 57.1 | 51.3 | 46.3 | 42 | 50.4 | 51.5 | 54.8 | 60 | 67.5 | 74.1 | 77.8 | 76.4 | 72.5 | 65.9 | 57.5 | 47.7 | 40.8 | 40.6 | 43.1 | 46.3 | 51.9 | 56.4 | 59.4 | 57.3 | 55 | 49.6 | 44.6 | 40.3 | 49.5 | 49.2 | 51.9 | 56.9 | 65.2 | 71.9 | 76.1 | 74.9 | 71.9 | 63.7 | 54.5 | 47.2 | 10.1 | 10 | 11.2 | 12.6 | 13 | 13.4 | 12.9 | 13.4 | 13.6 | 12.5 | 10.4 | 9.7 | 12.7 | 12.6 | 14 | 15.6 | 15 | 14.1 | 13.2 | 13.5 | 14 | 13.6 | 12.1 | 12.6 | 8.7 | 9 | 10.5 | 11 | 10.6 | 10.6 | 9 | 8.2 | 8.3 | 8.4 | 8.5 | 8.6 | 11 | 11.2 | 13 | 14.7 | 14.7 | 13.8 | 12.6 | 12.9 | 13.6 | 12.9 | 11.5 | 10 | 8.4 | 9 | 10.1 | 11 | 10.8 | 11 | 9.2 | 8.5 | 9.3 | 8.7 | 8.6 | 8.4 | 0.276 | 0.275 | 0.296 | 0.306 | 0.312 | 0.305 | 0.307 | 0.294 | 0.299 | 0.285 | 0.268 | 0.282 | 2.528 | 2.557 | 2.5 | 2.486 | 2.497 | 2.538 | 2.541 | 2.566 | 2.563 | 2.602 | 2.612 | 2.506 | 289 | 305 | 307 | 308 | 306 | 307 | 305 | 308 | 302 | 298 | 292 | 277 | 23 | 26 | 31 | 33 | 34 | 32 | 32 | 30 | 29 | 25 | 21 | 22 | 722 | 992 | 1400 | 1850 | 2255 | 2623 | 2617 | 2355 | 1892 | 1323 | 841 | 615 | 110 | 141 | 170 | 189 | 189 | 139 | 111 | 92 | 80 | 101 | 70 | 106 | 1.48 | N/A | N/A | N/A | N/A | N/A | -212 | -324 | 198 | 97 | 0.79 | N/A | -1.98 | N/A | N/A | N/A | -58 | -175 | 236 | 95 | 26
| TRUCKEE-TAHOE_STYP20 | 16 | 4 | USA | CA | TRUCKEE-TAHOE | 725846 | 93201 | 39.32 | -120.139 | 5900 | 11.82 | -8 | NAP | 94-19 | 6A | 1 | 0.5 | 6.7 | -2.8 | 5.9 | 4 | 1.3 | 7.3 | 9.8 | 28.7 | 38.3 | 26.2 | 39.2 | 0.3 | 170 | N/A | 7 | 40.8 | 88.2 | 58.3 | 84.5 | 56.8 | 82.3 | 56 | 61.6 | 80.2 | 59.9 | 79 | 58.5 | 78.2 | 9.9 | 230 | 55.4 | 81.6 | 65.9 | 53.5 | 76.1 | 65.5 | 49.9 | 66.3 | 64.6 | 30.6 | 80 | 29.1 | 79.1 | 28 | 78.4 | 69.1 | 22.2 | 18.7 | 16.6 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 44 | 28.5 | 30.3 | 35.7 | 39.8 | 48.4 | 55.1 | 62.5 | 61.5 | 54.2 | 45.2 | 36.2 | 29.8 | 13.62 | 8.23 | 7.06 | 6.89 | 7 | 6.81 | 6.04 | 5.12 | 4.22 | 5.43 | 6.93 | 8.03 | 8.4 | 3349 | 667 | 551 | 445 | 307 | 114 | 26 | 0 | 0 | 22 | 177 | 414 | 626 | 7709 | 1132 | 971 | 910 | 755 | 514 | 299 | 110 | 124 | 325 | 614 | 864 | 1091 | 1163 | 0 | 0 | 0 | 2 | 65 | 177 | 387 | 356 | 148 | 28 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 15 | 1 | 0 | 0 | 0 | 4252 | 0 | 0 | 0 | 0 | 104 | 493 | 1733 | 1417 | 448 | 57 | 0 | 0 | 1227 | 0 | 0 | 0 | 0 | 10 | 79 | 597 | 452 | 82 | 7 | 0 | 0 | 4.7 | 3.9 | 4.2 | 5.3 | 5.8 | 5.7 | 4.8 | 4.9 | 4.8 | 4.4 | 4.2 | 4 | 4 | 29 | 5.5 | 4.5 | 4 | 2 | 1.4 | 0.6 | 0.3 | 0.4 | 0.5 | 1.5 | 2.8 | 5.8 | 54.6 | 12.1 | 9.4 | 14.3 | 5.7 | 4 | 1.5 | 0.8 | 1.4 | 3.3 | 4.6 | 6.1 | 16.9 | 18.7 | 0.9 | 0.7 | 0.9 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 1.3 | 8.7 | 3.4 | 2.6 | 3.3 | 1.5 | 1.1 | 0.5 | 0.2 | 0.4 | 0.7 | 1.3 | 1.7 | 4.4 | 52.1 | 56.9 | 66 | 72.2 | 81.5 | 85.3 | 91.4 | 90.4 | 84.9 | 80.5 | 66.5 | 54.7 | 39.9 | 41.7 | 46.8 | 49 | 56.4 | 57.9 | 59.5 | 58.5 | 55.4 | 52.6 | 47.7 | 41.1 | 47.8 | 50.7 | 61.2 | 67.6 | 77.2 | 82 | 89.8 | 88 | 82.1 | 74 | 61.3 | 50 | 39.8 | 39.4 | 44.7 | 47.7 | 54 | 56.3 | 59.3 | 56.9 | 53.7 | 50.1 | 44.6 | 40.6 | 45 | 45.9 | 55.5 | 63.1 | 72.7 | 80.5 | 86.3 | 84.3 | 79.5 | 70.5 | 55.4 | 46.3 | 36.8 | 36.9 | 41.9 | 45.8 | 52.4 | 55.4 | 58.3 | 56.1 | 53.8 | 48.9 | 42.4 | 39.1 | 41.1 | 42.8 | 51.8 | 57.2 | 68.5 | 76.7 | 82.5 | 82 | 75.4 | 65.7 | 51.7 | 43.3 | 35.4 | 35.9 | 40.4 | 42.8 | 50.5 | 53.7 | 56.9 | 55.7 | 52.2 | 47.4 | 40.8 | 37.6 | 46.2 | 43.4 | 48.3 | 51.2 | 58.8 | 61.8 | 64.5 | 62.5 | 61.4 | 54.4 | 49.1 | 46.2 | 48 | 52.5 | 62.6 | 67.4 | 75.5 | 79.3 | 82.1 | 80.5 | 71.8 | 73.8 | 63.6 | 50 | 40.1 | 40.7 | 45.5 | 48.8 | 55.8 | 59 | 62.3 | 60.3 | 58.1 | 52 | 46.4 | 43 | 45.5 | 48.8 | 59.5 | 64.2 | 73.8 | 77.7 | 81.8 | 79.3 | 75 | 71.3 | 58.7 | 47 | 37.8 | 38.4 | 43.1 | 46.4 | 53.6 | 56.7 | 60.5 | 58.9 | 55.6 | 49.8 | 43.9 | 40.4 | 41.7 | 44.1 | 54.7 | 60.8 | 71.3 | 76.2 | 80.8 | 78.5 | 73.6 | 68.4 | 53.6 | 45.1 | 36.4 | 36.5 | 40.7 | 44.2 | 51.3 | 54.9 | 59.1 | 57.1 | 53.5 | 47.4 | 41.5 | 38.1 | 40.1 | 41 | 50.3 | 56.6 | 67.1 | 73.7 | 79.5 | 77.4 | 73.8 | 63.9 | 50 | 42.2 | 21.7 | 23 | 25 | 26.2 | 31.3 | 36.9 | 40.8 | 40.3 | 39.5 | 34.8 | 26.9 | 22.6 | 27.2 | 29.7 | 33.9 | 38.9 | 40.3 | 43.3 | 44.1 | 44.8 | 46.2 | 44.8 | 37 | 27.7 | 18.5 | 19.6 | 19 | 20.5 | 18.9 | 19.9 | 17.2 | 18.7 | 21.7 | 23.1 | 21.9 | 18.3 | 21.2 | 25 | 32.4 | 35.9 | 38.9 | 41.2 | 39.9 | 38.8 | 40.3 | 42.4 | 33 | 22.6 | 15.2 | 17 | 18.7 | 19.4 | 18.7 | 19.7 | 16.5 | 17.5 | 20.2 | 22.6 | 20.3 | 15.9 | 0.27 | 0.283 | 0.296 | 0.308 | 0.318 | 0.312 | 0.317 | 0.308 | 0.299 | 0.284 | 0.267 | 0.267 | 2.491 | 2.478 | 2.462 | 2.451 | 2.455 | 2.494 | 2.5 | 2.506 | 2.545 | 2.58 | 2.58 | 2.509 | 291 | 301 | 306 | 307 | 304 | 305 | 302 | 304 | 302 | 298 | 292 | 284 | 24 | 28 | 32 | 35 | 35 | 34 | 33 | 32 | 29 | 25 | 22 | 22 | 740 | 1013 | 1434 | 1883 | 2256 | 2620 | 2586 | 2337 | 1895 | 1335 | 861 | 629 | 103 | 130 | 147 | 171 | 192 | 147 | 123 | 99 | 79 | 97 | 64 | 97 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.59 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 157 | 74 | 20
| LAKE-TAHOE_STYP20 | 16 | 4 | USA | CA | LAKE TAHOE | 725847 | 93230 | 38.898 | -119.995 | 6314 | 11.64 | -8 | NAP | 00-19 | 6A | 1 | 3.4 | 9.1 | -3.7 | 5.7 | 17.2 | 0.7 | 7.2 | 21.4 | 25.7 | 37.4 | 22.4 | 37.1 | 2.8 | 190 | 0.607 | 7 | 35.4 | 84.5 | 56.9 | 82.2 | 55.8 | 80 | 55 | 60.1 | 78.3 | 58.5 | 77.2 | 57 | 75.8 | 7.8 | 30 | 53.1 | 76.1 | 66.2 | 50.6 | 69.2 | 65.8 | 48.2 | 63.3 | 64.9 | 29.2 | 77.9 | 28 | 77.1 | 26.9 | 75.8 | 65.5 | 21.1 | 18.3 | 16 | -6.2 | 88.8 | 5 | 2 | -9.8 | 90.2 | -12.8 | 91.4 | -15.6 | 92.6 | -19.2 | 94 | -6.9 | 63 | 4.8 | 1.7 | -10.4 | 64.3 | -13.3 | 65.3 | -16 | 66.2 | -19.5 | 67.5 | 44.6 | 30.5 | 31.2 | 35.8 | 40.3 | 47.8 | 56 | 62.7 | 60.8 | 54.8 | 45.7 | 37.2 | 31 | 13.04 | 7.27 | 7.6 | 7.14 | 6.71 | 6.32 | 5.83 | 4.23 | 3.89 | 5.8 | 5.99 | 7.21 | 7.46 | 3149 | 605 | 527 | 440 | 292 | 116 | 17 | 0 | 0 | 25 | 155 | 384 | 588 | 7490 | 1070 | 946 | 904 | 740 | 533 | 274 | 94 | 137 | 308 | 597 | 834 | 1053 | 1167 | 0 | 0 | 0 | 2 | 48 | 196 | 395 | 335 | 168 | 22 | 1 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 3 | 24 | 7 | 1 | 0 | 0 | 0 | 2653 | 0 | 0 | 0 | 0 | 23 | 335 | 1144 | 858 | 283 | 10 | 0 | 0 | 465 | 0 | 0 | 0 | 0 | 2 | 53 | 250 | 139 | 21 | 0 | 0 | 0 | 5.3 | 4.6 | 5.5 | 6.2 | 6.3 | 5.6 | 5.6 | 4.7 | 4.7 | 4.7 | 4.7 | 5.1 | 5.6 | 22.8 | 3.6 | 3.5 | 3.3 | 1.4 | 1.2 | 0.7 | 0.4 | 0.5 | 0.6 | 1.5 | 2.5 | 3.6 | 37.4 | 10.9 | 8.1 | 11.1 | 3.3 | 3.9 | 2.5 | 1.3 | 1.7 | 2.6 | 5.7 | 6.1 | 10.1 | 12.1 | 0.2 | 0.7 | 0.6 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0.2 | 5.7 | 2.5 | 2 | 2.4 | 0.8 | 0.9 | 0.7 | 0.4 | 0.4 | 0.6 | 1.3 | 1.3 | 2.6 | 55.7 | 57.5 | 63.1 | 68.9 | 77.2 | 85.3 | 88.2 | 86.3 | 82.4 | 75.4 | 63.9 | 55 | 40.3 | 40.8 | 45.1 | 48.2 | 52.6 | 57.8 | 58.6 | 56 | 53.8 | 51.8 | 47.2 | 39.4 | 50.2 | 53.2 | 58.3 | 64.7 | 72.7 | 81.1 | 85.3 | 83.5 | 79.8 | 69.8 | 59.9 | 50.5 | 38 | 38.9 | 42.4 | 46.2 | 50.6 | 55.3 | 57.9 | 55.7 | 53.1 | 49 | 43.9 | 38.1 | 46.7 | 49 | 54.6 | 61.2 | 69.3 | 77.9 | 82.9 | 81.4 | 77.5 | 66.5 | 56 | 47.6 | 36.8 | 37.4 | 40.7 | 44.3 | 49.2 | 53.5 | 56.9 | 55 | 52.4 | 47.1 | 41.8 | 36.8 | 43.5 | 44.8 | 50.4 | 56.8 | 65.4 | 74.8 | 80.5 | 79.2 | 74.8 | 63.2 | 52 | 44.6 | 35.4 | 35.3 | 38.8 | 42.5 | 47.7 | 52.3 | 56.2 | 54.6 | 52 | 45.9 | 39.6 | 36.4 | 42.4 | 43.2 | 46.2 | 50.4 | 54.6 | 60.1 | 63 | 60.3 | 57.9 | 53.4 | 48.6 | 43.8 | 50.7 | 53.9 | 60.2 | 65.4 | 70.8 | 80.4 | 78.9 | 77.6 | 74.3 | 69.7 | 60.4 | 50.1 | 40.3 | 40.5 | 43.5 | 47.5 | 52.4 | 57.5 | 61.1 | 58.5 | 55.7 | 50.9 | 45.6 | 40.9 | 47.4 | 49.7 | 56.1 | 61.7 | 69.4 | 75.9 | 78.5 | 77.3 | 74.3 | 66.1 | 57.1 | 46.8 | 37.9 | 38.4 | 41.5 | 45.3 | 50.4 | 55.5 | 59.5 | 57.2 | 54 | 48.8 | 43 | 38.7 | 44.8 | 46.8 | 52.9 | 59.1 | 66.5 | 73.8 | 78.4 | 76.6 | 74.1 | 63.4 | 53.5 | 45 | 36 | 36.2 | 39.4 | 43.2 | 48.6 | 53.5 | 58.1 | 55.9 | 52.4 | 46.6 | 40.9 | 36.7 | 42.2 | 43.6 | 49 | 55.5 | 63.5 | 71.5 | 76.8 | 75.9 | 72.9 | 60.7 | 50.5 | 43.2 | 23.4 | 22.6 | 22.9 | 23.9 | 27.6 | 32.9 | 35.4 | 36.3 | 35.4 | 30.5 | 25.5 | 22.4 | 28.1 | 29.4 | 30.9 | 34.6 | 36.4 | 38.8 | 37.9 | 39.5 | 40.8 | 37.8 | 33 | 27 | 18.1 | 17.9 | 17.2 | 18.2 | 17.4 | 17 | 15.7 | 17.3 | 19 | 20.2 | 19.7 | 17.4 | 25.2 | 25.7 | 28.7 | 32.4 | 34.8 | 36.6 | 34 | 35.8 | 37.9 | 35.1 | 30.5 | 22.8 | 17.3 | 16.3 | 16.6 | 17.7 | 17.3 | 16.6 | 14.6 | 16.4 | 18 | 19.5 | 19.3 | 16.1 | 0.248 | 0.264 | 0.273 | 0.286 | 0.296 | 0.296 | 0.3 | 0.292 | 0.282 | 0.27 | 0.252 | 0.247 | 2.54 | 2.524 | 2.524 | 2.523 | 2.533 | 2.557 | 2.577 | 2.575 | 2.612 | 2.637 | 2.632 | 2.557 | 303 | 310 | 316 | 315 | 311 | 310 | 308 | 309 | 309 | 305 | 300 | 295 | 23 | 27 | 30 | 32 | 33 | 32 | 31 | 30 | 27 | 24 | 21 | 21 | 750 | 1024 | 1435 | 1886 | 2262 | 2622 | 2568 | 2333 | 1907 | 1358 | 886 | 648 | 98 | 128 | 146 | 168 | 187 | 153 | 128 | 99 | 80 | 98 | 62 | 94 | 1.17 | N/A | N/A | N/A | N/A | N/A | -304 | -461 | N/A | N/A | 0.67 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 173 | 77 | 25
| HAYWARD_STYP20 | 3 | 4 | USA | CA | HAYWARD | 725850 | 93228 | 37.654 | -122.115 | 43 | 14.67 | -8 | NAP | 98-19 | 3C | 1 | 37 | 39.1 | 18.4 | 13.9 | 53 | 23.7 | 18 | 50.6 | 20.9 | 52.9 | 18.8 | 53.8 | 3.3 | 60 | 0.474 | 9 | 17.4 | 87.4 | 65 | 82.7 | 64 | 78.8 | 63.1 | 67.5 | 82.1 | 65.9 | 79.1 | 64.5 | 76.1 | 10.6 | 290 | 62.3 | 84.1 | 71.1 | 61 | 80.2 | 69.4 | 59.8 | 76.7 | 68.5 | 31.8 | 82 | 30.6 | 79.1 | 29.5 | 76.2 | 81.5 | 19.4 | 17.6 | 16.1 | 33.3 | 96.4 | 2 | 4.6 | 31.9 | 99.7 | 30.8 | 102.4 | 29.7 | 105.1 | 28.2 | 108.4 | 30.2 | 70.7 | 2.3 | 3.2 | 28.6 | 73 | 27.3 | 74.9 | 26 | 76.7 | 24.3 | 79 | 59.3 | 51 | 53 | 55.8 | 57.5 | 60.6 | 63.9 | 65.9 | 66.4 | 66.7 | 63 | 56.1 | 51.1 | 7.28 | 4.22 | 4.33 | 4.78 | 4.84 | 4.63 | 5.01 | 4 | 3.68 | 5.12 | 4.59 | 4.51 | 4.56 | 110 | 39 | 18 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 41 | 2414 | 435 | 337 | 289 | 234 | 156 | 78 | 32 | 23 | 32 | 96 | 270 | 432 | 3492 | 69 | 101 | 185 | 226 | 329 | 416 | 494 | 508 | 501 | 402 | 188 | 73 | 319 | 0 | 0 | 3 | 8 | 20 | 45 | 60 | 66 | 83 | 33 | 1 | 0 | 2168 | 1 | 4 | 26 | 91 | 195 | 368 | 345 | 316 | 576 | 235 | 11 | 0 | 693 | 0 | 0 | 3 | 21 | 64 | 133 | 101 | 96 | 218 | 56 | 1 | 0 | 6.9 | 5.1 | 6.3 | 7.1 | 8.3 | 8.7 | 8.4 | 8.2 | 7.6 | 6.6 | 5.6 | 5 | 5.5 | 19.6 | 3.9 | 3.6 | 2.7 | 1.3 | 0.7 | 0.2 | 0 | 0 | 0.1 | 1 | 2.2 | 4 | 33.8 | 9.4 | 12.7 | 7.6 | 4.1 | 2.6 | 1.6 | 0.1 | 0.8 | 0.4 | 3.7 | 6.6 | 9.7 | 7.8 | 0.3 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 5.6 | 2.6 | 2.5 | 2.2 | 1 | 0.7 | 0.4 | 0 | 0.2 | 0.1 | 1 | 1.6 | 2.7 | 67.9 | 72.3 | 77.4 | 82.8 | 87.3 | 91.1 | 89 | 89.7 | 92.6 | 86.1 | 74.9 | 66.8 | 51.9 | 56.4 | 60.1 | 62.6 | 63.3 | 66.3 | 67.6 | 66.4 | 65.9 | 61.2 | 58.5 | 55 | 63.3 | 66.6 | 71.9 | 75.6 | 79.5 | 83.3 | 81.9 | 81.5 | 86.6 | 80.5 | 70.1 | 63.1 | 52.8 | 54.9 | 57.8 | 59 | 61.7 | 64.5 | 65.8 | 65.7 | 64.5 | 61.2 | 56.9 | 54.7 | 60.6 | 63.4 | 67.6 | 70 | 72.9 | 77.5 | 77.2 | 76.6 | 80.6 | 75.7 | 66.6 | 60.9 | 53.1 | 54.3 | 56.2 | 57.6 | 59.8 | 63 | 64.4 | 64.3 | 63.6 | 59.8 | 56.2 | 54 | 58.3 | 60.7 | 64.1 | 65.4 | 68.2 | 72.6 | 73.6 | 73.4 | 75.6 | 71.9 | 63.9 | 58.9 | 52.1 | 52.9 | 54.8 | 55.4 | 58.4 | 61.4 | 62.7 | 62.9 | 62.7 | 59.5 | 55.8 | 52.9 | 58.1 | 59.5 | 62 | 64.7 | 66.5 | 68.5 | 69.1 | 69 | 68.6 | 66.5 | 62.5 | 60.2 | 61.2 | 65.3 | 73.4 | 79.5 | 82.5 | 86.1 | 85.1 | 83.5 | 84.3 | 76.9 | 69.2 | 63.8 | 56.1 | 57.4 | 59.5 | 60.9 | 63.2 | 65.9 | 66.4 | 66.3 | 66.6 | 64.1 | 60.4 | 58 | 59.7 | 63.8 | 68.5 | 73.3 | 75.8 | 80.7 | 80.3 | 78.8 | 80.2 | 73.9 | 66.3 | 60.8 | 54.7 | 55.9 | 57.7 | 58.6 | 60.6 | 63.8 | 64.6 | 64.8 | 65 | 62.4 | 59 | 56.2 | 58.4 | 61.4 | 65 | 67.8 | 71.1 | 76.4 | 76.2 | 75.6 | 77.6 | 71.4 | 64.3 | 59.3 | 53.2 | 54.4 | 56.2 | 56.5 | 58.8 | 61.7 | 63.1 | 63.4 | 63.6 | 60.9 | 57.3 | 54.2 | 57.1 | 59.2 | 62.6 | 64 | 67.4 | 72.3 | 72.9 | 72.7 | 74.1 | 69.2 | 62.4 | 57.5 | 13.9 | 14.4 | 15.1 | 15.2 | 14.8 | 16 | 15.9 | 15.2 | 17.4 | 17.1 | 15.2 | 13.9 | 17.3 | 19.5 | 20.9 | 24.1 | 24.9 | 25.8 | 23 | 21.7 | 27.3 | 24.7 | 19.3 | 15.6 | 10.2 | 11 | 11.4 | 12.4 | 12 | 11.8 | 10.3 | 10 | 12.5 | 12.5 | 10.6 | 9.1 | 12.2 | 15.4 | 17.5 | 21.1 | 21.3 | 23.1 | 21.3 | 20.1 | 22.9 | 19.8 | 15 | 10.3 | 8.3 | 9.6 | 10.2 | 11.5 | 11 | 11 | 9.7 | 9.5 | 10.9 | 10.9 | 9.8 | 7.3 | 0.324 | 0.331 | 0.342 | 0.36 | 0.367 | 0.361 | 0.368 | 0.349 | 0.35 | 0.338 | 0.325 | 0.326 | 2.543 | 2.524 | 2.48 | 2.399 | 2.405 | 2.426 | 2.411 | 2.459 | 2.445 | 2.52 | 2.541 | 2.544 | 274 | 287 | 293 | 292 | 290 | 290 | 287 | 291 | 285 | 279 | 271 | 265 | 24 | 28 | 32 | 37 | 37 | 36 | 37 | 34 | 33 | 28 | 24 | 23 | 757 | 1059 | 1499 | 1955 | 2263 | 2480 | 2356 | 2105 | 1775 | 1307 | 898 | 667 | 106 | 127 | 134 | 157 | 143 | 102 | 75 | 85 | 66 | 81 | 56 | 96 | N/A | N/A | -3.65 | N/A | -1.13 | -1.64 | N/A | -313 | 374 | N/A | N/A | N/A | -2.11 | N/A | N/A | N/A | N/A | -198 | 243 | N/A | 44
| UKIAH_STYP20 | 2 | 4 | USA | CA | UKIAH | 725905 | 23275 | 39.126 | -123.201 | 601 | 14.38 | -8 | NAP | 94-19 | 3A | 12 | 28.5 | 30.6 | 21.1 | 16.2 | 49.2 | 24.8 | 19.3 | 46.4 | 18.1 | 51.6 | 16.1 | 50.9 | 0.3 | 310 | 0.463 | 7 | 35.6 | 100.4 | 67.4 | 97.4 | 66.6 | 93.9 | 65.6 | 70.2 | 95.2 | 68.5 | 92.8 | 67.1 | 90.7 | 7.9 | 120 | 60.8 | 81.2 | 79.5 | 58.7 | 75.4 | 77.2 | 57.1 | 71.1 | 75.1 | 34.3 | 95.3 | 32.9 | 93 | 31.7 | 90.7 | 76.8 | 15.9 | 13.4 | 12.1 | 24.8 | 106.7 | 3.1 | 2.6 | 22.6 | 108.6 | 20.7 | 110.1 | 19 | 111.5 | 16.7 | 113.4 | 23.7 | 73.2 | 3.1 | 1.9 | 21.5 | 74.6 | 19.7 | 75.8 | 18 | 76.9 | 15.7 | 78.3 | 59.5 | 47.5 | 49.3 | 52.7 | 55.8 | 62.3 | 69 | 74.8 | 73.6 | 69.6 | 61.1 | 51.8 | 46.3 | 11.36 | 4.7 | 5.27 | 5.89 | 6.4 | 6.26 | 6.38 | 5.12 | 4.54 | 5.62 | 5.57 | 5.58 | 5.07 | 410 | 104 | 70 | 38 | 16 | 1 | 0 | 0 | 0 | 0 | 1 | 44 | 136 | 2950 | 542 | 439 | 381 | 284 | 130 | 30 | 1 | 1 | 20 | 148 | 395 | 579 | 3893 | 27 | 51 | 123 | 189 | 381 | 569 | 767 | 732 | 588 | 344 | 99 | 23 | 957 | 0 | 0 | 1 | 7 | 45 | 149 | 303 | 268 | 158 | 26 | 0 | 0 | 14783 | 0 | 7 | 97 | 311 | 961 | 2335 | 4218 | 3703 | 2408 | 711 | 32 | 0 | 7839 | 0 | 0 | 15 | 96 | 404 | 1194 | 2456 | 2102 | 1299 | 271 | 2 | 0 | 3.7 | 2.6 | 3.4 | 3.9 | 4.5 | 4.8 | 5.1 | 4.6 | 4 | 3.4 | 2.7 | 2.3 | 2.6 | 42 | 8.3 | 6.8 | 5.6 | 2.6 | 1 | 0.3 | 0 | 0.2 | 0.5 | 2 | 5.9 | 8 | 82.4 | 25 | 22.3 | 18.7 | 9.8 | 6.4 | 2.2 | 0.9 | 1.5 | 3.2 | 8.2 | 17.4 | 22.4 | 15 | 0.5 | 0.4 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 12.8 | 5.6 | 5 | 4.3 | 2.2 | 1.4 | 0.5 | 0.2 | 0.4 | 0.8 | 1.9 | 4.3 | 6 | 69.9 | 74.5 | 82 | 88.2 | 95.5 | 102.4 | 105.5 | 104.3 | 101.5 | 93.4 | 78.9 | 65.1 | 53.3 | 56.7 | 59.6 | 61.4 | 65.6 | 69.1 | 69.5 | 67.7 | 65.2 | 62.4 | 58.6 | 52.3 | 63.8 | 69.2 | 76.2 | 82.4 | 89.7 | 97.1 | 100.4 | 99.3 | 97.1 | 87 | 72.5 | 61 | 51.8 | 54.4 | 56.9 | 60.1 | 63.3 | 67.3 | 68.1 | 66.8 | 64.8 | 60.5 | 56.3 | 52.3 | 59.4 | 64 | 71.5 | 76.9 | 84.3 | 91.7 | 97.1 | 95.4 | 92.8 | 82 | 66.5 | 57.9 | 51.2 | 51.9 | 55.3 | 58.2 | 61.6 | 65.1 | 67.5 | 65.5 | 63.9 | 59.1 | 54 | 52 | 55.9 | 59.2 | 65.8 | 70.8 | 79.2 | 87.2 | 93 | 91.6 | 88.4 | 76.9 | 62 | 55.5 | 50.8 | 51 | 52.9 | 55.3 | 59.6 | 63.5 | 66.5 | 65.1 | 62.9 | 57.5 | 53 | 50.9 | 57.4 | 59.1 | 61.5 | 63.9 | 67.9 | 72.2 | 72.9 | 70.6 | 69.5 | 65.2 | 61.3 | 57.8 | 62.1 | 69.4 | 78.9 | 83.7 | 91.1 | 97.6 | 98.7 | 97.4 | 95.6 | 84.9 | 74 | 60.3 | 54.8 | 56.3 | 58.7 | 60.7 | 65.2 | 69 | 70.7 | 68.6 | 67.1 | 62.8 | 58.4 | 55.8 | 58.5 | 64.7 | 73.7 | 79.4 | 86.5 | 92.9 | 95.7 | 94 | 91.2 | 81.2 | 67.4 | 58.1 | 53.3 | 54.1 | 56.2 | 58.8 | 62.7 | 66.6 | 69 | 67.4 | 65.2 | 60.8 | 56.3 | 53.8 | 56.9 | 60.7 | 67.7 | 75.3 | 82 | 88.6 | 93.3 | 92.1 | 89.1 | 77.8 | 63.2 | 56.1 | 51.4 | 52.1 | 54 | 56.3 | 60.2 | 64.4 | 67.4 | 66 | 63.4 | 58.9 | 54.4 | 51.7 | 55.4 | 57.8 | 63 | 69.3 | 76.9 | 84.7 | 90.9 | 89.6 | 85.8 | 73.4 | 60.1 | 54.5 | 18.7 | 20 | 22.7 | 24.7 | 27.9 | 31.2 | 35.6 | 36.4 | 35.4 | 30.7 | 21.6 | 18.3 | 27.4 | 30.8 | 34.8 | 36.9 | 38.9 | 39.8 | 40.9 | 41.7 | 43.3 | 41 | 31.5 | 23.9 | 16.5 | 17 | 17.2 | 17.1 | 16.2 | 15.2 | 15 | 15.1 | 16.4 | 17.3 | 16.6 | 15.1 | 18.6 | 24.4 | 29.6 | 33.5 | 35.3 | 37 | 38 | 38.5 | 39 | 34.9 | 24.3 | 14.5 | 12.4 | 14.3 | 15.6 | 16.2 | 15.9 | 15.4 | 15.5 | 15.4 | 15.9 | 15.9 | 13.7 | 10.4 | 0.316 | 0.319 | 0.324 | 0.346 | 0.339 | 0.343 | 0.341 | 0.332 | 0.328 | 0.32 | 0.312 | 0.317 | 2.559 | 2.55 | 2.548 | 2.445 | 2.505 | 2.501 | 2.508 | 2.525 | 2.525 | 2.588 | 2.582 | 2.552 | 274 | 289 | 298 | 295 | 298 | 295 | 295 | 296 | 292 | 285 | 273 | 264 | 23 | 27 | 30 | 35 | 34 | 34 | 33 | 32 | 30 | 25 | 23 | 22 | 692 | 980 | 1393 | 1864 | 2245 | 2501 | 2422 | 2133 | 1765 | 1250 | 816 | 589 | 112 | 138 | 145 | 160 | 141 | 120 | 87 | 81 | 75 | 95 | 73 | 104 | 0.7 | N/A | -1.94 | N/A | -0.68 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | -2.43 | N/A | N/A | N/A | N/A | N/A | 243 | 70 | 36
| RED-BLUFF_STYP20 | 11 | 4 | USA | CA | RED BLUFF | 725910 | 24216 | 40.152 | -122.254 | 353 | 14.51 | -8 | NAP | 95-19 | 3A | 12 | 30.6 | 33.3 | 12.1 | 10.3 | 56.4 | 16.5 | 12.8 | 56.6 | 34.5 | 52.7 | 30 | 50.7 | 4.9 | 320 | 0.486 | 7 | 30.7 | 105.1 | 68.3 | 101.7 | 67.3 | 98.9 | 66.7 | 72.5 | 95 | 70.8 | 93.2 | 69.3 | 91.6 | 8.6 | 150 | 65.2 | 94.3 | 81.6 | 63.2 | 88 | 80.4 | 61.2 | 81.8 | 78.9 | 36.2 | 95.6 | 34.8 | 93 | 33.5 | 91.9 | 79.3 | 26 | 22.1 | 18.7 | 25.6 | 111.2 | 2.9 | 2.4 | 23.5 | 113 | 21.7 | 114.4 | 20.1 | 115.8 | 18 | 117.5 | 23.8 | 75.8 | 3.3 | 2 | 21.4 | 77.2 | 19.5 | 78.4 | 17.6 | 79.5 | 15.2 | 81 | 63.5 | 47.6 | 50.7 | 55 | 59.7 | 68 | 77 | 82.3 | 80.1 | 75 | 64.9 | 53.7 | 47.2 | 13.83 | 5.28 | 5.6 | 6.23 | 7.15 | 7.59 | 7.41 | 5.28 | 4.89 | 6.41 | 6.39 | 6.19 | 5.34 | 336 | 109 | 53 | 21 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 116 | 2483 | 539 | 400 | 314 | 191 | 55 | 6 | 0 | 0 | 5 | 81 | 341 | 551 | 5268 | 35 | 73 | 177 | 296 | 559 | 809 | 1000 | 934 | 751 | 461 | 143 | 30 | 1941 | 0 | 0 | 5 | 32 | 149 | 365 | 535 | 469 | 306 | 77 | 3 | 0 | 26682 | 5 | 14 | 125 | 530 | 2082 | 4996 | 7642 | 6292 | 3882 | 1049 | 65 | 0 | 15219 | 0 | 0 | 19 | 174 | 976 | 2883 | 4787 | 3813 | 2169 | 389 | 9 | 0 | 7.7 | 7.1 | 8.8 | 8.7 | 8.5 | 8.3 | 8.4 | 6.8 | 6.4 | 6.9 | 7.4 | 7 | 7.8 | 22.6 | 4.1 | 3.6 | 3 | 1.4 | 0.8 | 0.4 | 0.1 | 0.2 | 0.5 | 1.3 | 3.3 | 3.7 | 49 | 10.2 | 8.6 | 9.2 | 4.9 | 3.3 | 1.6 | 0.7 | 1.6 | 5 | 5.2 | 8.4 | 10.3 | 7.2 | 0.2 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 0 | 7.6 | 2.5 | 2.8 | 1.9 | 1.3 | 0.9 | 0.5 | 0.2 | 0.4 | 0.9 | 1.4 | 2.4 | 2.5 | 73.5 | 76.4 | 82.6 | 90.1 | 99.4 | 108.4 | 109.9 | 108 | 104.4 | 94.4 | 80.9 | 69.1 | 52 | 56 | 58.5 | 62.3 | 66.4 | 68.5 | 69.6 | 69.9 | 65.7 | 62.7 | 57.7 | 50.7 | 66.8 | 70.7 | 77.4 | 85.1 | 94.3 | 102.8 | 105.3 | 103.1 | 99.4 | 88.4 | 74.9 | 63.3 | 49.8 | 53.2 | 57.1 | 60.2 | 64.5 | 67.1 | 69 | 67.4 | 65 | 60.4 | 56.1 | 49.3 | 61.4 | 65.6 | 73 | 80.6 | 90.1 | 98.5 | 102 | 99.7 | 96.1 | 84.3 | 70.2 | 59.4 | 49.4 | 51 | 55.6 | 59 | 63.1 | 66.1 | 68 | 67.2 | 64 | 59.1 | 54.4 | 49.4 | 56.8 | 61.4 | 68.3 | 75.3 | 85.4 | 94.3 | 98.9 | 96.7 | 92.4 | 80 | 65.2 | 56.5 | 48.5 | 50.3 | 53.7 | 56.8 | 61.3 | 64.8 | 67.7 | 66 | 63.3 | 57.6 | 52.6 | 49.4 | 56.5 | 58.5 | 61.7 | 65.5 | 70 | 74.4 | 74.5 | 75.5 | 71.3 | 65.3 | 61.3 | 57.4 | 61.2 | 67.1 | 74.6 | 82.2 | 90.7 | 95.9 | 97.1 | 98.8 | 91.7 | 85.7 | 73.9 | 60 | 53.7 | 56.3 | 59.3 | 62.5 | 67.3 | 71 | 72.7 | 71.6 | 68.2 | 63.1 | 58.8 | 55 | 58.3 | 64.6 | 72.2 | 79.6 | 88.3 | 92.5 | 95.9 | 93.5 | 89.6 | 82.7 | 68.5 | 57.3 | 52.2 | 54.2 | 57.4 | 60.4 | 65.1 | 68.8 | 71.1 | 69.7 | 66.4 | 61.4 | 56.8 | 53.1 | 57 | 61.6 | 68.6 | 76.2 | 85.4 | 90.5 | 94.2 | 91.4 | 88.9 | 78.4 | 65 | 55.7 | 50.7 | 52.3 | 55.4 | 58.4 | 63 | 67.1 | 69.7 | 68.1 | 64.8 | 59.6 | 55 | 51.1 | 55.8 | 59.1 | 65.6 | 72 | 81.7 | 89.4 | 92.9 | 90.2 | 87.8 | 75.1 | 62.3 | 54.4 | 17.1 | 18.4 | 21 | 23.2 | 25.7 | 27.6 | 30.7 | 31.1 | 30.2 | 26 | 20.1 | 16.5 | 27.8 | 27.7 | 29.6 | 31.8 | 33.2 | 33.1 | 34.6 | 35 | 35.3 | 33 | 28.8 | 23.9 | 14.8 | 14.1 | 14.3 | 13.6 | 12.3 | 11.2 | 11.1 | 11.9 | 12.5 | 13.5 | 13.8 | 13.6 | 17.9 | 20.4 | 25.4 | 29.1 | 30.7 | 30.3 | 31.1 | 31.1 | 31 | 28 | 22.3 | 12.9 | 11 | 11.5 | 13.4 | 13.5 | 12 | 11.4 | 10.9 | 11.4 | 11.6 | 12.3 | 11.6 | 9.1 | 0.314 | 0.316 | 0.336 | 0.351 | 0.341 | 0.349 | 0.354 | 0.337 | 0.339 | 0.329 | 0.31 | 0.314 | 2.528 | 2.53 | 2.478 | 2.428 | 2.497 | 2.478 | 2.452 | 2.494 | 2.48 | 2.522 | 2.553 | 2.527 | 271 | 288 | 292 | 293 | 297 | 293 | 290 | 294 | 287 | 279 | 271 | 262 | 23 | 27 | 31 | 35 | 34 | 34 | 35 | 33 | 31 | 27 | 23 | 22 | 658 | 949 | 1346 | 1833 | 2258 | 2572 | 2608 | 2320 | 1855 | 1262 | 774 | 557 | 121 | 135 | 169 | 184 | 161 | 140 | 82 | 80 | 75 | 108 | 81 | 111 | 1.06 | N/A | -2.29 | N/A | N/A | N/A | -74 | -257 | 364 | 202 | 0.67 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 209 | 49 | 23
| REDDING_STYP20 | 11 | 4 | USA | CA | REDDING | 725920 | 24257 | 40.518 | -122.299 | 497 | 14.43 | -8 | NAP | 94-19 | 3A | 12 | 29.4 | 31.8 | 11.1 | 9.9 | 55.2 | 15.5 | 12.3 | 55.7 | 34.1 | 51.7 | 28.7 | 52.8 | 1.2 | 30 | 0.459 | 7 | 31 | 105.4 | 68 | 102.4 | 67.1 | 99.4 | 66 | 71.4 | 96.5 | 69.9 | 94.5 | 68.5 | 92.7 | 7.8 | 160 | 63.5 | 89.4 | 79.4 | 61.4 | 82.8 | 78.3 | 59.5 | 77.3 | 77 | 35.4 | 97.3 | 34.1 | 94.1 | 32.9 | 93 | 76.8 | 25.4 | 20 | 16.8 | 24.5 | 111.2 | 3.2 | 2.7 | 22.1 | 113.1 | 20.2 | 114.6 | 18.4 | 116.1 | 16.1 | 118 | 22.9 | 74.1 | 3.1 | 1.6 | 20.7 | 75.2 | 18.8 | 76.2 | 17.1 | 77.1 | 14.8 | 78.3 | 63.2 | 47.4 | 50.1 | 54.4 | 59.1 | 67.7 | 76.8 | 83 | 80.6 | 74.9 | 64.2 | 52.7 | 46.6 | 14.26 | 5.59 | 6.04 | 6.55 | 7.4 | 7.8 | 7.83 | 5.32 | 4.92 | 6.36 | 6.66 | 6.42 | 5.56 | 399 | 116 | 67 | 29 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 135 | 2619 | 545 | 419 | 334 | 207 | 63 | 8 | 0 | 0 | 6 | 96 | 370 | 571 | 5218 | 37 | 68 | 165 | 282 | 550 | 804 | 1023 | 948 | 747 | 439 | 126 | 29 | 1961 | 0 | 1 | 6 | 30 | 147 | 362 | 558 | 483 | 302 | 70 | 2 | 0 | 27663 | 6 | 17 | 124 | 505 | 1980 | 4967 | 8084 | 6758 | 4079 | 1074 | 68 | 1 | 15939 | 0 | 1 | 19 | 161 | 904 | 2852 | 5123 | 4161 | 2298 | 409 | 11 | 0 | 5.8 | 5.2 | 6.6 | 6.6 | 6.5 | 6.5 | 6.7 | 5.6 | 5.1 | 5.2 | 5.5 | 4.6 | 5.4 | 37.9 | 7 | 5.7 | 5.2 | 2.5 | 1.6 | 0.7 | 0.1 | 0.4 | 0.9 | 2 | 5.2 | 6.6 | 73.1 | 27 | 15.8 | 16.4 | 9.2 | 7.7 | 2.6 | 3.3 | 5.5 | 7.4 | 8.8 | 16.2 | 17.7 | 20.1 | 0.3 | 0.2 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 11.1 | 5.3 | 4.1 | 3.7 | 2 | 1.9 | 0.7 | 0.5 | 0.9 | 1.5 | 1.9 | 3.9 | 4.6 | 74.2 | 76.8 | 82.7 | 89.7 | 98.7 | 108.1 | 110.3 | 108.4 | 104.3 | 95.2 | 81.1 | 69.3 | 52.2 | 55.9 | 58.2 | 61 | 65.2 | 68.5 | 69.5 | 69.1 | 65.4 | 62.4 | 57.7 | 50.4 | 67.9 | 71.1 | 77.5 | 84.8 | 93.7 | 102.6 | 106 | 103.9 | 99.9 | 88.8 | 75 | 63.9 | 50.1 | 52.9 | 56.9 | 59.8 | 64.4 | 67.2 | 68.7 | 67.2 | 64.1 | 60.8 | 56.1 | 48.9 | 62.2 | 66.3 | 73 | 80.2 | 89.6 | 98.4 | 102.9 | 100.5 | 96.5 | 84.5 | 70.2 | 59.8 | 48.9 | 51.1 | 55 | 58.6 | 62.6 | 65.7 | 67.9 | 66.2 | 63.6 | 58.9 | 54.2 | 48.7 | 57.8 | 61.6 | 68.3 | 75 | 85 | 94.3 | 99.7 | 97.5 | 93 | 80.1 | 65.1 | 56.4 | 48 | 49.7 | 53 | 56.6 | 61 | 64.4 | 66.9 | 65.3 | 63 | 57.5 | 52 | 48.7 | 56.3 | 58.3 | 60.9 | 64.9 | 69.2 | 72.7 | 73.6 | 72.6 | 71.1 | 64.9 | 61.2 | 57.1 | 62.2 | 68 | 75.3 | 82.4 | 89 | 95.9 | 99 | 100.5 | 91 | 87 | 74.6 | 59.4 | 53.7 | 56.3 | 58.8 | 62.1 | 66.5 | 70 | 71.8 | 70.3 | 67.8 | 62.9 | 58.6 | 54.5 | 59.2 | 64.9 | 72.4 | 79.4 | 87.6 | 93.6 | 98.1 | 95.3 | 91.1 | 83.4 | 69.4 | 57.2 | 52 | 54 | 56.9 | 59.9 | 64.6 | 68.1 | 70.4 | 68.6 | 65.9 | 61.1 | 56.5 | 52.6 | 57.4 | 62 | 68.7 | 76.1 | 85.1 | 92.2 | 96.1 | 93.2 | 89.6 | 79.3 | 65.3 | 55.6 | 50.6 | 51.9 | 54.8 | 57.9 | 62.7 | 66.3 | 69 | 67.2 | 64.2 | 59.3 | 54.7 | 50.5 | 56.3 | 58.8 | 65.3 | 72.1 | 81.4 | 89.6 | 93.9 | 91.4 | 88.4 | 75.3 | 62 | 54.6 | 17.7 | 18.6 | 20.7 | 22.9 | 25.3 | 27.6 | 31 | 32.2 | 31.1 | 26.7 | 20.8 | 16.7 | 29.7 | 28.5 | 29.5 | 31.5 | 32.6 | 32.5 | 34.7 | 35.9 | 37 | 34.6 | 30.6 | 25.2 | 15.6 | 14.5 | 13.8 | 13 | 10.8 | 9.6 | 9.5 | 10.3 | 11.8 | 13.4 | 14.9 | 14.3 | 19.7 | 21.8 | 25.4 | 28.7 | 29.8 | 30.8 | 31.9 | 32.5 | 32.4 | 30 | 24.3 | 13.9 | 11.8 | 12.2 | 12.9 | 12.7 | 10.8 | 9.9 | 9.4 | 10 | 11.1 | 12.4 | 12.8 | 9.6 | 0.313 | 0.319 | 0.329 | 0.347 | 0.351 | 0.35 | 0.354 | 0.341 | 0.339 | 0.329 | 0.309 | 0.314 | 2.535 | 2.524 | 2.508 | 2.443 | 2.471 | 2.488 | 2.473 | 2.5 | 2.494 | 2.533 | 2.566 | 2.528 | 271 | 286 | 294 | 294 | 294 | 292 | 291 | 292 | 286 | 278 | 271 | 260 | 23 | 27 | 30 | 35 | 35 | 34 | 34 | 32 | 30 | 26 | 22 | 22 | 642 | 927 | 1313 | 1803 | 2233 | 2555 | 2599 | 2309 | 1840 | 1242 | 751 | 539 | 122 | 134 | 174 | 186 | 165 | 145 | 83 | 82 | 76 | 113 | 86 | 113 | 0.92 | N/A | -2.66 | N/A | N/A | N/A | -67 | -167 | 299 | 184 | N/A | N/A | N/A | 0.76 | N/A | N/A | N/A | N/A | 184 | 47 | 16
| SALINAS_STYP20 | 3 | 4 | USA | CA | SALINAS | 725930 | 23233 | 36.664 | -121.608 | 74 | 14.66 | -8 | NAP | 94-19 | 3C | 12 | 34.3 | 36.7 | 21.6 | 16.3 | 51.9 | 25.6 | 19.7 | 48.7 | 26.9 | 55.9 | 24.6 | 55.1 | 5.1 | 120 | 0.525 | 9 | 18.1 | 83.6 | 61.9 | 79 | 61 | 75.3 | 60.6 | 65 | 77.8 | 63.6 | 74.8 | 62.4 | 72.5 | 9.3 | 300 | 60.6 | 79.3 | 67.5 | 59.1 | 75.1 | 66.4 | 58.1 | 72.2 | 65.5 | 29.8 | 77.8 | 28.9 | 74.9 | 28 | 72.6 | 80.6 | 20.9 | 18.6 | 17 | 30.1 | 94.5 | 2.7 | 4.4 | 28.1 | 97.7 | 26.5 | 100.3 | 25 | 102.8 | 23 | 106 | 28.2 | 69.3 | 2.8 | 3.2 | 26.2 | 71.6 | 24.5 | 73.4 | 23 | 75.2 | 21 | 77.5 | 58.1 | 52.3 | 53.1 | 55.3 | 56.6 | 59 | 61.4 | 62.6 | 63.7 | 63.9 | 61.3 | 56.2 | 51.4 | 6.14 | 5.09 | 5.06 | 4.71 | 4.64 | 3.69 | 3.44 | 2.77 | 2.98 | 4.04 | 4.89 | 5.33 | 4.86 | 117 | 34 | 21 | 9 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 41 | 2641 | 393 | 334 | 304 | 257 | 193 | 120 | 85 | 62 | 66 | 139 | 268 | 420 | 3075 | 106 | 108 | 172 | 202 | 280 | 341 | 392 | 424 | 418 | 350 | 196 | 86 | 122 | 0 | 1 | 2 | 5 | 7 | 11 | 12 | 21 | 34 | 24 | 5 | 0 | 1131 | 12 | 21 | 40 | 86 | 94 | 117 | 57 | 101 | 267 | 264 | 68 | 4 | 331 | 1 | 1 | 7 | 29 | 30 | 38 | 9 | 23 | 85 | 92 | 16 | 0 | 7.8 | 7.4 | 7.7 | 7.5 | 8.1 | 9 | 9.3 | 8.6 | 8 | 7.2 | 6.7 | 6.6 | 7.4 | 12.4 | 2.4 | 2.2 | 2 | 1 | 0.2 | 0.1 | 0 | 0 | 0.2 | 0.5 | 1.7 | 2 | 23.7 | 7.9 | 10 | 6 | 5.7 | 1.9 | 0.6 | 0.6 | 0.7 | 1.2 | 1.9 | 4.8 | 5.1 | 6.4 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.5 | 2 | 2.2 | 1.5 | 1.1 | 0.4 | 0.1 | 0.1 | 0.1 | 0.4 | 0.6 | 1.4 | 1.3 | 75.1 | 77.5 | 79 | 84 | 84 | 85 | 79.8 | 82.5 | 89.6 | 89.5 | 81.8 | 72 | 55.1 | 58.6 | 59.6 | 61.8 | 62.8 | 63.3 | 64.4 | 64.6 | 64.3 | 62.8 | 59.4 | 52.9 | 69.2 | 70.7 | 72.4 | 74.2 | 74.9 | 76.3 | 74.7 | 76 | 81.2 | 81.2 | 73.9 | 66.4 | 54.5 | 56.7 | 57.4 | 58.5 | 60.2 | 61.6 | 62.5 | 63.2 | 62.8 | 59.8 | 57.1 | 54 | 64.3 | 65.4 | 67.8 | 69 | 69.9 | 71.8 | 71.8 | 72.9 | 75.7 | 75 | 68.9 | 63.1 | 54.3 | 54.7 | 56.1 | 56.8 | 58.4 | 60.1 | 61.6 | 62.3 | 62 | 58.6 | 56 | 53.6 | 60.8 | 61.8 | 64 | 65 | 66.3 | 68.8 | 69.3 | 70.4 | 72.1 | 70.4 | 65 | 60.1 | 53.5 | 53.5 | 54.8 | 55.2 | 56.9 | 59 | 60.4 | 61.1 | 61.1 | 58 | 55.3 | 52.8 | 60.3 | 62.2 | 62 | 63.4 | 65 | 65.7 | 65.4 | 66.1 | 67.1 | 65.2 | 62.4 | 60.6 | 65.2 | 71.2 | 75.6 | 77.3 | 79.1 | 81.4 | 78 | 78.6 | 81.7 | 78.6 | 73.5 | 65 | 57.7 | 58.9 | 59.3 | 60.2 | 61.4 | 62.5 | 63.2 | 64.1 | 64.5 | 62.7 | 60.1 | 58.2 | 62.9 | 66.3 | 68.4 | 70.9 | 72.1 | 74.1 | 73.3 | 74.6 | 76.6 | 74.6 | 69.1 | 62 | 55.9 | 56.7 | 57.4 | 58.1 | 59.3 | 60.8 | 61.9 | 62.7 | 63 | 61.1 | 58.5 | 56.1 | 61.4 | 63.7 | 64.7 | 67.2 | 68.3 | 70.2 | 71 | 71.9 | 73.4 | 71.3 | 66 | 59.8 | 54.2 | 54.7 | 55.7 | 56.1 | 57.5 | 59.4 | 60.6 | 61.6 | 61.7 | 59.5 | 56.9 | 54.2 | 59.6 | 60.5 | 62.5 | 63.9 | 65.3 | 67.7 | 68.3 | 70 | 71.1 | 67.8 | 63.3 | 58.3 | 18.7 | 18.3 | 19.4 | 18.5 | 15.8 | 15.5 | 14.3 | 15.2 | 18.1 | 21.6 | 20.7 | 18.7 | 24.5 | 25.3 | 26.3 | 26.8 | 24.3 | 22.6 | 18.6 | 19.6 | 26.7 | 30.7 | 26.7 | 23.1 | 13.6 | 13.5 | 13.5 | 13.6 | 11.7 | 10.8 | 8.7 | 8.9 | 12 | 14 | 13.5 | 13.3 | 18.4 | 20.8 | 21.9 | 23.7 | 21 | 20 | 17.4 | 18.5 | 22.1 | 24.8 | 21.6 | 15.3 | 11.3 | 11.8 | 12 | 12.7 | 10.7 | 9.9 | 8.3 | 8.6 | 10.3 | 12.1 | 11.8 | 10.1 | 0.318 | 0.323 | 0.325 | 0.349 | 0.36 | 0.347 | 0.354 | 0.339 | 0.345 | 0.329 | 0.311 | 0.312 | 2.544 | 2.538 | 2.533 | 2.446 | 2.43 | 2.476 | 2.476 | 2.507 | 2.486 | 2.554 | 2.571 | 2.575 | 279 | 291 | 300 | 296 | 292 | 295 | 292 | 295 | 289 | 285 | 279 | 274 | 25 | 28 | 31 | 35 | 36 | 35 | 35 | 33 | 32 | 27 | 24 | 23 | 836 | 1112 | 1565 | 1981 | 2309 | 2527 | 2399 | 2170 | 1839 | 1369 | 965 | 737 | 91 | 122 | 129 | 167 | 123 | 88 | 60 | 65 | 56 | 77 | 50 | 91 | 0.74 | N/A | -2.43 | N/A | N/A | N/A | N/A | -317 | 301 | N/A | 0.74 | N/A | -2.16 | N/A | N/A | N/A | N/A | -229 | 270 | 67 | 40
| WOODLEY-ISLAND_STYP20 | 1 | 4 | USA | CA | WOODLEY ISLAND | 725940 | 24213 | 40.8097 | -124.16 | 20 | 14.69 | -8 | NAP | 94-19 | 4C | 12 | 33.1 | 35.4 | 26.9 | 20.9 | 41.8 | 30 | 24 | 40.5 | 26.1 | 57.3 | 22.4 | 53.9 | 3.2 | 90 | 0.539 | 8 | 8.6 | 68.9 | 59.1 | 66.4 | 58.9 | 64.5 | 58.2 | 61.6 | 66.2 | 60.3 | 64.5 | 59.3 | 63.2 | 9.4 | 340 | 59.6 | 76.3 | 63.2 | 58.4 | 73.1 | 62 | 57.4 | 70.3 | 61 | 27.4 | 66.5 | 26.6 | 64.8 | 25.9 | 63.3 | 67.6 | 20.4 | 18.2 | 16.3 | 29.4 | 78.5 | 1.6 | 4.9 | 28.3 | 82 | 27.3 | 84.8 | 26.4 | 87.5 | 25.3 | 91.1 | 28.5 | 63.8 | 1.6 | 1.8 | 27.3 | 65.1 | 26.4 | 66.2 | 25.4 | 67.2 | 24.2 | 68.5 | 51.8 | 47.8 | 47.7 | 48.5 | 49.7 | 52.1 | 54.9 | 56.7 | 57.3 | 55.9 | 53.5 | 49.9 | 47.4 | 5.43 | 5.11 | 4.76 | 4.13 | 3.8 | 3.38 | 2.7 | 2.6 | 2.9 | 3.88 | 4.25 | 4.75 | 5.42 | 534 | 103 | 94 | 78 | 49 | 16 | 1 | 0 | 0 | 1 | 14 | 59 | 119 | 4818 | 533 | 485 | 511 | 458 | 400 | 303 | 258 | 240 | 275 | 356 | 452 | 547 | 1193 | 35 | 29 | 32 | 41 | 81 | 148 | 207 | 226 | 177 | 123 | 57 | 37 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 1 | 1 | 2 | 1 | 2 | 11 | 5 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 6 | 5.6 | 6.1 | 6.9 | 7.1 | 6.9 | 6.8 | 5.8 | 5.2 | 4.9 | 4.9 | 5.1 | 6.1 | 39.1 | 6.4 | 5.2 | 5.4 | 3.2 | 1.7 | 0.6 | 0.2 | 0.4 | 0.7 | 2.4 | 6.1 | 7.1 | 67.2 | 13.9 | 13.9 | 11.2 | 11.3 | 6.1 | 3.1 | 1.1 | 3.4 | 3.3 | 6.8 | 16.6 | 23.3 | 21.7 | 0.7 | 0.6 | 1.2 | 0.4 | 0.1 | 0 | 0 | 0 | 0 | 0 | 1.3 | 0.5 | 10.1 | 3.3 | 2.8 | 2.7 | 2.3 | 1.2 | 0.6 | 0.2 | 0.7 | 0.8 | 1.8 | 3.8 | 4.7 | 64 | 65.2 | 64.4 | 67.2 | 69 | 67.6 | 68 | 69.8 | 73.7 | 72.4 | 66.5 | 63.1 | 54.2 | 54.9 | 53.5 | 55.1 | 59.2 | 58.6 | 60.2 | 61.1 | 61.1 | 57.8 | 55.7 | 54.9 | 60.5 | 60.8 | 60 | 61.3 | 62.7 | 63.4 | 65 | 66.9 | 67.9 | 66.8 | 62.2 | 60.4 | 53.5 | 54 | 53.1 | 54.5 | 57 | 57.2 | 59.3 | 60.4 | 60.2 | 57.6 | 55.8 | 54.4 | 58.2 | 58 | 57.5 | 58 | 59.7 | 61.6 | 63.2 | 65 | 65.3 | 63.5 | 59.8 | 58.2 | 53 | 52.4 | 52 | 52.9 | 55.1 | 56.5 | 58.3 | 59.6 | 59 | 57.2 | 55.1 | 53.6 | 56.1 | 55.5 | 55.5 | 56.1 | 58 | 60.2 | 61.8 | 63 | 63.1 | 61.3 | 58 | 56.3 | 52.1 | 51 | 51.2 | 51.6 | 53.9 | 55.6 | 57.6 | 58.5 | 58 | 56 | 54 | 52.5 | 57.6 | 58 | 56.6 | 58.2 | 61.2 | 60.7 | 62 | 62.8 | 63.3 | 62.2 | 59.4 | 58.2 | 59.9 | 61.5 | 60.3 | 63.6 | 66.5 | 65.5 | 65.9 | 67.1 | 70.1 | 66.2 | 62.1 | 60.4 | 55.7 | 55.7 | 54.7 | 55.3 | 57.8 | 58.8 | 60.1 | 61.3 | 61.3 | 59.9 | 57.8 | 56.5 | 58.5 | 59.4 | 57.8 | 59.3 | 61.6 | 62 | 63.8 | 65.8 | 66 | 64.1 | 60.4 | 58.7 | 54.2 | 53.5 | 53.2 | 53.7 | 55.8 | 57.3 | 58.9 | 60 | 59.9 | 58.5 | 56.3 | 54.9 | 57 | 56.3 | 56.2 | 56.9 | 59.1 | 60.5 | 62.4 | 64.1 | 64.1 | 62.2 | 58.8 | 57.4 | 52.6 | 51.8 | 51.8 | 52.4 | 54.4 | 56.2 | 57.8 | 58.9 | 58.7 | 56.8 | 54.7 | 53 | 55.4 | 54.7 | 54.7 | 55.6 | 57.3 | 59.3 | 61.1 | 62.5 | 62.4 | 60.3 | 57.2 | 55.5 | 10.9 | 11.2 | 10.9 | 10.6 | 9.4 | 9.7 | 8.3 | 8.6 | 11.4 | 12.2 | 11.3 | 11.1 | 13.1 | 14.5 | 13.6 | 14.2 | 12.6 | 12.5 | 11.1 | 12.8 | 16.9 | 16.9 | 13.5 | 11.6 | 8.3 | 8.8 | 8.3 | 8.7 | 7.9 | 7.6 | 6.4 | 7.4 | 9.3 | 9.6 | 8.4 | 7.6 | 9.3 | 10.6 | 10.9 | 12 | 11 | 10.7 | 10.2 | 11.5 | 14 | 13 | 9.9 | 7.8 | 7.3 | 7.6 | 7.7 | 8.1 | 7.5 | 7 | 6.1 | 7 | 8.3 | 8.8 | 7.3 | 6.7 | 0.327 | 0.334 | 0.337 | 0.36 | 0.365 | 0.355 | 0.368 | 0.355 | 0.346 | 0.34 | 0.321 | 0.331 | 2.535 | 2.521 | 2.531 | 2.428 | 2.453 | 2.492 | 2.461 | 2.501 | 2.503 | 2.55 | 2.582 | 2.521 | 265 | 280 | 291 | 290 | 289 | 291 | 286 | 287 | 284 | 274 | 265 | 252 | 23 | 27 | 30 | 35 | 35 | 34 | 35 | 32 | 30 | 26 | 22 | 22 | 597 | 857 | 1241 | 1701 | 2077 | 2313 | 2271 | 1963 | 1621 | 1107 | 683 | 493 | 93 | 121 | 126 | 152 | 133 | 133 | 112 | 99 | 84 | 93 | 74 | 91 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.92 | N/A | N/A | N/A | N/A | 212 | 9 | 12
| CALIFORNIA-REDWOOD-COAST_STYP20 | 1 | 4 | USA | CA | CALIFORNIA REDWOOD COAST | 725945 | 24283 | 40.978 | -124.109 | 200 | 14.59 | -8 | NAP | 94-19 | 4C | 12 | 31.4 | 33.6 | 26 | 20.1 | 41.5 | 29.1 | 23.3 | 38.9 | 24.6 | 54.4 | 21.2 | 53.3 | 3.5 | 90 | 0.555 | 8 | 11.4 | 70.9 | 59.4 | 67.9 | 59.3 | 65.7 | 58.4 | 62.4 | 67.1 | 61.1 | 65.6 | 60 | 63.9 | 9.7 | 340 | 60.7 | 80 | 63.7 | 59.2 | 75.6 | 62.3 | 58.1 | 72.7 | 61.3 | 28.1 | 67.6 | 27.1 | 65.5 | 26.4 | 64 | 68.9 | 20.2 | 18.3 | 16.4 | 27.9 | 81.9 | 2.1 | 5 | 26.4 | 85.5 | 25.2 | 88.5 | 24 | 91.3 | 22.5 | 95 | 27.2 | 65.1 | 2.2 | 1.8 | 25.6 | 66.4 | 24.3 | 67.4 | 23 | 68.4 | 21.4 | 69.7 | 52.1 | 48.2 | 48 | 48.6 | 49.7 | 52.4 | 55.1 | 57 | 57.4 | 56.3 | 53.7 | 50.5 | 47.7 | 5.53 | 5.29 | 5 | 4.2 | 3.93 | 3.64 | 2.89 | 2.65 | 2.73 | 3.83 | 4.52 | 5.06 | 5.46 | 515 | 98 | 90 | 78 | 51 | 15 | 1 | 0 | 0 | 1 | 14 | 55 | 112 | 4725 | 521 | 477 | 510 | 460 | 390 | 298 | 249 | 235 | 261 | 351 | 436 | 537 | 1268 | 42 | 33 | 33 | 41 | 90 | 153 | 216 | 231 | 191 | 129 | 69 | 40 | 3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 62 | 0 | 0 | 0 | 3 | 10 | 4 | 3 | 3 | 19 | 19 | 1 | 0 | 13 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 1 | 4 | 5 | 0 | 0 | 6.1 | 6.1 | 6.5 | 6.9 | 6.9 | 6.8 | 6.8 | 5.8 | 5.2 | 4.9 | 5 | 5.5 | 6.4 | 46.4 | 7.9 | 5.7 | 6.5 | 4 | 1.9 | 0.9 | 0.2 | 0.2 | 0.7 | 2.7 | 5.7 | 10.2 | 74.1 | 16.3 | 15.1 | 14.1 | 12.4 | 5.1 | 3.5 | 0.9 | 0.7 | 3.9 | 11.5 | 16 | 24.2 | 21.7 | 1.9 | 0.7 | 2.1 | 1.3 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 1.1 | 11.9 | 4.2 | 3.3 | 3.5 | 2.5 | 1.5 | 0.9 | 0.2 | 0.2 | 0.9 | 2.5 | 3.3 | 5.6 | 66.1 | 66.4 | 65.6 | 69.7 | 72.8 | 70.4 | 70.2 | 71.3 | 76.5 | 75.1 | 69 | 65 | 54 | 55.1 | 54.5 | 56.4 | 60.3 | 60.2 | 60.7 | 61.2 | 61.8 | 58 | 56.8 | 54.1 | 61.6 | 61.7 | 61.1 | 62.2 | 63.8 | 64.9 | 66.1 | 67.8 | 69.5 | 68.4 | 63.6 | 61.4 | 53.6 | 53.3 | 53.4 | 55.3 | 58.4 | 57.9 | 59.9 | 61 | 60.4 | 57.7 | 56.2 | 54.1 | 58.8 | 58.5 | 58.2 | 58.6 | 60.8 | 62.9 | 63.9 | 65.5 | 66.3 | 64.4 | 61 | 58.8 | 53.2 | 52.9 | 52.9 | 53.4 | 55.9 | 57.4 | 58.8 | 60 | 59.4 | 56.8 | 55.1 | 53.6 | 56.6 | 55.9 | 56 | 56.5 | 58.7 | 61 | 62.4 | 63.3 | 63.9 | 61.8 | 58.5 | 56.6 | 52.4 | 51.4 | 51.6 | 52.2 | 54.5 | 56.3 | 58.1 | 59 | 58.4 | 56.2 | 54.4 | 52.6 | 58.4 | 58.6 | 57.8 | 59.1 | 63.8 | 61.5 | 62.8 | 63.8 | 64.1 | 62.5 | 60.4 | 58.5 | 60.8 | 62.8 | 61.1 | 64.7 | 67.6 | 67.5 | 66.4 | 67.6 | 71.2 | 67.9 | 63.9 | 60.9 | 56.3 | 56.1 | 55.3 | 56.1 | 58.9 | 59.5 | 60.9 | 62 | 62 | 60.3 | 58.5 | 56.8 | 59.1 | 59.3 | 58.9 | 60.4 | 63.3 | 63.4 | 64.8 | 66.1 | 67.4 | 64.9 | 61.4 | 59.2 | 54.6 | 54 | 53.7 | 54.4 | 56.7 | 58.2 | 59.5 | 60.5 | 60.4 | 58.7 | 56.8 | 54.9 | 57.4 | 56.9 | 56.7 | 57.5 | 60.1 | 61.7 | 63 | 64.2 | 64.9 | 62.9 | 59.5 | 57.5 | 53.1 | 52.1 | 52.3 | 53 | 55 | 57 | 58.4 | 59.3 | 59.1 | 57 | 55 | 53.3 | 55.7 | 55 | 55.2 | 55.8 | 58 | 60.2 | 61.7 | 62.7 | 63 | 60.8 | 57.6 | 55.8 | 14.3 | 14.2 | 13.9 | 13.4 | 12.2 | 12.5 | 10.5 | 11.4 | 14.6 | 16.3 | 14.6 | 14.4 | 16.9 | 17.6 | 16.8 | 16.7 | 16.3 | 15.9 | 13.4 | 16 | 19.6 | 21.2 | 16.5 | 16.4 | 10.7 | 10.9 | 11 | 10.9 | 10.5 | 10 | 8.1 | 9.7 | 11.3 | 12.2 | 10.3 | 10.9 | 13 | 14.2 | 14.4 | 14.7 | 14.4 | 13.8 | 12.3 | 13.9 | 16.9 | 17.8 | 13.3 | 11.8 | 9.4 | 9.8 | 10.4 | 10.2 | 9.8 | 9.1 | 7.7 | 8.8 | 10.4 | 11.4 | 9.3 | 9.3 | 0.323 | 0.328 | 0.333 | 0.355 | 0.361 | 0.352 | 0.364 | 0.353 | 0.342 | 0.336 | 0.317 | 0.325 | 2.544 | 2.535 | 2.544 | 2.442 | 2.467 | 2.502 | 2.473 | 2.51 | 2.514 | 2.562 | 2.59 | 2.536 | 266 | 282 | 292 | 291 | 290 | 292 | 287 | 288 | 285 | 275 | 266 | 254 | 23 | 27 | 29 | 35 | 35 | 34 | 34 | 32 | 30 | 26 | 22 | 22 | 591 | 852 | 1234 | 1693 | 2079 | 2318 | 2290 | 1978 | 1624 | 1104 | 676 | 489 | 93 | 122 | 128 | 155 | 133 | 135 | 111 | 102 | 86 | 96 | 75 | 91 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.95 | N/A | N/A | N/A | N/A | 202 | 25 | 15
| CRESCENT-CITY-DEL-NORTE_STYP20 | 1 | 4 | USA | CA | CRESCENT CITY DEL NORTE | 725946 | 24286 | 41.78 | -124.237 | 57 | 14.67 | -8 | NAP | 94-19 | 4C | 12 | 35 | 36.7 | 23.8 | 18 | 43.4 | 27.9 | 21.9 | 43.6 | 34.3 | 52.5 | 31.3 | 52.7 | 4.6 | 90 | 0.596 | 8 | 9.4 | 67.7 | 59.2 | 65.5 | 58.8 | 63.7 | 57.8 | 61.4 | 65.3 | 60.1 | 63.8 | 59.1 | 62.6 | 8.5 | 190 | 59.4 | 75.9 | 62.5 | 58.3 | 72.8 | 61.4 | 57.2 | 70 | 60.4 | 27.2 | 65.3 | 26.4 | 63.9 | 25.7 | 62.6 | 68.5 | 27.6 | 24.5 | 20.8 | 31.4 | 77.6 | 2.2 | 4.1 | 29.8 | 80.6 | 28.5 | 83 | 27.3 | 85.3 | 25.7 | 88.3 | 29.2 | 63.8 | 2.4 | 2 | 27.5 | 65.3 | 26.1 | 66.4 | 24.7 | 67.6 | 22.9 | 69 | 52.2 | 48.5 | 48.3 | 48.7 | 49.9 | 52.5 | 54.7 | 56.7 | 57.6 | 56.5 | 53.9 | 50.9 | 48 | 4.98 | 4.43 | 4.34 | 3.61 | 3.29 | 3 | 2.58 | 2.41 | 2.63 | 3.24 | 3.96 | 4.09 | 4.54 | 413 | 80 | 77 | 68 | 40 | 8 | 1 | 0 | 0 | 0 | 8 | 37 | 94 | 4674 | 510 | 469 | 505 | 454 | 387 | 310 | 256 | 230 | 257 | 345 | 423 | 528 | 1213 | 35 | 28 | 27 | 35 | 86 | 140 | 209 | 235 | 194 | 129 | 64 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 1 | 1 | 2 | 0 | 0 | 3 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4 | 9.1 | 9.5 | 9.8 | 9.3 | 8.6 | 8.6 | 6.9 | 6.4 | 6.9 | 7.5 | 8.3 | 9.5 | 75 | 11.8 | 9.4 | 9.3 | 6.9 | 3.8 | 1.7 | 0.4 | 0.6 | 1.1 | 4.7 | 10.3 | 15 | 115.6 | 23.5 | 21.4 | 19.1 | 15.9 | 8.4 | 5.7 | 1.7 | 2.1 | 5.4 | 9.8 | 25.2 | 35 | 45.2 | 3.7 | 2.7 | 3.8 | 1.7 | 0 | 0.1 | 0 | 0 | 0 | 0.4 | 3.1 | 4.5 | 18 | 5.7 | 5 | 4.3 | 3.8 | 2.2 | 1.5 | 0.4 | 0.6 | 1.3 | 2.8 | 5.2 | 7.5 | 63.5 | 63.8 | 62.5 | 66 | 68.1 | 65.8 | 67.1 | 68.6 | 70.4 | 73 | 64.6 | 62.1 | 51.3 | 52.3 | 52.3 | 55.2 | 57.9 | 59.7 | 60.4 | 61.5 | 60.4 | 57.2 | 55.1 | 52.5 | 59 | 59 | 58.2 | 59 | 61.5 | 62.9 | 64.4 | 66.2 | 66.2 | 65.7 | 61.1 | 58.7 | 51.4 | 52.1 | 52.2 | 53.1 | 56.1 | 57.3 | 59 | 60.5 | 59.8 | 56.1 | 54.1 | 53 | 56.7 | 56.5 | 56.2 | 56.8 | 59.2 | 61.2 | 63.1 | 64.3 | 64.1 | 62.6 | 58.9 | 56.7 | 51.5 | 51.4 | 51.5 | 51.9 | 54.9 | 56.4 | 58.2 | 59.3 | 58.5 | 55.8 | 53.8 | 52.4 | 55 | 54.6 | 54.6 | 55.2 | 57.3 | 59.7 | 61.5 | 62.9 | 62.7 | 60.5 | 57.1 | 54.9 | 51.2 | 50.6 | 50.7 | 51.1 | 53.4 | 55.4 | 57.2 | 58.4 | 57.6 | 55.5 | 53.1 | 51.4 | 55.9 | 56.1 | 55.4 | 57 | 59.8 | 60.5 | 62.2 | 62.6 | 62.6 | 60.6 | 58.6 | 57.3 | 58.6 | 59.9 | 58.7 | 63.4 | 65 | 64.4 | 65.4 | 66.3 | 66.8 | 65.3 | 61.1 | 58.5 | 54.2 | 54.1 | 53.8 | 54.3 | 57.1 | 58.4 | 60.1 | 61.3 | 60.8 | 59 | 56.8 | 55.4 | 56.2 | 56.9 | 55.9 | 57.1 | 60.9 | 61.4 | 63.4 | 65 | 64.6 | 62.8 | 59 | 57.3 | 53.2 | 52.7 | 52.7 | 53.1 | 55.4 | 57.2 | 58.9 | 60 | 59.5 | 57.6 | 55.3 | 53.8 | 55.2 | 55.3 | 54.9 | 55.5 | 58.8 | 60.2 | 62.2 | 63.7 | 63 | 61.1 | 57.4 | 55.3 | 51.9 | 51.3 | 51.4 | 51.9 | 54.2 | 56.1 | 57.8 | 58.8 | 58.4 | 56.2 | 54.1 | 52.3 | 54.5 | 53.6 | 54 | 54.5 | 56.8 | 59.1 | 61 | 62.3 | 61.7 | 59.5 | 56.2 | 54.2 | 11.1 | 10.9 | 10.8 | 10.4 | 9.8 | 10.1 | 8.9 | 9.4 | 11.2 | 12 | 11.3 | 11 | 13.2 | 13.3 | 12.2 | 12.2 | 11.9 | 11.5 | 10.8 | 12 | 14.1 | 16 | 13.4 | 12.1 | 8.6 | 8.5 | 8.7 | 8.4 | 8 | 7.7 | 6.9 | 7.6 | 8.8 | 9.7 | 8.9 | 7.9 | 9.5 | 10.3 | 10 | 10.5 | 10.6 | 10.5 | 10 | 11.5 | 12.8 | 13.3 | 10 | 8.1 | 7.2 | 7.2 | 7.6 | 7.8 | 7.5 | 7.3 | 6.5 | 7.4 | 8.4 | 8.9 | 7.7 | 6.6 | 0.321 | 0.321 | 0.327 | 0.352 | 0.357 | 0.348 | 0.353 | 0.349 | 0.341 | 0.33 | 0.315 | 0.319 | 2.56 | 2.571 | 2.576 | 2.462 | 2.491 | 2.524 | 2.516 | 2.54 | 2.534 | 2.589 | 2.604 | 2.569 | 265 | 284 | 294 | 292 | 291 | 293 | 290 | 289 | 285 | 276 | 266 | 255 | 22 | 25 | 28 | 34 | 34 | 33 | 33 | 31 | 29 | 24 | 21 | 21 | 554 | 812 | 1186 | 1645 | 2049 | 2269 | 2276 | 1937 | 1571 | 1041 | 627 | 456 | 85 | 115 | 124 | 148 | 123 | 136 | 111 | 114 | 91 | 95 | 73 | 83 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 4 | 16
| SISKIYOU-COUNTY-AP_STYP20 | 16 | 4 | USA | CA | SISKIYOU COUNTY AP | 725955 | 24259 | 41.781 | -122.468 | 2651 | 13.34 | -8 | NAP | 94-19 | 4A | 12 | 16.5 | 19.5 | 8.1 | 9.2 | 25.1 | 12.3 | 11.3 | 28 | 34.6 | 45.8 | 31.5 | 45.6 | 1.9 | 30 | 0.561 | 7 | 35.3 | 97.2 | 63.7 | 93.9 | 62.5 | 90.9 | 61.5 | 66 | 91.2 | 64.4 | 89.3 | 63 | 87.5 | 7.5 | 0 | 56.6 | 75.3 | 72.1 | 54.4 | 69.4 | 72.2 | 52.5 | 64.6 | 71.4 | 32 | 91.6 | 30.7 | 89.4 | 29.6 | 87.6 | 74.5 | 26.6 | 21.7 | 18.3 | 8.7 | 103.4 | 7.6 | 3 | 3.3 | 105.5 | -1.2 | 107.3 | -5.4 | 109 | -10.9 | 111.1 | 7.9 | 68.9 | 7.3 | 2 | 2.6 | 70.4 | -1.7 | 71.5 | -5.8 | 72.6 | -11.1 | 74.1 | 52.4 | 36.4 | 39.5 | 43.8 | 48.6 | 56.4 | 64.3 | 73.6 | 71.7 | 64.2 | 52.2 | 41.7 | 35.3 | 14.52 | 6.07 | 5.71 | 5.76 | 6.68 | 7.11 | 7.3 | 5.39 | 4.81 | 6.47 | 6.46 | 6.63 | 7.09 | 1817 | 421 | 294 | 204 | 106 | 21 | 2 | 0 | 0 | 2 | 49 | 262 | 456 | 5245 | 885 | 713 | 658 | 491 | 279 | 99 | 6 | 6 | 91 | 397 | 700 | 920 | 2693 | 1 | 1 | 12 | 65 | 219 | 430 | 733 | 674 | 428 | 118 | 11 | 1 | 647 | 0 | 0 | 0 | 0 | 12 | 77 | 274 | 216 | 67 | 1 | 0 | 0 | 11191 | 0 | 0 | 1 | 67 | 456 | 1541 | 4062 | 3379 | 1552 | 133 | 0 | 0 | 5482 | 0 | 0 | 0 | 8 | 140 | 668 | 2216 | 1744 | 679 | 27 | 0 | 0 | 6.1 | 5 | 6.2 | 6.9 | 6.8 | 6.8 | 7.5 | 6.6 | 6.1 | 5.4 | 5.1 | 4.8 | 5.3 | 19.1 | 3.1 | 2 | 2 | 1.5 | 1.4 | 0.8 | 0.4 | 0.3 | 0.4 | 1.3 | 2.4 | 3.3 | 30.8 | 6.2 | 5 | 8.1 | 3.5 | 3.7 | 2.4 | 1.7 | 1.4 | 1.1 | 4.8 | 7.8 | 8.9 | 10.9 | 0.7 | 0.9 | 0.5 | 0.6 | 0.4 | 0 | 0 | 0 | 0 | 0.2 | 0.4 | 0.6 | 5.2 | 1.8 | 1.1 | 1.6 | 0.7 | 0.9 | 0.7 | 0.4 | 0.3 | 0.3 | 1.1 | 1.6 | 2.4 | 56.9 | 63.5 | 71.6 | 80.8 | 89.7 | 97 | 102.1 | 100.2 | 94.5 | 83.7 | 67.9 | 55.8 | 46.6 | 49.6 | 51.9 | 56.8 | 60.5 | 63.6 | 66 | 64.2 | 60.7 | 57.8 | 52.1 | 48.1 | 53 | 58.4 | 66.3 | 75 | 83.8 | 91.5 | 98.4 | 96.3 | 90.9 | 77.8 | 62.1 | 52.2 | 45.2 | 46.4 | 50 | 54.9 | 59 | 61.7 | 64.5 | 63 | 59.8 | 55.1 | 49.9 | 45.7 | 49.7 | 54.3 | 62 | 70 | 79.2 | 87.8 | 95.1 | 92.9 | 88 | 72.8 | 57.4 | 49.4 | 43.3 | 44.8 | 48.2 | 52.4 | 57.1 | 60.2 | 63.5 | 61.8 | 59.1 | 53.2 | 47.6 | 43.7 | 46.5 | 50.8 | 57.1 | 64.3 | 74.2 | 83.4 | 91.4 | 90 | 83.8 | 68.3 | 53.9 | 46.5 | 41.5 | 42.8 | 45.8 | 49.9 | 55.2 | 58.9 | 62.7 | 61 | 58 | 51.3 | 45.8 | 41.7 | 48.9 | 51 | 54.3 | 58.8 | 63.1 | 66.2 | 68.8 | 66.9 | 64 | 59.2 | 54.4 | 49.5 | 53.8 | 60.5 | 67.5 | 76.6 | 84.6 | 91.1 | 95.1 | 93.6 | 89.9 | 78.2 | 64.6 | 54.3 | 46.1 | 48.1 | 51.4 | 55.6 | 60.3 | 63.5 | 66.9 | 64.9 | 61.6 | 57.2 | 51.3 | 46.4 | 51.1 | 56.6 | 63.5 | 72.6 | 80.2 | 87.6 | 92 | 90.8 | 86 | 75.3 | 59.8 | 50.8 | 44 | 45.7 | 49.2 | 53.1 | 58.4 | 61.3 | 65.2 | 63.5 | 59.9 | 54.6 | 48.9 | 44.4 | 48.7 | 52.9 | 59.5 | 68.1 | 76.4 | 84.2 | 90.1 | 89.2 | 84.4 | 70 | 56.1 | 48.5 | 42 | 43.6 | 46.9 | 50.5 | 56.2 | 59.6 | 63.8 | 62 | 58.5 | 52.3 | 46.4 | 42.2 | 46.4 | 50.2 | 56.2 | 62.9 | 72.2 | 80.8 | 88.4 | 86.8 | 81.8 | 65.6 | 52.9 | 46.1 | 17.5 | 21.5 | 24.2 | 26.5 | 28.8 | 32.3 | 35.3 | 35.9 | 35.6 | 30.1 | 21.3 | 16.9 | 22.1 | 27.9 | 34.2 | 37.6 | 38.3 | 39 | 39 | 39.9 | 42.1 | 38.5 | 27.8 | 18 | 15.2 | 17.5 | 19.7 | 19.8 | 17.4 | 15.2 | 14.4 | 15.5 | 18.8 | 20.3 | 17.6 | 12.4 | 18.9 | 25.3 | 30.1 | 35.3 | 35.4 | 36.7 | 36.4 | 37.1 | 39.5 | 34.3 | 24.5 | 15.7 | 13.4 | 16.4 | 17.7 | 19.3 | 16.4 | 14.8 | 13.7 | 14.7 | 18.3 | 18.6 | 15.8 | 11.2 | 0.291 | 0.295 | 0.301 | 0.319 | 0.326 | 0.319 | 0.324 | 0.32 | 0.302 | 0.301 | 0.286 | 0.295 | 2.531 | 2.545 | 2.554 | 2.494 | 2.513 | 2.566 | 2.563 | 2.555 | 2.592 | 2.592 | 2.598 | 2.516 | 276 | 293 | 303 | 302 | 301 | 302 | 299 | 298 | 298 | 287 | 277 | 264 | 23 | 26 | 29 | 33 | 33 | 31 | 31 | 30 | 27 | 24 | 21 | 21 | 594 | 879 | 1245 | 1706 | 2139 | 2485 | 2552 | 2254 | 1777 | 1167 | 678 | 486 | 93 | 111 | 131 | 167 | 169 | 141 | 93 | 95 | 85 | 111 | 80 | 95 | 0.86 | N/A | N/A | 1.13 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.94 | N/A | N/A | N/A | N/A | 176 | 32 | 16
| MOUNT-SHASTA_STYP20 | 16 | 4 | USA | CA | MOUNT SHASTA | 725957 | 24215 | 41.333 | -122.333 | 3535 | 12.91 | -8 | NAP | 94-19 | 5C | 12 | 18.2 | 21.7 | 6.7 | 8.9 | 29.1 | 11.5 | 11.3 | 30.3 | 13.4 | 38.6 | 12.2 | 38 | 1.7 | 50 | 0.493 | 7 | 33 | 91.9 | 64.2 | 89.4 | 63.1 | 86.4 | 61.7 | 67.7 | 86.1 | 65.6 | 84.8 | 63.8 | 82.9 | 2.1 | 290 | 61 | 91.5 | 78.2 | 57.3 | 79.9 | 76 | 55.1 | 73.7 | 74 | 33.9 | 86 | 32.1 | 84.7 | 30.7 | 82.8 | 77.7 | 11.9 | 10.5 | 9.1 | 10.7 | 97.2 | 5.1 | 2.7 | 7.1 | 99.1 | 4.1 | 100.7 | 1.2 | 102.2 | -2.5 | 104.2 | 9.5 | 70.7 | 4.9 | 3 | 6 | 72.9 | 3.1 | 74.7 | 0.3 | 76.4 | -3.3 | 78.6 | 50.8 | 36.7 | 38.4 | 42.4 | 46.9 | 55.1 | 62.4 | 69.4 | 67.6 | 61.7 | 51.2 | 41.5 | 35.6 | 13.34 | 5.83 | 5.89 | 6.54 | 7.27 | 7.43 | 7.02 | 5.05 | 4.74 | 6.34 | 6.47 | 6.41 | 5.91 | 1948 | 414 | 326 | 249 | 144 | 36 | 5 | 0 | 0 | 3 | 63 | 262 | 446 | 5529 | 879 | 745 | 702 | 542 | 316 | 128 | 17 | 26 | 131 | 428 | 704 | 911 | 2246 | 0 | 1 | 13 | 52 | 193 | 375 | 602 | 547 | 354 | 101 | 8 | 0 | 350 | 0 | 0 | 0 | 0 | 7 | 48 | 154 | 108 | 32 | 1 | 0 | 0 | 7196 | 0 | 0 | 1 | 43 | 314 | 964 | 2641 | 2165 | 987 | 81 | 0 | 0 | 2761 | 0 | 0 | 0 | 3 | 76 | 311 | 1156 | 879 | 323 | 13 | 0 | 0 | 3.1 | 3.2 | 3.3 | 3.6 | 3.9 | 3.6 | 3.6 | 2.4 | 2.2 | 2.6 | 2.9 | 2.9 | 3.3 | 40.6 | 7 | 6 | 5.3 | 2.9 | 1.9 | 1 | 0.3 | 0.4 | 0.7 | 2.2 | 5.6 | 7 | 75.2 | 27.5 | 21.8 | 18.9 | 9.1 | 9.3 | 3.8 | 1.7 | 2.6 | 3.9 | 9.7 | 17.2 | 25.9 | 14.2 | 0.2 | 0.2 | 0.4 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | 0.1 | 13 | 5.3 | 4.9 | 4.3 | 2.2 | 2 | 1 | 0.4 | 0.6 | 0.9 | 2.2 | 4.2 | 5.8 | 58.9 | 64.3 | 71 | 79.2 | 87 | 92 | 96.8 | 95.2 | 91.1 | 81.4 | 67.6 | 54.9 | 44.6 | 48.2 | 51.6 | 55.4 | 60.2 | 64.6 | 66.4 | 64.3 | 61.7 | 58.7 | 51.9 | 44.5 | 54 | 58.7 | 65.8 | 73.5 | 81.7 | 87.3 | 92.8 | 90.9 | 87.3 | 75.3 | 62.7 | 50.6 | 42.7 | 45.9 | 49.1 | 53.6 | 59.6 | 62.9 | 65.1 | 63.6 | 59.8 | 55.4 | 49.7 | 42.9 | 49.6 | 53.6 | 61.4 | 68.8 | 77.3 | 83.5 | 90 | 88.2 | 83.8 | 71.8 | 57.2 | 47.8 | 41.8 | 43.1 | 46.8 | 51.3 | 56.6 | 61.3 | 63.8 | 62.3 | 59 | 53.5 | 46.6 | 42.3 | 46 | 49 | 56 | 63.3 | 72.7 | 80 | 86.8 | 85.2 | 80.5 | 66.6 | 53.1 | 45.2 | 40.7 | 41.6 | 44.8 | 49.3 | 54.9 | 59.9 | 63 | 60.9 | 58.4 | 51.4 | 44.6 | 41 | 48.3 | 50.1 | 53.8 | 57.7 | 64.1 | 68.8 | 71.1 | 69.5 | 66 | 59.8 | 54.2 | 48 | 53 | 61 | 67.8 | 74.5 | 81.4 | 85.7 | 89.2 | 86.4 | 85.1 | 76.2 | 64 | 51 | 45.3 | 47.4 | 50.5 | 54.7 | 60.6 | 65.5 | 68.3 | 66.3 | 62.6 | 57.2 | 51 | 45.5 | 50.3 | 55.5 | 62.5 | 70.9 | 78.5 | 83.7 | 86.6 | 85.6 | 81.5 | 73 | 59.6 | 48.3 | 43.3 | 44.8 | 48.2 | 52.2 | 58.3 | 62.9 | 66.2 | 64.2 | 60.4 | 54.7 | 48.3 | 43.7 | 48.2 | 51.5 | 58.9 | 66.5 | 75 | 80.6 | 85.5 | 83.8 | 79.8 | 68.9 | 55.3 | 46.8 | 41.2 | 42.4 | 45.8 | 49.7 | 55.7 | 60.7 | 64.3 | 62.4 | 58.7 | 52.3 | 46 | 41.2 | 45.6 | 48.3 | 54.6 | 61.5 | 70.7 | 77.9 | 83.7 | 82.3 | 78.3 | 64.7 | 51.2 | 44.6 | 15.3 | 17.1 | 19.9 | 22.8 | 25.9 | 28.3 | 33 | 34 | 32.1 | 26 | 18.5 | 14.5 | 23.1 | 27 | 31 | 34.7 | 35 | 34.5 | 37 | 37.5 | 38.7 | 35.1 | 27.2 | 20.2 | 14.5 | 16.2 | 17.2 | 18 | 16.5 | 15.9 | 15.9 | 16.2 | 17.5 | 18.2 | 16.8 | 13.5 | 17.7 | 22.5 | 27.4 | 31.6 | 32.2 | 32.3 | 33.8 | 34.6 | 35.1 | 31.1 | 23.9 | 15.2 | 12 | 14.4 | 16 | 17.2 | 16 | 16.8 | 16.3 | 16.6 | 17.1 | 16.9 | 15.4 | 11.3 | 0.279 | 0.284 | 0.289 | 0.305 | 0.315 | 0.308 | 0.31 | 0.306 | 0.293 | 0.291 | 0.276 | 0.281 | 2.553 | 2.563 | 2.579 | 2.529 | 2.536 | 2.59 | 2.596 | 2.59 | 2.611 | 2.618 | 2.623 | 2.55 | 283 | 298 | 308 | 307 | 304 | 305 | 304 | 303 | 302 | 292 | 284 | 272 | 22 | 25 | 28 | 32 | 32 | 31 | 30 | 30 | 27 | 24 | 20 | 21 | 620 | 909 | 1281 | 1753 | 2179 | 2521 | 2569 | 2279 | 1808 | 1204 | 712 | 513 | 101 | 114 | 142 | 174 | 167 | 140 | 92 | 91 | 81 | 112 | 82 | 101 | 0.74 | N/A | N/A | 2.18 | N/A | N/A | N/A | N/A | 230 | 86 | N/A | N/A | N/A | 0.94 | N/A | N/A | N/A | N/A | 169 | 27 | 15
| ALTURAS_STYP20 | 16 | 4 | USA | CA | ALTURAS | 725958 | 94299 | 41.483 | -120.567 | 4375 | 12.52 | -8 | NAP | 98-19 | 5C | 12 | 3.5 | 10.1 | -1.1 | 6.1 | 11.4 | 4.6 | 8.2 | 19.1 | 25.8 | 41.6 | 22 | 39.3 | 0.9 | 20 | 0.601 | 7 | 41 | 94.4 | 60 | 91.4 | 59.1 | 88.9 | 58.1 | 62.5 | 87.5 | 60.8 | 85.7 | 59.5 | 84.4 | 9.3 | 270 | 54.1 | 73.2 | 66.7 | 51.4 | 66.1 | 66.4 | 48.4 | 59.2 | 64.6 | 30.1 | 87.4 | 28.8 | 85.7 | 27.8 | 84.3 | 69.4 | 22.1 | 19 | 16.9 | -5.6 | 99.5 | 8.2 | 2.6 | -11.5 | 101.4 | -16.3 | 102.9 | -20.8 | 104.3 | -26.8 | 106.2 | -5.9 | 65.4 | 8 | 2.2 | -11.7 | 67 | -16.4 | 68.2 | -20.9 | 69.4 | -26.7 | 71 | 47.7 | 31.8 | 34.2 | 39.2 | 44 | 52.3 | 60.6 | 68.4 | 66 | 58.4 | 47.4 | 37.8 | 30.8 | 14.56 | 8.49 | 7.01 | 6.45 | 6.8 | 6.97 | 6.73 | 5.05 | 4.74 | 6.6 | 6.59 | 7.87 | 8.19 | 2709 | 565 | 442 | 336 | 201 | 57 | 7 | 0 | 0 | 12 | 126 | 368 | 595 | 6575 | 1030 | 862 | 799 | 631 | 396 | 158 | 23 | 43 | 211 | 547 | 815 | 1060 | 1854 | 0 | 0 | 2 | 20 | 127 | 326 | 571 | 497 | 263 | 45 | 3 | 0 | 245 | 0 | 0 | 0 | 0 | 1 | 28 | 129 | 75 | 12 | 0 | 0 | 0 | 9060 | 0 | 0 | 1 | 24 | 288 | 1288 | 3494 | 2689 | 1179 | 97 | 0 | 0 | 4060 | 0 | 0 | 0 | 1 | 66 | 484 | 1797 | 1254 | 438 | 20 | 0 | 0 | 5.3 | 4.3 | 5.3 | 6.4 | 6.7 | 6.5 | 6.3 | 5.7 | 5.1 | 4.5 | 4.4 | 4.4 | 4.6 | 14.1 | 1.6 | 1.3 | 1.6 | 1.6 | 1.7 | 0.9 | 0.2 | 0.3 | 0.4 | 1 | 1.6 | 1.9 | 23.5 | 3.9 | 3.1 | 4.2 | 3.9 | 5.6 | 2.4 | 0.8 | 1.2 | 1.4 | 3.1 | 4.2 | 5.3 | 8.3 | 0.1 | 0.4 | 0.6 | 0.4 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0.2 | 0.5 | 4.4 | 1.1 | 0.7 | 0.9 | 0.8 | 1.4 | 0.7 | 0.2 | 0.4 | 0.4 | 0.8 | 0.9 | 1.5 | 57.7 | 61.3 | 70.4 | 77.3 | 86.9 | 94.5 | 99.3 | 96.7 | 92.5 | 83.3 | 69.5 | 54 | 43.1 | 45.5 | 48.7 | 52.3 | 57.9 | 60.6 | 63 | 61 | 58.8 | 54.5 | 49.6 | 42.8 | 53.1 | 55.4 | 64.2 | 72.3 | 81.4 | 89.6 | 95.4 | 93 | 88.3 | 75.5 | 63.7 | 49.9 | 41.9 | 42.1 | 46.3 | 50.3 | 55.9 | 59 | 60.3 | 59.6 | 56.4 | 51.6 | 47.5 | 41 | 48.4 | 51.1 | 59.9 | 67.3 | 77 | 85.6 | 92.7 | 90.3 | 85.2 | 72.4 | 57.4 | 46.5 | 40.2 | 41.3 | 44.3 | 48.1 | 53.5 | 56.8 | 59.5 | 58.5 | 55.5 | 50 | 44.4 | 40.2 | 44.8 | 46.7 | 54.4 | 62.3 | 72.3 | 81.8 | 90.1 | 87.6 | 81.7 | 67.2 | 52.4 | 43.5 | 38.7 | 39 | 42.4 | 45.9 | 51.7 | 55.9 | 58.9 | 57.4 | 54.8 | 48.2 | 42.6 | 38.5 | 47.1 | 47.4 | 50.2 | 54.3 | 59.9 | 62.9 | 65.4 | 64.9 | 62 | 55.6 | 51.3 | 45.6 | 54.6 | 57.9 | 66.3 | 72.6 | 81.8 | 88.4 | 92.5 | 91.4 | 81.7 | 75.4 | 65.6 | 49.9 | 43.5 | 44.3 | 47.6 | 51.4 | 57 | 60.1 | 63.2 | 61.6 | 59.2 | 53.1 | 48.4 | 43.2 | 50 | 52.9 | 61.1 | 69.5 | 77.9 | 85 | 89.1 | 86.2 | 81.6 | 72 | 60.7 | 47.7 | 41 | 41.8 | 45.5 | 49.1 | 54.9 | 58.4 | 61.4 | 59.9 | 57 | 51.2 | 46 | 41.2 | 47.1 | 49.1 | 57.7 | 64.9 | 73.4 | 82 | 86.9 | 84.7 | 81 | 69.3 | 56.2 | 45.3 | 38.9 | 39.6 | 43.3 | 46.8 | 52.7 | 56.7 | 59.9 | 58.5 | 55.2 | 49.2 | 43.6 | 38.8 | 44.2 | 46.5 | 53.4 | 60.2 | 69.3 | 78.8 | 85.7 | 83.4 | 79.7 | 64.9 | 51.3 | 43.1 | 22.3 | 22.2 | 25.1 | 27.1 | 30.1 | 35.5 | 41 | 41.3 | 40.3 | 34.6 | 25.8 | 20.7 | 29.6 | 30.1 | 37.8 | 40.8 | 41 | 43.4 | 44.5 | 45.7 | 47.6 | 45.6 | 36.8 | 25.9 | 19.4 | 18.6 | 21 | 20.7 | 18.2 | 16.8 | 16.5 | 18.7 | 21.6 | 23.9 | 22.1 | 17.9 | 24.2 | 25.5 | 33.1 | 37.1 | 36.9 | 40.4 | 41 | 41.3 | 43.6 | 40.2 | 32.4 | 19.3 | 16.4 | 16.3 | 19 | 19.2 | 16.7 | 16.3 | 15.8 | 17.7 | 20.4 | 21.8 | 19.7 | 13.8 | 0.279 | 0.289 | 0.3 | 0.307 | 0.314 | 0.308 | 0.312 | 0.31 | 0.298 | 0.297 | 0.28 | 0.275 | 2.507 | 2.51 | 2.505 | 2.493 | 2.513 | 2.557 | 2.545 | 2.53 | 2.56 | 2.551 | 2.563 | 2.531 | 281 | 295 | 303 | 306 | 305 | 305 | 303 | 301 | 300 | 288 | 280 | 274 | 23 | 27 | 30 | 33 | 33 | 32 | 32 | 31 | 28 | 25 | 22 | 21 | 627 | 912 | 1288 | 1723 | 2133 | 2501 | 2536 | 2243 | 1784 | 1194 | 709 | 502 | 83 | 113 | 123 | 167 | 190 | 131 | 108 | 106 | 89 | 100 | 75 | 98 | N/A | N/A | N/A | 1.06 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.08 | N/A | N/A | N/A | N/A | 164 | 76 | 7
| MADERA_STYP20 | 13 | 4 | USA | CA | MADERA | 745046 | 93242 | 36.988 | -120.111 | 253 | 14.56 | -8 | NAP | 99-19 | 3B | 12 | 30 | 32.5 | 22.9 | 17.4 | 49.5 | 26.4 | 20.6 | 46.4 | 21 | 54 | 18.8 | 52.8 | 2.2 | 90 | 0.458 | 7 | 33.5 | 102 | 69.7 | 99.6 | 68.9 | 97.3 | 67.8 | 72.8 | 95.7 | 71.1 | 94.2 | 69.5 | 92.3 | 8.7 | 300 | 64.5 | 91.6 | 82.4 | 63 | 86.9 | 80.9 | 61.1 | 81.2 | 78.7 | 36.5 | 94.8 | 34.9 | 94.1 | 33.6 | 92.4 | 82.2 | 18.5 | 16.2 | 13.5 | 26.5 | 106.7 | 2.6 | 1.9 | 24.6 | 108.1 | 23.1 | 109.2 | 21.6 | 110.3 | 19.7 | 111.7 | 25.1 | 75.3 | 2.5 | 2.2 | 23.3 | 76.9 | 21.8 | 78.2 | 20.3 | 79.4 | 18.5 | 81.1 | 63.1 | 47.5 | 51.1 | 55.9 | 60.3 | 67.9 | 75 | 80 | 78.4 | 74.2 | 64.6 | 54.3 | 47.3 | 12.77 | 5.11 | 4.93 | 5.61 | 6.57 | 6.22 | 6.15 | 4.86 | 4.16 | 5.64 | 5.75 | 5.65 | 5.21 | 309 | 111 | 42 | 12 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 118 | 2383 | 544 | 389 | 284 | 170 | 40 | 4 | 0 | 0 | 4 | 77 | 322 | 549 | 5092 | 32 | 73 | 196 | 313 | 554 | 749 | 930 | 881 | 726 | 452 | 152 | 34 | 1692 | 0 | 0 | 3 | 30 | 129 | 303 | 465 | 416 | 281 | 64 | 1 | 0 | 23759 | 0 | 2 | 126 | 578 | 2057 | 4361 | 6459 | 5524 | 3645 | 957 | 50 | 0 | 13238 | 0 | 0 | 20 | 201 | 938 | 2472 | 3982 | 3304 | 1996 | 320 | 5 | 0 | 6 | 4.6 | 5.4 | 5.8 | 7.1 | 7.9 | 7.9 | 7.2 | 6.7 | 5.7 | 4.8 | 4.1 | 4.7 | 11.2 | 1.8 | 1.8 | 1.9 | 1.2 | 0.2 | 0 | 0 | 0 | 0.2 | 0.6 | 1.7 | 1.5 | 22.1 | 5.7 | 5.3 | 5.1 | 5.5 | 1.8 | 0.4 | 0.1 | 0.3 | 1.6 | 2 | 4.3 | 3.3 | 5.6 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 1.5 | 1.5 | 1.3 | 1.2 | 0.4 | 0.1 | 0 | 0.1 | 0.4 | 0.6 | 1.1 | 0.9 | 67.9 | 73.2 | 82.3 | 91.6 | 99 | 103.9 | 106 | 104.3 | 101.4 | 93.4 | 79.2 | 66.7 | 54 | 58.6 | 61.5 | 63.2 | 67.6 | 71.2 | 72.3 | 69.2 | 67.6 | 65.4 | 60.3 | 54.5 | 63.6 | 68.7 | 77.2 | 85.7 | 93.6 | 100.1 | 102.2 | 100.3 | 98.4 | 87.7 | 74.5 | 63 | 53.1 | 56.8 | 59.7 | 61.8 | 65.6 | 69.3 | 70.3 | 68.6 | 67.1 | 63.4 | 58.5 | 52.8 | 60.4 | 65.2 | 73.3 | 80.9 | 89.8 | 96.8 | 99.7 | 98.3 | 95.2 | 83.1 | 70.6 | 60 | 52.3 | 55 | 58.8 | 60.4 | 63.5 | 67.6 | 69.8 | 68 | 66.1 | 61.3 | 57 | 52.3 | 57.1 | 62.2 | 69.6 | 75.5 | 85.1 | 92.9 | 97 | 95.3 | 91.3 | 79.5 | 66.3 | 57 | 51.1 | 53.7 | 57.3 | 58.4 | 61.9 | 66.1 | 68.5 | 67 | 65.4 | 60.6 | 55.3 | 51.1 | 58.1 | 60.6 | 65.1 | 67.4 | 70.3 | 74.7 | 75.6 | 73.2 | 71.9 | 68 | 62.5 | 58.6 | 63.2 | 68.4 | 76.8 | 83.9 | 93.8 | 98.4 | 100.4 | 95.1 | 93.9 | 84.3 | 74.3 | 63.8 | 55.5 | 58.5 | 62.2 | 64.1 | 67.5 | 71.7 | 73.3 | 71.2 | 69.2 | 65.7 | 60.3 | 55.7 | 60.2 | 66.4 | 73.6 | 81.4 | 89.4 | 95 | 96.1 | 94.8 | 92 | 81.9 | 71.4 | 59.5 | 53.5 | 56.4 | 59.9 | 61.7 | 65.3 | 69.4 | 71.4 | 69.6 | 67.7 | 63.7 | 58.5 | 53.9 | 57.7 | 63.8 | 70.6 | 77.3 | 86.2 | 91.9 | 94.5 | 92.7 | 90.9 | 79.6 | 68 | 57.8 | 51.4 | 54.4 | 57.8 | 59.7 | 63.2 | 67.8 | 69.8 | 68.4 | 66.2 | 61.8 | 56.6 | 51.8 | 56.6 | 60.8 | 67.8 | 73.9 | 82.7 | 89.7 | 92.9 | 91.1 | 88.6 | 76.6 | 64.6 | 55.9 | 17.7 | 20.6 | 23.8 | 26.6 | 30 | 32.9 | 33.5 | 33.9 | 32.7 | 28 | 23.2 | 18.2 | 23.9 | 25.7 | 30.2 | 34.1 | 36.3 | 36 | 34.7 | 36.2 | 36.4 | 33.2 | 29.2 | 22.2 | 15 | 15.1 | 14.9 | 13.6 | 13 | 11.9 | 11.4 | 11.1 | 11.8 | 13.7 | 15.3 | 13.7 | 17.5 | 22.8 | 27.7 | 30.8 | 34.2 | 34.2 | 32.9 | 34.2 | 33.9 | 29 | 25.3 | 15.2 | 11.9 | 14 | 15 | 13.6 | 13 | 11.9 | 11.7 | 11.6 | 11.7 | 12.1 | 13.9 | 10.4 | 0.349 | 0.362 | 0.384 | 0.376 | 0.365 | 0.362 | 0.377 | 0.366 | 0.37 | 0.379 | 0.372 | 0.357 | 2.37 | 2.344 | 2.278 | 2.333 | 2.388 | 2.397 | 2.374 | 2.382 | 2.38 | 2.318 | 2.289 | 2.334 | 263 | 274 | 279 | 287 | 291 | 290 | 285 | 286 | 279 | 264 | 250 | 249 | 29 | 34 | 39 | 39 | 38 | 38 | 38 | 37 | 35 | 34 | 31 | 29 | 775 | 1106 | 1570 | 2001 | 2385 | 2669 | 2583 | 2359 | 1953 | 1419 | 957 | 705 | 111 | 127 | 137 | 156 | 132 | 97 | 92 | 71 | 62 | 82 | 55 | 97 | 1.69 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.9 | N/A | -2.09 | N/A | N/A | N/A | N/A | -245 | 304 | 95 | 27
| OROVILLE_STYP20 | 11 | 4 | USA | CA | OROVILLE | 745048 | 93210 | 39.49 | -121.618 | 190 | 14.6 | -8 | NAP | 99-19 | 3A | 12 | 33.1 | 35.6 | 18.1 | 13.8 | 51.6 | 22.1 | 16.7 | 50.1 | 27.7 | 51.5 | 24.9 | 51 | 3 | 320 | 0.44 | 7 | 29.3 | 100.5 | 69.8 | 98.1 | 69.2 | 95.2 | 67.9 | 73.3 | 95 | 71.5 | 93.3 | 70.1 | 91.5 | 6.3 | 180 | 65.5 | 94.9 | 86.2 | 63.2 | 87.3 | 84.5 | 61.3 | 81.4 | 82.2 | 37 | 95.3 | 35.4 | 93.4 | 34 | 91.5 | 88.2 | 20.7 | 18.2 | 16.1 | 28.1 | 106.4 | 2.5 | 2.4 | 26.3 | 108.1 | 24.8 | 109.6 | 23.4 | 110.9 | 21.6 | 112.7 | 26.3 | 77.2 | 2.2 | 4.7 | 24.8 | 80.6 | 23.5 | 83.4 | 22.3 | 86.1 | 20.7 | 89.5 | 63.2 | 47.7 | 51.2 | 55.7 | 60.2 | 68 | 75.7 | 80.5 | 78.3 | 73.7 | 64.6 | 54 | 47.7 | 12.82 | 4.58 | 4.76 | 5.46 | 6.55 | 6.77 | 6.63 | 5.22 | 4.43 | 5.57 | 5.59 | 5.7 | 4.96 | 282 | 97 | 39 | 12 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 104 | 2388 | 535 | 387 | 292 | 174 | 44 | 6 | 0 | 0 | 5 | 75 | 332 | 538 | 5091 | 27 | 72 | 188 | 308 | 558 | 772 | 946 | 878 | 711 | 452 | 147 | 32 | 1720 | 0 | 0 | 3 | 29 | 137 | 328 | 481 | 413 | 266 | 62 | 1 | 0 | 22120 | 1 | 1 | 78 | 459 | 1772 | 4242 | 6453 | 5110 | 3184 | 799 | 19 | 2 | 11361 | 0 | 0 | 7 | 136 | 728 | 2245 | 3744 | 2738 | 1526 | 236 | 1 | 0 | 6.1 | 5.3 | 6.7 | 7.1 | 7.1 | 7.1 | 6.7 | 6 | 5.6 | 5.4 | 5.2 | 5 | 5.8 | 20.9 | 4.3 | 4 | 3 | 1.6 | 1.3 | 0.4 | 0 | 0.1 | 0.1 | 1.1 | 1.9 | 4.5 | 35.5 | 14.1 | 11.5 | 10.4 | 4.9 | 4 | 1.5 | 0.1 | 0.6 | 0.6 | 3.7 | 5 | 11.1 | 12.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 5.9 | 3.4 | 2.8 | 3.2 | 1.4 | 1.1 | 0.4 | 0 | 0.2 | 0.2 | 0.9 | 1.4 | 2.7 | 68.1 | 72.1 | 81 | 89.2 | 96.8 | 103.5 | 105.8 | 102.1 | 99.3 | 91.1 | 76.6 | 66.2 | 50.6 | 56.7 | 60.4 | 63.4 | 69.3 | 71.1 | 71.5 | 69.2 | 67.6 | 64.1 | 58.5 | 53.7 | 61.8 | 67.4 | 75.8 | 83.9 | 91.9 | 99.1 | 101.5 | 98.7 | 95.3 | 86 | 72.2 | 61.3 | 50.7 | 55.2 | 58.5 | 61.5 | 66.7 | 69.8 | 70.4 | 68.7 | 66.1 | 61.5 | 57.3 | 53 | 58.5 | 63.6 | 72.2 | 79.8 | 88.2 | 95.3 | 98.8 | 95.5 | 92.5 | 81.9 | 68 | 58.6 | 51.1 | 53.2 | 57.1 | 60.3 | 64.8 | 67.7 | 69.9 | 67.7 | 65.6 | 60.1 | 55.6 | 52.2 | 55.6 | 60.6 | 67.9 | 74.6 | 83.6 | 91.4 | 95.5 | 92.7 | 89.3 | 78.7 | 63.9 | 56.2 | 50.2 | 52.1 | 54.9 | 58.1 | 62.8 | 66.4 | 68.8 | 67.3 | 65 | 58.9 | 54.4 | 50.7 | 56.7 | 59.8 | 62.5 | 66.5 | 75.3 | 75.6 | 76.1 | 74.4 | 72.8 | 67 | 61.8 | 58.9 | 60.7 | 67.9 | 76.2 | 83 | 88.1 | 96.4 | 99.6 | 92.9 | 89.7 | 84.3 | 72.5 | 63.3 | 54.2 | 57.2 | 60.3 | 63.5 | 69.4 | 72.2 | 73.4 | 71.5 | 69.1 | 64.3 | 59.3 | 56.4 | 57.7 | 64.3 | 72.9 | 80.8 | 87.6 | 93.8 | 96.6 | 92.8 | 90.2 | 80.8 | 67.6 | 59.6 | 52.7 | 55.2 | 58.4 | 61.2 | 66.4 | 70.2 | 71.8 | 70 | 67.3 | 62.4 | 57.7 | 54 | 55.9 | 61.1 | 69.1 | 77 | 85 | 91.4 | 94.6 | 91.1 | 88.4 | 77.3 | 64.1 | 56.3 | 51.1 | 53.4 | 56.5 | 59.2 | 64 | 68.2 | 70.4 | 68.5 | 65.7 | 60.5 | 56.1 | 52.1 | 55.1 | 58.6 | 65.7 | 72.7 | 81.4 | 88.8 | 92.6 | 89.5 | 86.9 | 74 | 62.2 | 54.6 | 15 | 17 | 19.6 | 22.4 | 24.9 | 27.3 | 29.3 | 28.8 | 27.6 | 24.4 | 17.9 | 14.7 | 21 | 23.4 | 27.5 | 30.6 | 30.7 | 31.3 | 31.2 | 30.7 | 32 | 30.5 | 24.7 | 18.5 | 12.6 | 13.7 | 14 | 13.3 | 12.4 | 11.3 | 11.4 | 11.3 | 12.4 | 12.8 | 12.6 | 11.1 | 14.1 | 18.6 | 23.5 | 28.4 | 28.7 | 29.7 | 29.7 | 29 | 29.5 | 26.1 | 19 | 11.7 | 9.6 | 11.8 | 12.8 | 12.9 | 13.8 | 11.8 | 12 | 11.9 | 12.4 | 11.7 | 10.5 | 8.2 | 0.328 | 0.329 | 0.351 | 0.36 | 0.36 | 0.356 | 0.353 | 0.34 | 0.343 | 0.339 | 0.323 | 0.327 | 2.485 | 2.494 | 2.426 | 2.397 | 2.435 | 2.448 | 2.439 | 2.47 | 2.473 | 2.486 | 2.517 | 2.489 | 267 | 284 | 287 | 290 | 291 | 291 | 291 | 293 | 286 | 276 | 266 | 258 | 25 | 28 | 33 | 36 | 36 | 36 | 36 | 34 | 31 | 28 | 24 | 23 | 671 | 968 | 1380 | 1863 | 2301 | 2605 | 2623 | 2335 | 1872 | 1288 | 800 | 581 | 121 | 137 | 170 | 185 | 157 | 119 | 82 | 79 | 72 | 101 | 72 | 104 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.74 | N/A | -2 | N/A | N/A | N/A | -58 | -180 | 241 | 90 | 32
| RAMONA_STYP20 | 10 | 4 | USA | CA | RAMONA | 745056 | 53120 | 33.038 | -116.916 | 1393 | 13.97 | -8 | NAP | 99-19 | 3A | 12 | 28.6 | 31.3 | 2.5 | 6.6 | 62.4 | 7.7 | 8.6 | 61.4 | 23.8 | 60.5 | 20.3 | 60.9 | 1.2 | 110 | 0.46 | 8 | 30.8 | 97.3 | 67.6 | 94.2 | 67.3 | 91.3 | 66.6 | 72.3 | 90.9 | 70.8 | 88.8 | 69.4 | 86.7 | 10.8 | 280 | 66.2 | 101.6 | 79 | 64.3 | 95 | 78.6 | 63.1 | 91.1 | 77.4 | 36.7 | 91 | 35.4 | 88.9 | 34.3 | 86.7 | 88.2 | 18.1 | 15.7 | 13 | 24.4 | 104.1 | 2.6 | 3.9 | 22.6 | 106.9 | 21.1 | 109.1 | 19.7 | 111.3 | 17.8 | 114.1 | 22.6 | 75.5 | 2.3 | 4.3 | 21 | 78.6 | 19.6 | 81.1 | 18.3 | 83.5 | 16.6 | 86.6 | 61.1 | 51.5 | 51.5 | 54.2 | 56.8 | 61.8 | 67.4 | 73.3 | 74 | 71.1 | 63.9 | 56.4 | 50.6 | 10 | 6.05 | 5.75 | 5.29 | 5.46 | 4.91 | 4.77 | 4.72 | 4.71 | 5.89 | 5.67 | 5.95 | 5.56 | 200 | 54 | 45 | 20 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 61 | 2349 | 420 | 380 | 337 | 253 | 124 | 23 | 0 | 0 | 10 | 89 | 265 | 448 | 4245 | 100 | 86 | 149 | 211 | 364 | 523 | 721 | 745 | 632 | 431 | 204 | 79 | 920 | 2 | 1 | 1 | 6 | 23 | 96 | 256 | 281 | 192 | 55 | 7 | 0 | 14466 | 98 | 120 | 200 | 386 | 698 | 1694 | 3170 | 3540 | 2741 | 1340 | 418 | 61 | 6692 | 9 | 15 | 40 | 123 | 259 | 717 | 1535 | 1846 | 1423 | 602 | 118 | 5 | 4.9 | 4.8 | 5 | 4.8 | 5.1 | 5.2 | 5.2 | 5.3 | 5 | 4.7 | 4.6 | 4.7 | 4.6 | 19 | 3.8 | 4.6 | 2.8 | 1.5 | 0.4 | 0.2 | 0.1 | 0.2 | 0.2 | 0.9 | 1.2 | 3.1 | 35.5 | 20.1 | 12.8 | 14.5 | 3.6 | 2.9 | 0.9 | 0.5 | 1.5 | 1.9 | 7.9 | 3 | 12.2 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 8.2 | 4.8 | 2.9 | 3.5 | 1.1 | 0.7 | 0.3 | 0.1 | 0.3 | 0.4 | 1.7 | 1 | 2.7 | 81.1 | 82.2 | 84.5 | 90.3 | 93.2 | 99.1 | 99.9 | 100.4 | 100.3 | 96.6 | 88 | 79.7 | 56 | 55 | 58.1 | 58.4 | 62.1 | 66.2 | 70.9 | 68.5 | 69.7 | 62.1 | 57.3 | 54.7 | 76.8 | 77.9 | 79.5 | 83.2 | 87.4 | 92 | 94.6 | 96.4 | 96.6 | 91 | 83.6 | 75.1 | 53.4 | 54 | 57.8 | 57.7 | 61.4 | 66.4 | 68.9 | 69 | 67.4 | 60.9 | 56.1 | 52.1 | 72.8 | 73.1 | 74.9 | 78.3 | 81.7 | 87.9 | 91.3 | 93.1 | 92.4 | 87.3 | 79.2 | 71.1 | 52.1 | 53.3 | 56.4 | 57.3 | 62.1 | 65.6 | 68.5 | 68.1 | 67.1 | 60.3 | 54.5 | 50.9 | 68.5 | 67.5 | 70.4 | 73 | 76.8 | 83.6 | 88.5 | 90.2 | 88.7 | 82.1 | 73.8 | 66.2 | 50 | 51.1 | 55.5 | 56.7 | 60.9 | 64.5 | 68.1 | 68 | 65.6 | 59.7 | 52.7 | 49.6 | 61.1 | 60.1 | 63.9 | 64.4 | 68.5 | 70.6 | 73.7 | 74 | 73.4 | 70.2 | 61.3 | 59.5 | 74.5 | 71.4 | 77.5 | 79.1 | 84.8 | 90.3 | 92.5 | 92.6 | 93.2 | 82.6 | 70.2 | 68 | 56.8 | 57.2 | 60.7 | 61.7 | 65.7 | 68.4 | 71.9 | 71.9 | 71.4 | 66 | 59.3 | 56.8 | 67.4 | 69.6 | 73.4 | 75.8 | 81.1 | 87.2 | 89.8 | 90.9 | 90 | 80.5 | 73.3 | 66 | 54.7 | 55.2 | 58.6 | 59.5 | 63.7 | 66.8 | 70.4 | 70.4 | 69.6 | 63.8 | 57.6 | 54.6 | 64.7 | 67.4 | 70.6 | 72.9 | 78.1 | 84.9 | 87.6 | 89 | 86.3 | 79.6 | 72.8 | 63 | 53 | 53.2 | 56.3 | 57.6 | 61.4 | 65.2 | 69 | 69 | 67.7 | 61.7 | 55.9 | 52.7 | 62.5 | 63.3 | 67.7 | 71 | 74.5 | 82.5 | 85.5 | 86.9 | 83.9 | 76.1 | 69.1 | 61 | 28.6 | 26.4 | 27.2 | 27 | 25.8 | 29.4 | 29.8 | 30.8 | 31.1 | 30.2 | 30.2 | 28.3 | 36.8 | 38.8 | 38.3 | 39.8 | 38.1 | 38.2 | 33.3 | 34.6 | 36 | 41.1 | 39.6 | 37.8 | 19.1 | 19.8 | 20 | 19.3 | 18.4 | 17 | 14 | 14.7 | 15.3 | 18.5 | 18.7 | 20.1 | 29.2 | 31.1 | 32.1 | 32.4 | 31.9 | 34.3 | 29.6 | 30.6 | 31.4 | 32.1 | 32.3 | 28.5 | 17.9 | 18.3 | 19 | 17.9 | 16.7 | 16.1 | 12.7 | 13.6 | 14.8 | 17 | 18.2 | 17.6 | 0.298 | 0.306 | 0.319 | 0.329 | 0.347 | 0.349 | 0.377 | 0.38 | 0.345 | 0.352 | 0.306 | 0.309 | 2.559 | 2.553 | 2.5 | 2.482 | 2.453 | 2.452 | 2.451 | 2.421 | 2.502 | 2.441 | 2.568 | 2.558 | 294 | 303 | 305 | 304 | 298 | 295 | 286 | 285 | 292 | 281 | 289 | 284 | 26 | 29 | 32 | 35 | 36 | 36 | 36 | 36 | 32 | 31 | 25 | 24 | 1054 | 1329 | 1771 | 2147 | 2324 | 2467 | 2345 | 2226 | 1924 | 1499 | 1157 | 954 | 68 | 119 | 93 | 98 | 141 | 126 | 128 | 87 | 84 | 97 | 63 | 64 | 1.19 | N/A | N/A | 1.64 | N/A | N/A | N/A | -331 | 421 | N/A | 1.19 | N/A | -2.9 | 1.35 | N/A | N/A | N/A | -193 | 423 | 223 | 41
| WATSONVILLE_STYP20 | 3 | 4 | USA | CA | WATSONVILLE | 745058 | 23277 | 36.936 | -121.789 | 160 | 14.61 | -8 | NAP | 99-19 | 3C | 12 | 34.1 | 36.4 | 22 | 16.6 | 52.5 | 25.9 | 20 | 50.1 | 18.4 | 56.2 | 15.7 | 56.8 | 2.5 | 330 | 0.455 | 9 | 20.5 | 86.2 | 62.5 | 81.1 | 62 | 77 | 61.2 | 65.4 | 79.8 | 64.1 | 77.1 | 62.8 | 74.4 | 6.4 | 210 | 60.9 | 80.3 | 66.6 | 59.3 | 75.9 | 66.2 | 58.3 | 73.1 | 65.3 | 30.2 | 80.1 | 29.2 | 77 | 28.4 | 74.4 | 72.9 | 15 | 12.4 | 10.9 | 30.1 | 96.8 | 2.6 | 4.3 | 28.3 | 99.9 | 26.8 | 102.4 | 25.3 | 104.8 | 23.4 | 107.9 | 28.2 | 68.9 | 2.5 | 1.4 | 26.4 | 70 | 24.9 | 70.8 | 23.5 | 71.6 | 21.7 | 72.7 | 57.6 | 51.3 | 52.3 | 54.2 | 55.6 | 58.4 | 61.2 | 62.6 | 63.3 | 63.8 | 61.2 | 55.5 | 50.9 | 6.43 | 4.89 | 4.97 | 4.7 | 4.67 | 3.91 | 3.58 | 3.09 | 3.48 | 4.93 | 5.18 | 5.1 | 4.61 | 148 | 45 | 29 | 13 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 45 | 2855 | 424 | 356 | 337 | 287 | 212 | 124 | 91 | 75 | 81 | 143 | 287 | 438 | 2906 | 86 | 94 | 142 | 173 | 260 | 337 | 389 | 414 | 413 | 348 | 177 | 73 | 137 | 0 | 0 | 1 | 5 | 6 | 11 | 15 | 24 | 45 | 27 | 3 | 0 | 1652 | 10 | 15 | 40 | 92 | 112 | 159 | 123 | 181 | 461 | 390 | 68 | 1 | 549 | 1 | 0 | 6 | 33 | 34 | 51 | 20 | 53 | 193 | 145 | 13 | 0 | 4.1 | 3.3 | 4 | 4.2 | 4.7 | 4.9 | 4.9 | 4.8 | 4.4 | 4.1 | 3.7 | 3.2 | 3.4 | 21.3 | 4.2 | 3.5 | 3.6 | 1.9 | 0.2 | 0.1 | 0.1 | 0.1 | 0.3 | 1.1 | 3.3 | 3.5 | 48.3 | 10.9 | 10.4 | 11 | 6.7 | 1 | 1.3 | 1.3 | 1.1 | 1.5 | 3.8 | 8 | 10.5 | 10.7 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 8.1 | 2.9 | 3 | 2.4 | 2 | 0.2 | 0.2 | 0.3 | 0.2 | 0.4 | 1.1 | 2.4 | 2.3 | 75 | 76.2 | 79.4 | 84 | 84.2 | 86.7 | 82.2 | 86.6 | 93.4 | 91.1 | 81.5 | 71.6 | 54.5 | 58.8 | 62.1 | 62.9 | 63 | 63.8 | 65.3 | 65.3 | 64.7 | 62.1 | 60.3 | 53.7 | 69.5 | 71.1 | 72.5 | 74.6 | 75.7 | 78.3 | 77.4 | 78.6 | 85.7 | 83.4 | 74.4 | 66 | 54.7 | 56.5 | 58.4 | 58.8 | 59.7 | 62.5 | 63.6 | 63.9 | 61.9 | 60.3 | 58.2 | 53.7 | 64.2 | 65.4 | 67.5 | 69.2 | 70.8 | 73.2 | 73.3 | 74.1 | 78.7 | 77.4 | 69.6 | 62.7 | 53.8 | 54.5 | 56.2 | 56.3 | 58.8 | 60.8 | 62.1 | 62.6 | 62.4 | 59 | 55.9 | 53.3 | 60.4 | 61.3 | 63.5 | 64.6 | 66.9 | 70.1 | 70.3 | 71.5 | 73.1 | 72 | 64.6 | 59.6 | 52.8 | 53.4 | 54.7 | 55.3 | 57.4 | 59.7 | 61 | 61.7 | 61.3 | 58.1 | 54.8 | 52.8 | 59.3 | 61.2 | 63.4 | 64.1 | 64.9 | 65.9 | 66.4 | 66.4 | 67.2 | 65.4 | 63.3 | 60.8 | 66 | 70.4 | 77 | 81.9 | 79.7 | 81.6 | 80.1 | 81.5 | 82.4 | 80.5 | 74.1 | 64.3 | 57.1 | 58.7 | 60.1 | 60.5 | 61.3 | 63.4 | 64.1 | 64.5 | 64.9 | 63.1 | 60.6 | 58.2 | 62.7 | 66.4 | 69.3 | 71.7 | 73.2 | 76.3 | 76 | 76.7 | 79.4 | 76.1 | 68 | 60.9 | 55.5 | 56.7 | 57.9 | 58.2 | 59.4 | 61.5 | 62.5 | 63.1 | 63.4 | 61.5 | 58.9 | 56.2 | 60.8 | 63.1 | 64.6 | 66.3 | 68.8 | 72.4 | 72.6 | 73.7 | 76.1 | 72.6 | 65.7 | 59.2 | 54 | 54.7 | 56 | 56.3 | 57.9 | 60 | 61.2 | 61.8 | 61.8 | 59.8 | 57.1 | 54.2 | 58.8 | 59.9 | 61.7 | 63.2 | 66.1 | 69.1 | 69.8 | 70.8 | 72.1 | 69 | 63.2 | 57.7 | 19.1 | 18.1 | 18.7 | 19.1 | 18.6 | 18.7 | 16.8 | 17 | 20.5 | 22.1 | 21 | 18.5 | 26.2 | 26.6 | 26.7 | 28 | 26.9 | 26.4 | 23 | 23.3 | 31.1 | 32.7 | 28.6 | 23.2 | 14.7 | 14.8 | 14.9 | 14.9 | 13.8 | 12.7 | 10.8 | 10.8 | 13.1 | 14.1 | 14.1 | 13.3 | 19.4 | 20.6 | 22 | 23.2 | 23.1 | 23.1 | 21.2 | 21.7 | 25.9 | 25.5 | 21.2 | 14.1 | 12.2 | 12.4 | 13.2 | 13.5 | 12.6 | 11.5 | 10 | 10.1 | 11.6 | 12 | 11.9 | 9.7 | 0.319 | 0.325 | 0.326 | 0.353 | 0.364 | 0.355 | 0.358 | 0.342 | 0.35 | 0.323 | 0.311 | 0.315 | 2.548 | 2.538 | 2.53 | 2.431 | 2.416 | 2.452 | 2.461 | 2.496 | 2.465 | 2.576 | 2.576 | 2.574 | 278 | 290 | 299 | 294 | 291 | 292 | 291 | 294 | 286 | 287 | 279 | 272 | 24 | 28 | 31 | 36 | 37 | 36 | 35 | 33 | 32 | 26 | 23 | 23 | 809 | 1094 | 1543 | 1969 | 2279 | 2487 | 2345 | 2114 | 1803 | 1342 | 941 | 714 | 95 | 122 | 130 | 165 | 135 | 100 | 70 | 80 | 67 | 79 | 52 | 93 | 0.65 | N/A | N/A | N/A | N/A | 1.26 | N/A | -351 | 331 | N/A | 0.67 | N/A | -2.2 | N/A | N/A | N/A | N/A | -194 | 245 | 56 | 44
| MOUNTAIN-VIEW-MOFFETT_STYP20 | 4 | 4 | USA | CA | MOUNTAIN VIEW MOFFETT | 745090 | 23244 | 37.417 | -122.05 | 39 | 14.68 | -8 | NAP | 94-19 | 3C | 12 | 36.4 | 38.8 | 21.1 | 15.9 | 52.3 | 25.4 | 19.4 | 51.1 | 20.5 | 56.5 | 18.2 | 55.5 | 1.3 | 140 | 0.442 | 8 | 16.5 | 88.1 | 65.6 | 83.8 | 64.8 | 80.5 | 64.1 | 68.3 | 82.6 | 66.9 | 79.9 | 65.8 | 77.5 | 9.7 | 340 | 63.2 | 86.9 | 74.2 | 61.6 | 81.9 | 71.9 | 60.8 | 79.8 | 71.1 | 32.5 | 81.9 | 31.4 | 79.9 | 30.5 | 77.6 | 74.8 | 18.8 | 17 | 15.4 | 31.3 | 96.2 | 2.3 | 4.2 | 29.6 | 99.2 | 28.3 | 101.7 | 27 | 104.1 | 25.2 | 107.2 | 28.7 | 70.4 | 2.4 | 2 | 27 | 71.9 | 25.6 | 73.1 | 24.2 | 74.2 | 22.5 | 75.7 | 60.3 | 51.4 | 53.3 | 56.1 | 58.8 | 62 | 66 | 67.8 | 68.1 | 67.9 | 63.6 | 56.5 | 51 | 7.71 | 4.34 | 4.49 | 4.58 | 4.93 | 4.59 | 4.53 | 3.65 | 3.71 | 4.71 | 4.57 | 4.66 | 4.85 | 108 | 35 | 17 | 5 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 44 | 2185 | 422 | 328 | 277 | 197 | 119 | 35 | 10 | 8 | 17 | 82 | 257 | 433 | 3852 | 79 | 109 | 195 | 264 | 372 | 481 | 552 | 562 | 538 | 422 | 202 | 76 | 451 | 0 | 0 | 1 | 10 | 25 | 66 | 97 | 105 | 105 | 39 | 3 | 0 | 2912 | 0 | 3 | 25 | 124 | 242 | 480 | 470 | 502 | 720 | 322 | 24 | 0 | 852 | 0 | 0 | 1 | 29 | 82 | 154 | 116 | 133 | 254 | 82 | 1 | 0 | 5.5 | 3.9 | 4.9 | 5.4 | 6.2 | 6.9 | 7.2 | 7.3 | 6.7 | 5.4 | 4.5 | 3.7 | 4.3 | 13.9 | 2.8 | 2.2 | 2.3 | 1 | 0.2 | 0.1 | 0 | 0 | 0.2 | 0.8 | 2 | 2 | 31.4 | 6.8 | 7.2 | 6.4 | 4 | 1.7 | 0.5 | 0.5 | 0.6 | 1.2 | 3.5 | 5.6 | 4.4 | 6.2 | 0.2 | 0.2 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 5.2 | 1.9 | 2 | 1.6 | 1.1 | 0.4 | 0.1 | 0.1 | 0.2 | 0.3 | 0.9 | 1.7 | 1.2 | 69.3 | 73.3 | 77.4 | 84.4 | 88.7 | 91.3 | 89.6 | 90.4 | 92.7 | 87.7 | 77.8 | 67.2 | 53.1 | 56.6 | 59.6 | 62.9 | 64.1 | 65.5 | 69.4 | 68 | 65.5 | 62.9 | 59 | 55.6 | 64.9 | 68.2 | 72.1 | 77.2 | 80.7 | 84.2 | 83 | 83.3 | 87.3 | 81.6 | 71.6 | 63.9 | 53.4 | 55.3 | 57.3 | 59.8 | 63.1 | 65.1 | 67.1 | 66.8 | 64.8 | 61 | 58.6 | 54.8 | 62.1 | 64.4 | 68.2 | 72.3 | 74.4 | 79.1 | 78.9 | 79.1 | 81.7 | 77.2 | 67.8 | 61.9 | 53.3 | 54 | 56.2 | 58.8 | 60.7 | 64.2 | 65.5 | 65.7 | 64.1 | 59.9 | 56.4 | 54.2 | 59.4 | 61.5 | 65 | 68.1 | 70.7 | 75.1 | 75.6 | 75.7 | 77.2 | 73.1 | 64.7 | 59.7 | 52.3 | 53 | 55.3 | 56.6 | 59 | 62.5 | 64.4 | 64.5 | 63.5 | 59.6 | 55.5 | 53.4 | 59.8 | 59.9 | 62 | 64.9 | 67.5 | 69.3 | 70.5 | 70.1 | 69.5 | 66.8 | 62.9 | 60.4 | 63.9 | 66.9 | 74.2 | 79.9 | 85 | 86.6 | 85.6 | 84.7 | 84.1 | 79 | 72.2 | 63.6 | 56.7 | 57.7 | 59.8 | 62.2 | 63.9 | 66.7 | 67.8 | 68 | 67.1 | 64.6 | 61 | 58.7 | 60.5 | 64.9 | 68.6 | 74.9 | 75.9 | 80.9 | 81.1 | 81 | 80.3 | 75.1 | 68.2 | 62 | 54.9 | 56 | 58.1 | 59.9 | 61.7 | 65 | 66.2 | 66.3 | 65.7 | 62.9 | 59.3 | 56.6 | 59.3 | 62.4 | 65.5 | 69.9 | 73.1 | 77.2 | 77.7 | 77.6 | 78.6 | 72.6 | 64.9 | 59.9 | 53.3 | 54.4 | 56.4 | 58 | 59.9 | 63.3 | 64.9 | 65 | 64.3 | 61.3 | 57.6 | 54.4 | 57.6 | 60.2 | 63.3 | 66.6 | 69.8 | 74.1 | 75.1 | 75 | 75.9 | 70 | 63.1 | 58.3 | 15.2 | 15.4 | 16.6 | 17.6 | 17.1 | 18.3 | 16.6 | 16.5 | 18.9 | 18.8 | 16.8 | 15.2 | 19.5 | 20.8 | 22.1 | 24.7 | 24 | 24.4 | 21.6 | 21.7 | 26.8 | 26.1 | 21.3 | 17.3 | 11 | 11.6 | 11.8 | 12.6 | 11.7 | 11.2 | 9.8 | 9.6 | 11.1 | 11.8 | 11 | 9.9 | 14.3 | 17.1 | 18.8 | 21.7 | 21.5 | 22 | 19.8 | 19.9 | 22.2 | 20.3 | 16.7 | 11.5 | 9.2 | 10.3 | 11 | 11.8 | 11 | 10.5 | 9.4 | 9.3 | 10 | 10 | 10 | 7.9 | 0.324 | 0.333 | 0.338 | 0.359 | 0.37 | 0.362 | 0.366 | 0.348 | 0.353 | 0.335 | 0.322 | 0.324 | 2.541 | 2.516 | 2.492 | 2.407 | 2.396 | 2.426 | 2.423 | 2.47 | 2.442 | 2.533 | 2.55 | 2.55 | 275 | 286 | 294 | 292 | 289 | 290 | 288 | 292 | 285 | 281 | 273 | 266 | 24 | 28 | 32 | 36 | 38 | 36 | 36 | 34 | 33 | 27 | 24 | 23 | 771 | 1069 | 1512 | 1961 | 2257 | 2466 | 2326 | 2082 | 1768 | 1311 | 909 | 680 | 101 | 125 | 132 | 157 | 144 | 102 | 75 | 88 | 68 | 80 | 55 | 95 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | -283 | N/A | N/A | N/A | N/A | -2.11 | N/A | N/A | N/A | N/A | -194 | 239 | N/A | 43
| TRAVIS-AFB_STYP20 | 12 | 4 | USA | CA | TRAVIS AFB | 745160 | 23202 | 38.267 | -121.933 | 62 | 14.66 | -8 | NAP | 94-19 | 3A | 1 | 30.3 | 33.2 | 17.3 | 13.2 | 53.8 | 21.2 | 16 | 52.1 | 29 | 52.2 | 25.9 | 51.8 | 3.8 | 30 | 0.641 | 8 | 30 | 99.2 | 67.5 | 95.4 | 66.6 | 91.4 | 65.6 | 70 | 93.6 | 68.4 | 90.9 | 67 | 88.4 | 10.2 | 240 | 61.5 | 81.7 | 72.3 | 60.1 | 77.8 | 71.5 | 58.9 | 74.6 | 70.9 | 33.8 | 93.7 | 32.5 | 91.1 | 31.4 | 88.1 | 81.5 | 28.8 | 26.8 | 25 | 24.7 | 105.8 | 4.3 | 2.8 | 21.6 | 107.8 | 19.2 | 109.5 | 16.8 | 111 | 13.7 | 113.1 | 23.8 | 73.3 | 4.1 | 2.7 | 20.9 | 75.2 | 18.5 | 76.8 | 16.2 | 78.3 | 13.2 | 80.2 | 60.9 | 47.7 | 50.9 | 55.3 | 58.6 | 64.1 | 70.1 | 72.8 | 73.1 | 71.5 | 64.4 | 54.3 | 47.7 | 10.7 | 4.82 | 4.5 | 4.97 | 5.9 | 5.99 | 5.93 | 4.89 | 4.77 | 5.41 | 5.3 | 5.7 | 5.28 | 284 | 101 | 39 | 11 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 107 | 2483 | 535 | 394 | 302 | 205 | 88 | 14 | 1 | 1 | 8 | 75 | 324 | 536 | 4273 | 31 | 66 | 176 | 262 | 438 | 602 | 707 | 715 | 644 | 445 | 151 | 36 | 994 | 0 | 0 | 1 | 14 | 61 | 166 | 243 | 251 | 202 | 55 | 1 | 0 | 12142 | 0 | 1 | 52 | 306 | 930 | 2191 | 2728 | 2710 | 2348 | 818 | 57 | 1 | 5832 | 0 | 0 | 3 | 84 | 380 | 1099 | 1389 | 1395 | 1197 | 280 | 5 | 0 | 12 | 7.4 | 8.6 | 9.9 | 12.1 | 15.2 | 16.7 | 18.4 | 17 | 13.5 | 10.1 | 7.3 | 7.4 | 21.7 | 4.1 | 4 | 2.8 | 1.2 | 0.8 | 0.2 | 0 | 0 | 0.1 | 1.1 | 2 | 4.3 | 35.4 | 13.3 | 12.9 | 10 | 4.2 | 3.1 | 2 | 0.4 | 0.6 | 0.6 | 5 | 6.3 | 12 | 11.2 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 6.1 | 3.5 | 2.9 | 2.7 | 1 | 0.8 | 0.5 | 0.1 | 0.1 | 0.2 | 1.2 | 1.5 | 3.3 | 68 | 72.2 | 79.4 | 87.9 | 95.4 | 102.3 | 102.8 | 102.7 | 100.3 | 93 | 80.3 | 67.9 | 52.7 | 57.6 | 60.7 | 63.7 | 66.2 | 69.4 | 68.8 | 68.7 | 66.1 | 63.4 | 59.5 | 54.1 | 63.4 | 67.7 | 74.7 | 81.8 | 89.5 | 97.1 | 97.3 | 97.5 | 96.8 | 87.4 | 74.5 | 63.1 | 54 | 56.4 | 59.5 | 61.9 | 64.7 | 68.1 | 67.7 | 67.7 | 65.4 | 62.2 | 58.4 | 53.7 | 60.2 | 63.8 | 71.2 | 77.1 | 84 | 91.3 | 92.6 | 92.8 | 92.2 | 82.2 | 70 | 60.2 | 52.5 | 54 | 58.2 | 60.1 | 62.6 | 65.9 | 67 | 66.6 | 64.2 | 60.1 | 56.3 | 52.5 | 57 | 60.8 | 67.2 | 72.2 | 78.9 | 86.3 | 88.1 | 88 | 87.6 | 78.5 | 65.8 | 57.3 | 51.3 | 52.8 | 56.2 | 58 | 60.9 | 64.4 | 65.9 | 65.8 | 63.4 | 58.8 | 55 | 51.6 | 59.9 | 61.1 | 63.8 | 67.4 | 69.1 | 72.4 | 71.6 | 71.5 | 69.6 | 66.6 | 63.3 | 60.4 | 62.3 | 66.7 | 74.1 | 82.8 | 91 | 96.9 | 98 | 97.1 | 92.5 | 84.5 | 71.1 | 62.9 | 56.3 | 58.8 | 61.4 | 64.1 | 66.3 | 69.3 | 69.2 | 69.2 | 67.5 | 64.4 | 61.1 | 57.5 | 59.7 | 64.4 | 71.5 | 77.7 | 85.9 | 92 | 93.6 | 92.5 | 89.7 | 81.3 | 70 | 59.7 | 54.3 | 56.6 | 59.4 | 61.5 | 64 | 67.2 | 67.7 | 67.6 | 66 | 62.5 | 59.2 | 55.3 | 57.5 | 61.5 | 68.3 | 74.2 | 81.5 | 89.3 | 90.3 | 89.5 | 87.3 | 76.8 | 66.4 | 57.5 | 52.4 | 54.6 | 57.4 | 59.3 | 61.8 | 65.1 | 66.2 | 66.1 | 64.5 | 61 | 57.2 | 53.3 | 55.7 | 58.8 | 64.8 | 70 | 76.5 | 84.5 | 86.8 | 86.6 | 84.4 | 73.6 | 63.5 | 55.7 | 17.2 | 18.7 | 21.3 | 23.4 | 25.3 | 28.5 | 30 | 30 | 29.6 | 26.1 | 22 | 17.9 | 23.8 | 24.9 | 28.3 | 31.8 | 34.1 | 36.9 | 36.6 | 37.4 | 37.6 | 33.8 | 29.3 | 22 | 15.2 | 14.9 | 15.9 | 15.6 | 13.8 | 13.4 | 12.7 | 12.7 | 12.7 | 14.1 | 15.2 | 13.8 | 16.6 | 20.3 | 24.6 | 27.9 | 31.3 | 34.2 | 33.8 | 33.4 | 32.3 | 28.1 | 23.2 | 13.9 | 12.5 | 13.6 | 14.6 | 14.9 | 13.9 | 13.5 | 12.8 | 12.5 | 12 | 12.5 | 13.7 | 10.7 | 0.32 | 0.322 | 0.335 | 0.355 | 0.36 | 0.359 | 0.36 | 0.346 | 0.345 | 0.329 | 0.323 | 0.326 | 2.526 | 2.524 | 2.473 | 2.398 | 2.408 | 2.417 | 2.407 | 2.437 | 2.445 | 2.52 | 2.518 | 2.511 | 274 | 289 | 294 | 293 | 292 | 291 | 289 | 292 | 286 | 282 | 270 | 262 | 24 | 28 | 32 | 37 | 37 | 37 | 37 | 35 | 33 | 27 | 24 | 23 | 715 | 1034 | 1469 | 1938 | 2320 | 2575 | 2534 | 2264 | 1859 | 1325 | 871 | 634 | 121 | 132 | 147 | 163 | 138 | 105 | 72 | 71 | 63 | 87 | 60 | 102 | N/A | -1.71 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.68 | N/A | -2.02 | N/A | N/A | N/A | N/A | -211 | 236 | N/A | 49
| CHINA-LAKE_STYP20 | 14 | 4 | USA | CA | CHINA LAKE | 746120 | 93104 | 35.688 | -117.693 | 2230 | 13.55 | -8 | NAP | 07-19 | 3B | 12 | 23.1 | 26.5 | -7.6 | 4 | 47.2 | -2.9 | 5.1 | 47.3 | 31.3 | 55.3 | 27.8 | 55 | 2.9 | 200 | 0.519 | 7 | 31.4 | 108.3 | 65.2 | 106 | 64.5 | 103.8 | 63.6 | 69 | 97.6 | 67.7 | 97.6 | 66.3 | 97 | 10.7 | 170 | 59.6 | 82.8 | 79.3 | 55.9 | 72.3 | 83.3 | 52.5 | 63.7 | 81.5 | 34.3 | 97.4 | 33.1 | 97.4 | 32 | 97.4 | 74.3 | 27.5 | 24.4 | 20.7 | 16.8 | 112.2 | 3.5 | 1.8 | 14.3 | 113.5 | 12.3 | 114.6 | 10.4 | 115.6 | 7.9 | 117 | 13.4 | 71.7 | 3.3 | 2.2 | 11 | 73.3 | 9.1 | 74.5 | 7.2 | 75.7 | 4.8 | 77.3 | 65.7 | 45.9 | 49.8 | 57.6 | 64.1 | 71.6 | 82 | 88.2 | 86.4 | 78.6 | 65.5 | 53.7 | 44.2 | 16.26 | 5.93 | 6.23 | 6.47 | 6.79 | 7.05 | 6.27 | 4.45 | 4.1 | 6.4 | 6.23 | 6.49 | 5.97 | 474 | 152 | 75 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 35 | 196 | 2431 | 593 | 426 | 239 | 95 | 24 | 0 | 0 | 0 | 3 | 66 | 339 | 646 | 6210 | 24 | 69 | 249 | 424 | 669 | 961 | 1184 | 1127 | 857 | 483 | 147 | 16 | 2692 | 0 | 0 | 11 | 68 | 228 | 511 | 719 | 662 | 410 | 82 | 1 | 0 | 43226 | 5 | 32 | 384 | 1248 | 3534 | 8109 | 11702 | 10434 | 6051 | 1551 | 176 | 0 | 26697 | 1 | 0 | 85 | 458 | 1838 | 5212 | 7933 | 6915 | 3639 | 597 | 19 | 0 | 7.6 | 5.3 | 7.3 | 8.8 | 9.8 | 9.3 | 8.7 | 8 | 7.9 | 7.3 | 6.9 | 5.6 | 5.8 | 4 | 0.8 | 1.1 | 0.5 | 0.1 | 0.1 | 0 | 0.1 | 0.1 | 0.2 | 0.2 | 0.3 | 0.6 | 9.4 | 5.1 | 4.4 | 2.6 | 1.4 | 0.8 | 0.2 | 0.7 | 0.6 | 2.1 | 1.2 | 1.3 | 3 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 1.1 | 1.1 | 0.6 | 0.3 | 0.2 | 0 | 0.1 | 0.1 | 0.4 | 0.3 | 0.3 | 0.7 | 71.7 | 77.9 | 87.1 | 93.5 | 101.2 | 110.4 | 111.8 | 108.8 | 104.8 | 93.8 | 82.6 | 69 | 50.1 | 51.6 | 55 | 58.2 | 60.6 | 64.4 | 66.1 | 65.5 | 65.2 | 59.9 | 53.7 | 50 | 67.4 | 74.5 | 82.2 | 89 | 96.9 | 106.5 | 109.3 | 106.7 | 101.6 | 90 | 79.3 | 65.1 | 47.1 | 50.5 | 53.6 | 55.8 | 59 | 63.4 | 65.6 | 65.1 | 63.1 | 58.9 | 51.9 | 47.4 | 64 | 70.5 | 78.1 | 85.4 | 94 | 103.9 | 106.8 | 104.8 | 99.2 | 86.6 | 75.2 | 61.8 | 46.1 | 49.1 | 51.9 | 54.6 | 58 | 62.1 | 65 | 64.3 | 62.4 | 56.4 | 51.3 | 45.9 | 60.5 | 66.3 | 74.6 | 81.8 | 90.3 | 100.7 | 104.3 | 102.6 | 96.7 | 82.8 | 70.2 | 58.3 | 45 | 47.1 | 50.7 | 53.5 | 57.2 | 61.3 | 64.3 | 63.3 | 61.2 | 54.8 | 48.9 | 44.4 | 53.5 | 54.7 | 56.5 | 59.5 | 61.8 | 67.4 | 71 | 70.7 | 68.6 | 64.3 | 55.4 | 53.5 | 62.6 | 66.6 | 76.9 | 87.4 | 97.1 | 104.1 | 92.2 | 97.8 | 95 | 82.9 | 76.5 | 62.5 | 50.9 | 51.4 | 54.9 | 57.3 | 60.1 | 65.5 | 69.2 | 68.9 | 67 | 61.4 | 53.6 | 51.1 | 59.5 | 70.7 | 75.9 | 85.1 | 92.9 | 100.6 | 98 | 97.2 | 95.6 | 81.8 | 74.5 | 60.8 | 49 | 50 | 53.3 | 55.8 | 59 | 63.9 | 68.2 | 67.1 | 65.1 | 59 | 52 | 48.6 | 58.4 | 68.1 | 75.6 | 81.9 | 90.5 | 98.7 | 97.7 | 96.9 | 92.3 | 81 | 71.8 | 57.5 | 46.8 | 48.3 | 51.7 | 54.3 | 57.7 | 62.4 | 66.9 | 65.6 | 63 | 56.9 | 50.3 | 45.9 | 58.5 | 64.3 | 72.4 | 79.1 | 87.9 | 96.7 | 97.4 | 96.8 | 91.4 | 78.3 | 68.5 | 55.5 | 28 | 28.8 | 29.3 | 29.9 | 30.7 | 33.1 | 31.4 | 32.7 | 32.7 | 32.1 | 31.2 | 26.6 | 33.7 | 35.8 | 35.9 | 35.1 | 35.9 | 36.6 | 33.9 | 34.1 | 34.8 | 36.7 | 36.7 | 32 | 18.6 | 17.5 | 15.8 | 14.2 | 13 | 11.9 | 11 | 11.6 | 12.7 | 16.3 | 18.6 | 18.5 | 24.7 | 32.3 | 32.4 | 32.2 | 34.6 | 34.4 | 27.5 | 29.3 | 29.8 | 29.5 | 32.9 | 24.1 | 14.9 | 16.3 | 14.4 | 13.6 | 13 | 10.9 | 9.4 | 10.5 | 10.6 | 12.6 | 17.1 | 15 | 0.267 | 0.277 | 0.285 | 0.31 | 0.327 | 0.322 | 0.345 | 0.334 | 0.314 | 0.292 | 0.269 | 0.268 | 2.582 | 2.57 | 2.539 | 2.463 | 2.44 | 2.46 | 2.451 | 2.455 | 2.516 | 2.571 | 2.604 | 2.594 | 302 | 310 | 314 | 309 | 303 | 303 | 295 | 297 | 300 | 300 | 299 | 295 | 24 | 27 | 30 | 35 | 36 | 36 | 36 | 35 | 31 | 27 | 23 | 22 | 961 | 1277 | 1751 | 2193 | 2491 | 2713 | 2523 | 2357 | 2012 | 1506 | 1106 | 871 | 72 | 117 | 75 | 81 | 101 | 96 | 106 | 69 | 52 | 77 | 46 | 65 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1.15 | N/A | -3.06 | 0.77 | N/A | N/A | N/A | -209 | 382 | 207 | 28
| LEMORE-NAS_STYP20 | 13 | 4 | USA | CA | LEMORE NAS | 747020 | 23110 | 36.333 | -119.95 | 232 | 14.57 | -8 | NAP | 94-19 | 3B | 12 | 28.3 | 31.1 | 17.4 | 13.3 | 41.1 | 20.7 | 15.6 | 44.3 | 24.4 | 51.6 | 20.2 | 50.6 | 4.2 | 260 | 0.484 | 7 | 34.5 | 103.7 | 70 | 101.3 | 69.1 | 98.9 | 68.4 | 73.2 | 97.4 | 71.4 | 96.1 | 69.9 | 94.6 | 8.4 | 10 | 64.3 | 91.1 | 84.8 | 62.1 | 84.1 | 83.7 | 59.8 | 77.4 | 81.9 | 36.8 | 97.1 | 35.2 | 96.2 | 33.8 | 94.7 | 82.6 | 21 | 18.2 | 16 | 25.2 | 108 | 4.2 | 2.1 | 22.1 | 109.5 | 19.7 | 110.7 | 17.3 | 111.9 | 14.3 | 113.4 | 23.3 | 75.9 | 4.4 | 2.9 | 20.2 | 78 | 17.6 | 79.6 | 15.2 | 81.3 | 12 | 83.4 | 63.8 | 48 | 51.5 | 57.2 | 61.8 | 68.4 | 75.6 | 81.1 | 80 | 75.1 | 65.1 | 54.4 | 46.8 | 13.16 | 5.26 | 5.44 | 5.73 | 6.72 | 6.79 | 6.22 | 4.46 | 4.47 | 6.12 | 5.88 | 6.07 | 5.55 | 313 | 101 | 43 | 9 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 132 | 2293 | 526 | 378 | 247 | 140 | 42 | 3 | 0 | 0 | 4 | 70 | 319 | 564 | 5356 | 40 | 86 | 232 | 355 | 571 | 767 | 965 | 930 | 752 | 467 | 158 | 33 | 1861 | 0 | 0 | 6 | 43 | 148 | 320 | 500 | 465 | 306 | 72 | 1 | 0 | 27832 | 1 | 12 | 223 | 873 | 2397 | 4966 | 7324 | 6556 | 4141 | 1239 | 100 | 0 | 15952 | 0 | 1 | 40 | 321 | 1155 | 2923 | 4627 | 4069 | 2335 | 473 | 8 | 0 | 7.1 | 5.2 | 6.1 | 7.2 | 8.9 | 9.1 | 8.8 | 7.8 | 7.3 | 7.1 | 6.4 | 5.4 | 5.5 | 6.9 | 1.3 | 1.4 | 1.3 | 0.6 | 0.3 | 0.1 | 0 | 0 | 0.2 | 0.3 | 0.9 | 0.9 | 15 | 5.4 | 4.6 | 4.8 | 2.3 | 2.2 | 0.4 | 0.2 | 0.4 | 1.2 | 1.3 | 2.7 | 3.7 | 3.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 2.6 | 1.3 | 1.3 | 1.1 | 0.6 | 0.5 | 0.1 | 0 | 0.1 | 0.4 | 0.4 | 0.7 | 0.7 | 70 | 75.6 | 84.7 | 93.4 | 99.4 | 105.8 | 106.4 | 106 | 102.5 | 95.7 | 81.2 | 69.2 | 54.1 | 58.8 | 60.8 | 64.2 | 65.6 | 70.8 | 69.8 | 71.3 | 68.9 | 65.8 | 60.9 | 58 | 64.5 | 70.4 | 79.7 | 88.2 | 95 | 102 | 103.7 | 102.5 | 99.5 | 89.6 | 77.1 | 64.1 | 54.4 | 57.5 | 60 | 62.4 | 64.3 | 68.6 | 70 | 70 | 67.8 | 63.4 | 59.1 | 55.2 | 61.4 | 66.6 | 75.8 | 83.3 | 91 | 98.3 | 101.3 | 100 | 96.6 | 85 | 72.6 | 60.5 | 53.1 | 56.1 | 58.1 | 60.7 | 62.9 | 66.9 | 69.5 | 69.3 | 67.1 | 61.7 | 58.1 | 52.9 | 58.4 | 63.2 | 72 | 78.9 | 86.8 | 94.8 | 98.6 | 97.4 | 93.1 | 81.2 | 68.1 | 57 | 52.1 | 54.8 | 57.1 | 58.8 | 61.4 | 65.7 | 69.2 | 68.1 | 66.2 | 60.4 | 55.8 | 51.1 | 59.6 | 62.3 | 64.1 | 67.3 | 68.3 | 73.2 | 75.5 | 76.6 | 74.2 | 68.2 | 63.1 | 60.7 | 64.7 | 69.6 | 78.6 | 86.8 | 93.7 | 101.2 | 99.1 | 99.4 | 95.4 | 88 | 76.9 | 66.1 | 56.4 | 59.4 | 61.5 | 64.1 | 66.1 | 70.7 | 73 | 73.1 | 71 | 66 | 61 | 57 | 61 | 67.1 | 75.3 | 84.5 | 91.6 | 97.7 | 97.5 | 97.5 | 90.8 | 85.6 | 74 | 61.7 | 54.5 | 57.4 | 59.7 | 61.8 | 64.2 | 68.6 | 71.3 | 70.9 | 68.6 | 63.9 | 59.1 | 54.6 | 59.3 | 65 | 72.7 | 80.5 | 88.1 | 94.8 | 97 | 95.4 | 92 | 81.4 | 70.4 | 58.4 | 52.6 | 55.3 | 57.8 | 59.6 | 62.2 | 66.7 | 69.9 | 69.1 | 67 | 61.5 | 56.9 | 52.3 | 57.5 | 62 | 70.1 | 76.7 | 84.4 | 91.9 | 95.2 | 93.4 | 90.7 | 77.7 | 67 | 56 | 19.6 | 21.8 | 26.3 | 29.1 | 30.4 | 33.8 | 34.5 | 34.8 | 33.2 | 30.7 | 26 | 19.3 | 25.4 | 27.5 | 33 | 35.8 | 36.5 | 37.9 | 36.5 | 36.4 | 36.8 | 36.3 | 32.1 | 24 | 17.3 | 17.2 | 17 | 17.1 | 15.1 | 14.7 | 14.1 | 14 | 15.1 | 17.5 | 19.4 | 16.3 | 19.4 | 23.4 | 28.7 | 32.4 | 33.8 | 35.7 | 34 | 34.8 | 34 | 31.3 | 28.4 | 16.8 | 13.7 | 15.6 | 15.8 | 16 | 14.5 | 14.3 | 14 | 14.6 | 14.5 | 15.2 | 17.7 | 12.3 | 0.349 | 0.363 | 0.364 | 0.362 | 0.362 | 0.356 | 0.374 | 0.355 | 0.362 | 0.383 | 0.375 | 0.347 | 2.371 | 2.34 | 2.347 | 2.374 | 2.391 | 2.406 | 2.385 | 2.414 | 2.406 | 2.304 | 2.278 | 2.385 | 264 | 275 | 286 | 292 | 292 | 292 | 286 | 290 | 283 | 263 | 250 | 257 | 30 | 34 | 37 | 38 | 38 | 37 | 38 | 36 | 35 | 35 | 32 | 28 | 794 | 1140 | 1617 | 2050 | 2428 | 2681 | 2570 | 2358 | 1968 | 1438 | 986 | 729 | 107 | 123 | 132 | 147 | 120 | 83 | 85 | 63 | 56 | 74 | 54 | 94 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.95 | N/A | -1.98 | 0.92 | N/A | N/A | N/A | -266 | 319 | 88 | 29
| ONTARIO_STYP20 | 10 | 4 | USA | CA | ONTARIO | 747040 | 03102 | 34.056 | -117.6 | 949 | 14.2 | -8 | NAP | 94-19 | 3A | 12 | 38.7 | 41 | 3.5 | 6.8 | 66.1 | 9.6 | 9.3 | 64.3 | 33.5 | 62.4 | 28 | 62.4 | 2.8 | 40 | 0.416 | 8 | 27.5 | 100.4 | 69.2 | 97.6 | 68.3 | 94.8 | 67.4 | 73 | 93.6 | 71.4 | 91.4 | 70.1 | 89.4 | 12 | 260 | 66.3 | 100.2 | 79.8 | 64.4 | 93.8 | 77.7 | 63.5 | 90.7 | 76 | 37 | 93.5 | 35.8 | 91.7 | 34.5 | 89.4 | 82.9 | 21 | 17.4 | 15.5 | 32.7 | 107.5 | 3.5 | 3.3 | 30.2 | 109.9 | 28.1 | 111.8 | 26.1 | 113.7 | 23.5 | 116 | 28.6 | 75.6 | 2.8 | 2.3 | 26.6 | 77.3 | 25 | 78.6 | 23.4 | 79.9 | 21.4 | 81.5 | 66.5 | 56.4 | 56.4 | 60.3 | 63.2 | 67.1 | 72.6 | 78.7 | 79.7 | 76.7 | 69.2 | 61.6 | 55.4 | 10.39 | 6.04 | 6 | 6.22 | 6.62 | 6.13 | 5.73 | 4.75 | 4.97 | 6.27 | 6.41 | 6.38 | 5.43 | 38 | 11 | 9 | 2 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 13 | 1323 | 273 | 247 | 173 | 110 | 46 | 7 | 0 | 0 | 1 | 29 | 138 | 299 | 6065 | 210 | 189 | 320 | 398 | 529 | 679 | 890 | 921 | 801 | 595 | 351 | 182 | 1878 | 7 | 8 | 26 | 57 | 110 | 236 | 425 | 456 | 353 | 160 | 37 | 3 | 20211 | 129 | 167 | 413 | 755 | 1141 | 2350 | 4450 | 4938 | 3630 | 1654 | 509 | 75 | 10170 | 16 | 36 | 122 | 286 | 486 | 1126 | 2412 | 2790 | 1964 | 755 | 171 | 6 | 6 | 5.1 | 5.2 | 6 | 6.8 | 7.1 | 7 | 6.9 | 6.4 | 5.8 | 5.6 | 4.7 | 5 | 22.4 | 5 | 5.6 | 3 | 1.5 | 0.6 | 0.2 | 0.1 | 0.1 | 0.2 | 0.9 | 1.4 | 3.6 | 39.9 | 20.9 | 16.3 | 11.5 | 4.4 | 5.6 | 1.3 | 0.6 | 0.4 | 1.2 | 6.4 | 3.2 | 11.9 | 9.5 | 0.4 | 0.2 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.6 | 9.2 | 5.4 | 4.1 | 3 | 1.1 | 1.2 | 0.4 | 0.2 | 0.1 | 0.3 | 1.4 | 0.9 | 2.9 | 82.2 | 84.6 | 89.4 | 93.6 | 97 | 101.5 | 103.2 | 104.6 | 103.9 | 97.9 | 90.5 | 80.8 | 54.8 | 56.4 | 58.8 | 60.1 | 64.4 | 68.4 | 70.7 | 70.6 | 68.1 | 62.9 | 58.5 | 53.7 | 77.8 | 79.4 | 83.4 | 87.6 | 90.5 | 95.3 | 98.6 | 100.1 | 99.3 | 92.9 | 85.3 | 75.5 | 53 | 54.6 | 57.8 | 59.1 | 63 | 67.6 | 70.9 | 69.9 | 68.6 | 61.7 | 57.4 | 52.3 | 73.6 | 74.1 | 78.7 | 82.3 | 85.6 | 90.5 | 95.2 | 97.1 | 95.4 | 88.5 | 80 | 71.8 | 51.9 | 53.2 | 56.5 | 58.1 | 62.5 | 66.5 | 69.3 | 68.7 | 67.3 | 60.5 | 55.8 | 51 | 69.7 | 68.6 | 73.4 | 77.6 | 80.5 | 86.8 | 92.1 | 93.4 | 91 | 83.5 | 74.9 | 67.1 | 50.8 | 52.1 | 55.4 | 56.7 | 61.9 | 65.9 | 68.6 | 68.1 | 66 | 59.6 | 54 | 50.1 | 60 | 60.6 | 63.9 | 65.2 | 69.8 | 72.2 | 75.6 | 75.9 | 73.3 | 69.4 | 62.4 | 59.4 | 69.6 | 74.7 | 79 | 85.1 | 89.5 | 91.9 | 97 | 95.6 | 95.5 | 84 | 73.6 | 66.4 | 57.2 | 57.9 | 61 | 62.7 | 66.8 | 69.7 | 73 | 73 | 71.3 | 66.5 | 60.3 | 57.3 | 66 | 68.1 | 76.2 | 80.4 | 84.7 | 89.6 | 93.2 | 93.7 | 91.8 | 81.1 | 73.3 | 65.4 | 55.4 | 56.1 | 59.1 | 60.3 | 64.6 | 68.2 | 71.3 | 71.2 | 69.7 | 64.6 | 58.8 | 55.4 | 63.9 | 67.1 | 72.1 | 75.7 | 80.7 | 86.6 | 90.9 | 91.4 | 88.9 | 79.3 | 72.2 | 62.8 | 53.9 | 54.5 | 57.3 | 58.6 | 62.7 | 66.6 | 69.8 | 69.5 | 68.2 | 62.8 | 57.3 | 53.7 | 63.2 | 64.6 | 69.1 | 72.7 | 76.6 | 83.4 | 88.1 | 89.4 | 85.5 | 76.3 | 69.4 | 61.1 | 20.8 | 19.8 | 21.5 | 22.3 | 21.9 | 24.9 | 26.8 | 27.5 | 25.8 | 23.5 | 23 | 20.8 | 28.7 | 30.1 | 30.5 | 31.2 | 30.9 | 31.1 | 29.5 | 30.4 | 30.8 | 31.9 | 31.3 | 29.2 | 12.9 | 12.5 | 12.4 | 12 | 11.3 | 10.3 | 9.9 | 10.5 | 10.3 | 11.5 | 12.5 | 13.3 | 20.3 | 22.4 | 25.2 | 26.8 | 27.6 | 28.9 | 27.6 | 27.9 | 27.4 | 26.3 | 24.8 | 19.3 | 10.6 | 10.6 | 11.4 | 11.2 | 10.8 | 10.5 | 10 | 10.3 | 9.8 | 10.3 | 11 | 10.1 | 0.304 | 0.313 | 0.335 | 0.35 | 0.352 | 0.362 | 0.377 | 0.361 | 0.345 | 0.338 | 0.301 | 0.3 | 2.544 | 2.534 | 2.448 | 2.413 | 2.437 | 2.422 | 2.442 | 2.474 | 2.505 | 2.496 | 2.591 | 2.587 | 290 | 299 | 298 | 297 | 295 | 291 | 286 | 290 | 291 | 285 | 289 | 285 | 26 | 29 | 34 | 37 | 36 | 37 | 36 | 34 | 32 | 30 | 24 | 23 | 1022 | 1307 | 1759 | 2141 | 2348 | 2523 | 2430 | 2299 | 1957 | 1490 | 1139 | 927 | 71 | 128 | 88 | 96 | 124 | 128 | 115 | 61 | 59 | 90 | 55 | 64 | 1.1 | N/A | -5.17 | N/A | N/A | N/A | N/A | -148 | 425 | 248 | 1.13 | N/A | -3.06 | 1.3 | N/A | N/A | N/A | -202 | 401 | 202 | 51
| IMPERIAL-COUNTY-AP_STYP20 | 15 | 4 | USA | CA | IMPERIAL COUNTY AP | 747185 | 03144 | 32.834 | -115.579 | -58 | 14.73 | -8 | NAP | 94-19 | 2B | 12 | 35.9 | 38.5 | 9.2 | 8.8 | 61 | 13.1 | 10.7 | 61.1 | 26.8 | 63 | 23.9 | 63.5 | 4.6 | 260 | 0.468 | 8 | 26.3 | 111.9 | 72.7 | 109.5 | 72.3 | 107.8 | 72 | 80.9 | 97.1 | 79.5 | 96.3 | 78.2 | 95.9 | 7.2 | 110 | 76.9 | 140 | 88.5 | 75 | 130.8 | 88.8 | 72.9 | 121.8 | 89.2 | 44.3 | 97 | 42.9 | 95.8 | 41.5 | 96.1 | 89.2 | 26.1 | 22.3 | 18.8 | 30.7 | 117.1 | 3.4 | 2.9 | 28.2 | 119.2 | 26.2 | 120.9 | 24.3 | 122.6 | 21.8 | 124.7 | 25.9 | 83.8 | 3 | 2.7 | 23.7 | 85.7 | 22 | 87.3 | 20.3 | 88.8 | 18.1 | 90.8 | 74.2 | 56.8 | 59.5 | 66.1 | 71.2 | 78.6 | 87.5 | 93.5 | 93.7 | 87.6 | 75.4 | 64.2 | 55.6 | 14.58 | 5.01 | 5.84 | 6.2 | 6.3 | 6.51 | 5.56 | 3.7 | 3.75 | 5.65 | 6.38 | 6.16 | 5.1 | 23 | 8 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 10 | 893 | 256 | 167 | 63 | 18 | 1 | 0 | 0 | 0 | 0 | 6 | 88 | 294 | 8869 | 220 | 270 | 500 | 635 | 888 | 1125 | 1350 | 1356 | 1128 | 787 | 427 | 183 | 4263 | 2 | 14 | 98 | 203 | 424 | 675 | 885 | 891 | 678 | 328 | 63 | 2 | 65067 | 108 | 339 | 1485 | 2737 | 5800 | 10323 | 14530 | 14580 | 10166 | 4057 | 881 | 61 | 41961 | 6 | 68 | 589 | 1324 | 3453 | 6938 | 10238 | 10257 | 6642 | 2164 | 279 | 3 | 7.1 | 5.4 | 6.6 | 7.9 | 9.5 | 9.2 | 8.6 | 7.9 | 7 | 6.5 | 6.3 | 5.5 | 5.2 | 2.4 | 0.4 | 0.3 | 0.2 | 0.1 | 0 | 0 | 0.1 | 0.1 | 0.3 | 0.2 | 0.3 | 0.3 | 4.9 | 1.5 | 1.3 | 1 | 0.6 | 0.1 | 0 | 1.1 | 0.5 | 3 | 1.9 | 1.7 | 1.6 | 0.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 0.5 | 0.4 | 0.3 | 0.2 | 0 | 0 | 0.2 | 0.2 | 0.7 | 0.4 | 0.5 | 0.4 | 80.3 | 86.1 | 93.9 | 99.7 | 107.9 | 113.9 | 115.4 | 114.6 | 110.2 | 101.9 | 90.5 | 79.3 | 56.7 | 58.6 | 61.4 | 64.3 | 67.6 | 70.2 | 73.5 | 73.6 | 71.6 | 68 | 60.7 | 57.7 | 77.1 | 82 | 90.2 | 95.4 | 102.5 | 110 | 112.1 | 111.5 | 107.8 | 98.6 | 86.7 | 75.2 | 55 | 57.6 | 60.4 | 62.5 | 65.9 | 69.7 | 73.3 | 73.4 | 71.2 | 66.9 | 59.6 | 55.3 | 73.9 | 78.6 | 86.5 | 91.5 | 99.7 | 107.4 | 109.3 | 109.1 | 105.4 | 95 | 83.2 | 72.3 | 54 | 56.8 | 59.3 | 61.1 | 65.9 | 68.7 | 72.8 | 73.8 | 70.8 | 64.5 | 59.1 | 53.8 | 71.2 | 74.4 | 82.6 | 88 | 96.4 | 104.3 | 107.4 | 107 | 102.3 | 91.3 | 79.4 | 68.9 | 53.4 | 55 | 58.2 | 60.1 | 64.3 | 67.9 | 72.6 | 73.7 | 71.1 | 63.4 | 57.7 | 52.2 | 61.9 | 63.7 | 65.6 | 67.9 | 73.5 | 78.2 | 81.9 | 84 | 81.8 | 75.1 | 64.9 | 61.3 | 74.2 | 78.6 | 85.1 | 90.8 | 96.6 | 101.4 | 101.5 | 99.9 | 96.4 | 91.1 | 80.9 | 72.8 | 59 | 60.6 | 62.5 | 65 | 69.8 | 75.7 | 80 | 81.4 | 79.5 | 71.4 | 62.3 | 58.6 | 70.5 | 75.1 | 84.4 | 89.4 | 94.2 | 97.7 | 98.4 | 96.4 | 94.5 | 86.9 | 80.5 | 69.7 | 56.9 | 58.3 | 60.8 | 63.1 | 67.6 | 73.4 | 78.6 | 80 | 77.6 | 68.5 | 60.5 | 56.6 | 68.9 | 73.6 | 82.6 | 87.4 | 94.1 | 96.6 | 97.1 | 95.9 | 94 | 87.3 | 79.5 | 67.5 | 54.7 | 56.4 | 59.1 | 61.2 | 65.7 | 71.3 | 77.4 | 78.6 | 75.7 | 65.8 | 58.8 | 54.1 | 67.5 | 71.5 | 80 | 85.1 | 92.2 | 96.4 | 96.4 | 95.6 | 93.6 | 87.4 | 77.4 | 65.5 | 27 | 26.5 | 28.5 | 28.9 | 30.1 | 31.6 | 27.2 | 26.3 | 27.7 | 28.8 | 27.8 | 25.9 | 31.6 | 31.8 | 33.6 | 33.7 | 34.2 | 34.5 | 30.1 | 29.1 | 30.1 | 32.5 | 31.8 | 29.7 | 16.9 | 15.5 | 14.4 | 13.5 | 12.6 | 12.8 | 11.2 | 11.3 | 11.5 | 13.2 | 14.8 | 15.8 | 25.4 | 27 | 31 | 31.3 | 32.6 | 30.9 | 24.2 | 23.5 | 23.8 | 26.7 | 28 | 24.3 | 15.2 | 14.6 | 14.4 | 13.3 | 13 | 13 | 10.4 | 10.5 | 12.6 | 12.6 | 14.1 | 13.8 | 0.291 | 0.295 | 0.313 | 0.33 | 0.348 | 0.349 | 0.393 | 0.388 | 0.351 | 0.321 | 0.295 | 0.291 | 2.514 | 2.523 | 2.457 | 2.411 | 2.379 | 2.38 | 2.365 | 2.372 | 2.437 | 2.49 | 2.531 | 2.54 | 297 | 307 | 307 | 304 | 297 | 295 | 282 | 282 | 290 | 293 | 293 | 291 | 27 | 29 | 34 | 37 | 39 | 39 | 39 | 38 | 34 | 30 | 26 | 25 | 1110 | 1419 | 1882 | 2300 | 2564 | 2675 | 2428 | 2260 | 1991 | 1602 | 1213 | 1004 | 56 | 99 | 68 | 58 | 70 | 93 | 98 | 90 | 71 | 65 | 53 | 54 | 0.94 | N/A | -2.84 | N/A | N/A | N/A | N/A | N/A | 391 | 293 | 0.86 | N/A | -2.32 | 1.06 | N/A | N/A | N/A | -137 | 313 | 164 | 23
| DESERT-RESORTS_STYP20 | 15 | 4 | USA | CA | DESERT RESORTS | 747187 | 03104 | 33.627 | -116.159 | -118 | 14.76 | -8 | NAP | 94-19 | 2B | 12 | 31.7 | 34.9 | 4.4 | 6.9 | 65.7 | 8.8 | 8.6 | 64.7 | 20.8 | 62 | 18.1 | 62.6 | 3 | 340 | 0.471 | 7 | 29.4 | 112.6 | 72 | 109.7 | 71.5 | 107.8 | 71 | 79.6 | 97.1 | 78.2 | 97 | 77 | 97 | 7.5 | 140 | 74.9 | 130.3 | 88.9 | 72.8 | 121.2 | 89.3 | 70.6 | 112.1 | 90.1 | 42.9 | 96.6 | 41.5 | 96.9 | 40.2 | 96.8 | 88 | 20.6 | 18.3 | 16.2 | 24.7 | 118.7 | 3.9 | 3.1 | 21.9 | 121 | 19.6 | 122.8 | 17.4 | 124.6 | 14.6 | 126.8 | 21.2 | 81.9 | 3.6 | 1.9 | 18.7 | 83.2 | 16.6 | 84.3 | 14.6 | 85.3 | 12 | 86.7 | 73.2 | 55.7 | 58.7 | 66.1 | 71.6 | 79.3 | 86.8 | 92.4 | 91.6 | 85.6 | 74 | 62.3 | 54 | 14.55 | 5.57 | 5.91 | 6.4 | 6.56 | 6.1 | 5.57 | 4.51 | 4.46 | 5.34 | 5.99 | 6.47 | 5.38 | 43 | 15 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 21 | 1038 | 292 | 188 | 66 | 17 | 1 | 0 | 0 | 0 | 0 | 8 | 124 | 342 | 8529 | 191 | 248 | 498 | 648 | 907 | 1103 | 1314 | 1291 | 1067 | 745 | 371 | 146 | 4049 | 3 | 12 | 99 | 215 | 443 | 653 | 849 | 826 | 617 | 288 | 42 | 2 | 65688 | 199 | 436 | 1728 | 3156 | 6285 | 10751 | 14676 | 14097 | 9419 | 3918 | 929 | 94 | 42681 | 28 | 115 | 741 | 1611 | 3765 | 7322 | 10477 | 9942 | 6186 | 2156 | 329 | 9 | 6.5 | 4.7 | 5.5 | 7.1 | 8.7 | 9.1 | 8.2 | 7 | 6.4 | 6.4 | 5.9 | 4.8 | 4.5 | 2.5 | 0.4 | 0.6 | 0.4 | 0 | 0.1 | 0 | 0.1 | 0.2 | 0.2 | 0.1 | 0.2 | 0.2 | 6.6 | 2.4 | 3.4 | 1.7 | 0.5 | 0.8 | 0.4 | 1.1 | 3.6 | 2.4 | 0.5 | 1.7 | 1 | 0.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7 | 0.6 | 0.8 | 0.4 | 0.1 | 0.2 | 0.1 | 0.2 | 0.7 | 0.5 | 0.1 | 0.4 | 0.3 | 83.4 | 88.1 | 96.3 | 102.2 | 108.4 | 115.3 | 117.1 | 115.3 | 111.5 | 103.8 | 92.1 | 81 | 55.8 | 58.3 | 61.2 | 64 | 68.8 | 70.9 | 74.9 | 72.4 | 71.2 | 67 | 60.8 | 56.7 | 79.2 | 83.6 | 91.5 | 97.5 | 103.7 | 110.2 | 112.4 | 111.9 | 108 | 99.2 | 88 | 76.5 | 55 | 56.6 | 59.9 | 62.2 | 66.2 | 69.2 | 72.7 | 72.7 | 70.5 | 65.6 | 59.8 | 55.1 | 75.4 | 79.8 | 88.1 | 93.3 | 100 | 107.4 | 109.4 | 109.1 | 105.2 | 95.2 | 83.8 | 72.9 | 53.7 | 55.8 | 58.9 | 60.9 | 65.3 | 68.7 | 72 | 72.5 | 69.9 | 63.6 | 58.5 | 53.1 | 72 | 75.2 | 83.9 | 89.4 | 96.7 | 104.4 | 107.2 | 106.4 | 102.1 | 91.6 | 79.5 | 69.5 | 52.5 | 54.2 | 57.3 | 59.4 | 64.2 | 67.8 | 71.8 | 72.2 | 69.6 | 63 | 57 | 51.6 | 60.3 | 62.3 | 63.7 | 67 | 72.9 | 77 | 80.6 | 81.9 | 80.4 | 72.8 | 64.3 | 60.6 | 74.3 | 79.4 | 87.4 | 96.5 | 102.5 | 103.3 | 99 | 97.9 | 95.2 | 90.2 | 83.3 | 74.9 | 58 | 59.5 | 61.9 | 64.3 | 69.5 | 74.1 | 78.9 | 80.2 | 78 | 69.8 | 61.8 | 58 | 71 | 75.3 | 85.6 | 91.7 | 96.2 | 99.9 | 97.6 | 97.1 | 95.2 | 89.1 | 82.4 | 70.2 | 56.1 | 57.5 | 60.4 | 62.5 | 67.4 | 72.1 | 77.6 | 78.7 | 76.1 | 67.4 | 60 | 55.9 | 70 | 73.9 | 83.4 | 88.6 | 93.4 | 99.4 | 97.6 | 96.8 | 94.4 | 90 | 80.3 | 68 | 54.1 | 55.9 | 58.9 | 60.9 | 65.7 | 70.3 | 76.5 | 77.4 | 74.1 | 65.1 | 58.4 | 53.6 | 68.6 | 72 | 80.5 | 85.7 | 92.4 | 98.1 | 97.6 | 96.8 | 93.6 | 87 | 77 | 65.8 | 31 | 30.5 | 31.3 | 30.6 | 30.1 | 32.9 | 29.4 | 29.5 | 31.8 | 32.7 | 32.8 | 30.5 | 36.7 | 37.5 | 38.2 | 38.2 | 35.7 | 35.9 | 31.8 | 32.2 | 34.9 | 38.8 | 38.1 | 35.1 | 18.2 | 16.8 | 14.7 | 13.6 | 11.4 | 11.8 | 11.3 | 11.6 | 11.9 | 14.5 | 16.9 | 18.1 | 30.8 | 31 | 34 | 34.3 | 33.9 | 34.5 | 26.3 | 26 | 27.6 | 33.1 | 33.7 | 29.1 | 16.2 | 14.9 | 13.7 | 12.8 | 11.5 | 13.1 | 11.1 | 12.3 | 12.7 | 13.9 | 15.7 | 16 | 0.305 | 0.308 | 0.328 | 0.352 | 0.369 | 0.369 | 0.405 | 0.395 | 0.36 | 0.337 | 0.309 | 0.308 | 2.496 | 2.505 | 2.435 | 2.373 | 2.353 | 2.368 | 2.367 | 2.38 | 2.446 | 2.47 | 2.524 | 2.521 | 289 | 300 | 301 | 296 | 291 | 289 | 278 | 280 | 286 | 286 | 286 | 282 | 27 | 30 | 35 | 38 | 40 | 39 | 39 | 38 | 34 | 30 | 26 | 25 | 1063 | 1363 | 1836 | 2247 | 2525 | 2681 | 2443 | 2279 | 1987 | 1564 | 1176 | 962 | 65 | 113 | 81 | 70 | 88 | 97 | 108 | 95 | 72 | 75 | 51 | 57 | 1.19 | N/A | -3.04 | N/A | -0.76 | N/A | N/A | N/A | 387 | 281 | 0.97 | N/A | -2.97 | 1.06 | N/A | N/A | N/A | -149 | 346 | 187 | 38
| BLYTHE_STYP20 | 15 | 4 | USA | CA | BLYTHE | 747188 | 23158 | 33.619 | -114.714 | 395 | 14.49 | -8 | NAP | 94-19 | 1B | 12 | 36.9 | 39.7 | -1.3 | 5.2 | 55.6 | 2.9 | 6.5 | 57.6 | 28.1 | 60.4 | 25.4 | 60.8 | 3.9 | 350 | 0.485 | 7 | 25.3 | 113 | 71.5 | 110.8 | 71 | 108.7 | 70.5 | 77.9 | 98.2 | 76.9 | 97.5 | 75.9 | 96.9 | 10.6 | 160 | 73.1 | 124.7 | 85.2 | 71.4 | 117.7 | 86.6 | 69.2 | 108.9 | 89.5 | 41.5 | 97.6 | 40.4 | 96.9 | 39.4 | 96.7 | 84.6 | 24.3 | 20.5 | 18.2 | 30.2 | 117.6 | 2.8 | 2.7 | 28.2 | 119.6 | 26.6 | 121.2 | 25 | 122.7 | 22.9 | 124.7 | 23.9 | 80.1 | 2.9 | 1.6 | 21.8 | 81.2 | 20.1 | 82.2 | 18.4 | 83 | 16.3 | 84.2 | 74.7 | 56.2 | 59.3 | 66.2 | 72.2 | 80.5 | 89.5 | 95.3 | 94.8 | 88.1 | 75.5 | 63.5 | 54.4 | 15.43 | 5.19 | 5.71 | 6.38 | 6.56 | 6.83 | 5.87 | 4.14 | 4.1 | 5.66 | 6.54 | 6.23 | 5.11 | 31 | 11 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 16 | 961 | 276 | 171 | 64 | 15 | 1 | 0 | 0 | 0 | 0 | 6 | 100 | 328 | 9048 | 202 | 264 | 503 | 665 | 945 | 1184 | 1404 | 1388 | 1143 | 790 | 406 | 154 | 4502 | 2 | 12 | 102 | 230 | 480 | 734 | 939 | 923 | 693 | 332 | 54 | 1 | 72798 | 46 | 248 | 1445 | 3239 | 7313 | 12566 | 16492 | 15961 | 10713 | 4076 | 677 | 22 | 48531 | 2 | 36 | 550 | 1603 | 4473 | 8804 | 12105 | 11595 | 7051 | 2116 | 195 | 1 | 7.7 | 6.4 | 7 | 7.5 | 9 | 8.9 | 9.2 | 9.5 | 8.5 | 7.1 | 6.7 | 6.1 | 6.4 | 3.5 | 0.5 | 0.5 | 0.4 | 0.1 | 0 | 0 | 0.2 | 0.6 | 0.4 | 0.2 | 0.2 | 0.3 | 9.2 | 2.3 | 3 | 2.2 | 1 | 0.1 | 0.1 | 1.2 | 2.1 | 2.1 | 1.9 | 0.9 | 2.2 | 1.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9 | 0.6 | 0.7 | 0.6 | 0.2 | 0 | 0 | 0.3 | 0.6 | 0.6 | 0.4 | 0.2 | 0.5 | 78.3 | 84.1 | 94.1 | 100.7 | 109.1 | 115.7 | 116.6 | 114.5 | 110.3 | 102.1 | 89.5 | 76.9 | 54.1 | 56.8 | 59.8 | 62.7 | 67.9 | 69.2 | 73.2 | 72.4 | 70.3 | 66.7 | 58.8 | 55.6 | 74.9 | 80.7 | 89.7 | 96.9 | 104.7 | 111.5 | 113.3 | 112.3 | 107.6 | 97.8 | 85.5 | 72.6 | 52.8 | 55.8 | 58.5 | 61.3 | 65.7 | 68.5 | 71.8 | 72.3 | 70.4 | 65.2 | 58.2 | 53.2 | 71.9 | 77.1 | 86.2 | 93.1 | 101.3 | 108.8 | 110.8 | 109.9 | 105.3 | 94.7 | 81.6 | 69.6 | 51.9 | 54.3 | 57.4 | 60 | 63.8 | 67.6 | 71.8 | 72.1 | 70 | 63.5 | 57.2 | 51.8 | 68.6 | 73.1 | 82.5 | 89.3 | 98 | 106.4 | 108.5 | 107.8 | 102.5 | 91.2 | 77.6 | 66.3 | 50.7 | 53 | 56 | 58.3 | 62.8 | 67.1 | 71.2 | 71.9 | 69.7 | 62.3 | 55.5 | 49.7 | 59.6 | 61.4 | 62.2 | 65 | 70.5 | 75.3 | 78.9 | 79.5 | 78.7 | 73.2 | 63.8 | 59.5 | 70 | 75.7 | 85.5 | 96.1 | 104.6 | 104.4 | 100.6 | 100.1 | 95.6 | 88.8 | 78.4 | 69.9 | 57.1 | 58.9 | 60.3 | 62.6 | 67.6 | 73.2 | 77.4 | 78.1 | 77 | 69.4 | 60.5 | 57 | 66.6 | 72.2 | 82.9 | 91.8 | 100.1 | 102.8 | 99.1 | 98.7 | 94.1 | 88.5 | 78.1 | 66.6 | 55 | 56.8 | 58.9 | 61 | 65.5 | 71.2 | 76.4 | 77.2 | 75.6 | 67.2 | 58.7 | 54.7 | 65.7 | 70.2 | 81.6 | 89.5 | 96.9 | 100.8 | 98.4 | 97.9 | 93.1 | 87.3 | 77.8 | 64.7 | 52.7 | 54.9 | 57.3 | 59.4 | 63.8 | 69.1 | 75.3 | 76.2 | 74.3 | 64.6 | 56.9 | 52.3 | 64.3 | 69.2 | 79.1 | 86.5 | 94.6 | 101.3 | 97.9 | 97.4 | 92.7 | 86.1 | 75.7 | 62.6 | 24.1 | 24.8 | 27.2 | 28.1 | 28.8 | 30.2 | 25.3 | 24.6 | 26.1 | 27.3 | 26.2 | 23.3 | 28.2 | 30.1 | 32.5 | 33.5 | 32.5 | 32.4 | 28 | 27.1 | 28.6 | 30.8 | 30.8 | 26.9 | 14.9 | 14.6 | 13.7 | 14.1 | 12.8 | 11.9 | 9.7 | 9.6 | 11.1 | 13.4 | 15.3 | 14.8 | 22.1 | 24.8 | 29.5 | 31.1 | 30.1 | 28 | 21.8 | 21.8 | 22 | 25 | 27 | 22.4 | 12.3 | 12.4 | 12.5 | 13.1 | 12.2 | 11.4 | 8.1 | 8.4 | 9.6 | 11.6 | 14.4 | 12.7 | 0.279 | 0.282 | 0.298 | 0.322 | 0.335 | 0.338 | 0.383 | 0.377 | 0.341 | 0.307 | 0.285 | 0.28 | 2.572 | 2.586 | 2.511 | 2.431 | 2.415 | 2.417 | 2.399 | 2.406 | 2.477 | 2.536 | 2.576 | 2.585 | 301 | 311 | 312 | 306 | 301 | 298 | 284 | 285 | 293 | 297 | 296 | 295 | 25 | 27 | 32 | 36 | 37 | 37 | 38 | 37 | 33 | 28 | 24 | 23 | 1086 | 1404 | 1871 | 2298 | 2574 | 2684 | 2410 | 2238 | 1975 | 1574 | 1192 | 980 | 57 | 97 | 66 | 63 | 64 | 88 | 93 | 88 | 66 | 64 | 51 | 56 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 0.68 | N/A | -3.24 | N/A | -0.72 | N/A | N/A | N/A | 277 | 173 | 13
ENDTABLE