## Rev1 Based on ACH (hidden)
Input Value
Calculated Value
| Sash Control Fraction | 1 |  |  |  | VAV Exhaust | 0.12
| Zone SF | 900 | ft2 |  |  | CAV Exhaust | 0.9
| Zone Height | 9 | ft
| Zone Volume | 8100 | ft3 |  |  | Fraction of Vent | Fraction of Exh
| Code Min Occupied (Design) Exhaust Flow (CFM_eu) | 900 | cfm | 1 | cfm/ft2 | 0.55556
| Occupied (Design) Exhaust Flow, VAV (CFM_eo) | 1620 | cfm | 12 | ACH | 1 | 1
| Unoccupied (Min) Exhaust Flow (CFM_eu) | 194.4 | cfm | 1.44 | ACH | 0.12 | 0.12
| Unoccupied (Min) Exhaust Flow, CAV (CFM_eu) | 1458 |  | 10.8 | ACH | 0.9 | 0.9
| Ventilation System OA Fraction | 1
| Occupied (Design) Terminal Flow (CFM_to) | 1620 | cfm | 12 | ACH | 1 | 1
| Unoccupied (Min) Terminal Flow (CFM_tu) | 270 | cfm | 2 | ACH | 0.16667 | 0.16667
| Code Unoccupied (Min) Vent Flow (CFM_vumin) | 0 | cfm | 0 | ACH | 0 | 0
| Modeled Unoccupied Terminal Flow Fraction,VAV | 0
| Modeled Unoccupied Terminal Flow Fraction,CAV | 0.9
| Modeled Unoccupied Terminal Flow (CFM_vumodel) | 0 | cfm | 2 | ACH | 0 | 0
Hour of Day
| Description |  | Daily Sch | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
| LabExhaustHoodVAVNoSashCtrl | Fraction | WD | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.4128 | 0.4718 | 0.37 | 0.37 | 0.4128 | 0.5308 | 0.4718 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37
|  |  | Sat | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37
|  |  | Sun | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37
| LabExhaustHoodVAVSashCtrl | Fraction | WD | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.3062 | 0.3807 | 0.4179 | 0.269 | 0.3062 | 0.3807 | 0.4552 | 0.4179 | 0.3062 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
|  |  | Sat | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
|  |  | Sun | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
| LabExhaustHoodCAV | Fraction | WD | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  | Sun | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
1) | Calculate exhaust flow schedule, which is function of zone sash control fraction
| LabExhaustHoodVAVComposite | Fraction | WD | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.3062 | 0.3807 | 0.4179 | 0.269 | 0.3062 | 0.3807 | 0.4552 | 0.4179 | 0.3062 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
|  |  | Sat | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
|  |  | Sun | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
2) | Multiply CFM_eu x 1)
| Exhaust Flow | 12 | WD | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 3.6744 | 4.5684 | 5.0148 | 3.228 | 3.6744 | 4.5684 | 5.4624 | 5.0148 | 3.6744 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44
|  |  | Sat | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44
|  |  | Sun | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44 | 1.44
|  |  | WD | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8
|  |  | Sat | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8
|  |  | Sun | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8
3) | Subtract CFM_vumin from 2)
| Diff Vent vs Exh |  | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6744 | 2.5684 | 3.0148 | 1.228 | 1.6744 | 2.5684 | 3.4624 | 3.0148 | 1.6744 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | WD | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8
|  |  | Sat | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8
|  |  | Sun | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8
4) | Add 'AllOn' schedule x CFM_vumin to 3)
| TerminalUnit (Vent) Flow | 2 | WD | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3.6744 | 4.5684 | 5.0148 | 3.228 | 3.6744 | 4.5684 | 5.4624 | 5.0148 | 3.6744 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | Sat | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | Sun | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
|  |  | WD | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8
|  |  | Sat | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8
|  |  | Sun | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8
5) | Multiply 1/CFM_eu x 4)
| TerminalUnit (Vent) Flow Fraction | 0.083333 | WD | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.3062 | 0.3807 | 0.4179 | 0.269 | 0.3062 | 0.3807 | 0.4552 | 0.4179 | 0.3062 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667
|  |  | Sat | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667
|  |  | Sun | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667
|  | 0.092593 |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Schedule Function Options/Inputs
Interpolate between two schedules with fraction
Scaled schedule values by a constant or by the values of another schedule
Union of two or more schedules
Schedule Function Outputs
New schedule
EFLH (Fraction, OnOff)
Max
Min
Note on E16: David Reddy: IN simulation, can't be less than min exhaust
Note on E17: David Reddy: Set to 0 if there is no code minimum ventilation flow for the zone. In this case, ventilation modeled to track exhaust.

## OffSml-Lab_SZVAV25-ap
| Input Value | [6 empty] | Proj:LabExhCAVMinFrac | 0.9
| Calculated Value | [6 empty] | Proj:LabExhVAVManualSashCtrlMinFrac | 0.5
[8 empty] | Proj:LabExhVAVAutoSashCtrlMinFrac | 0.2
Proj: | OffSml-Lab_SZVAV25
|  | SDD Property | Input/Calc
| Exhaust Control |  | VAV
| Zone SF |  | 5502 | ft2
| Zone Height |  | 10 | ft
| Zone Volume |  | 55020 | ft3 |  |  |  | MinVentFlowFrac | 0.25
| Total Fume Hood Length |  | 57 |  |  |  |  | MinExhFlowFrac | 0.25
| Hood Density |  | 10.3599
| Vertical Sash Fume Hood Exhaust Flow |  | 14250 |  | 250 | CFM/LF
| Space Vertical Sash Fume Hood Auto Sash Control Frac |  | 0
| Other Exhaust Flow |  | 422
| Zone Exh Flow Auto Sash Control Frac | ThrmlZn:LabExhFlowAutoSashCtrlFrac | 0
| Occupied (Design) Exhaust Flow, VAV (CFM_eo) |  | 14672 | cfm | 16 | ACH | 2.6667 | CFM/ft2
| Unoccupied (Min) Exhaust Flow, VAV (CFM_vaveu) |  | 3668 | cfm | 4 | ACH | 0.66667 | CFM/ft2
|  | ThrmlZn:LabExhFlowMinSchFrac | 0.5
| Ventilation System OA Fraction |  | 1
| Occupied (Design) Terminal Flow (CFM_to) |  | 14672 | cfm | 16 | ACH | 2.6667 | CFM/ft2
| Unoccupied (Min) Terminal Flow (CFM_tu) |  | 3668 | cfm | 4 | ACH | 0.66667 | CFM/ft2
| Code Unoccupied (Min) Vent Flow (CFM_vumin) |  | 3668 | cfm | 4 | ACH | 0.66667 | CFM/ft2
| LabExhToTrmlUnitFlowMaxFrac | TrmlUnit:LabExhToTrmlUnitFlowMaxFrac | 1 |  |  |  | 0.00018175
|  | TrmlUnit:LabExhToTrmlUnitFlowMinFrac | 0.5
| Modeled Unoccupied Terminal Flow Fraction | TrmlUnit:LabTrmlUnitFlowMinFrac | 0.5
| Modeled Unoccupied Terminal Flow (CFM_vumodel) |  | 7336 | cfm | 4 | ACH
Hour of Day
| Description |  |  | Daily Sch | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
| LabExhaustVAVManualSashCtrl |  | Fraction | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.51 | 0.56 | 0.56 | 0.53 | 0.53 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.52 | 0.52 | 0.52 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  |  | Sun | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.52 | 0.52 | 0.52 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
| LabExhaustVAVAutoSashCtrl |  | Fraction | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.21 | 0.22 | 0.33 | 0.33 | 0.26 | 0.26 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.24 | 0.21 | 0.21 | 0.21 | 0.2 | 0.2
|  |  |  | Sat | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.21 | 0.21 | 0.24 | 0.24 | 0.24 | 0.24 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
|  |  |  | Sun | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.21 | 0.21 | 0.24 | 0.24 | 0.24 | 0.24 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
| LabExhaustCAV |  | Fraction | WD | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sun | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
| LabUnoccExhaustFraction |  | Fraction | WD | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | New for 2025. Enforce exhaust flow schdule to be equal to ratio of occ/unocc
|  |  |  | Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Sun | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
| LabOccupancySch |  | Fraction | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.9 | 0.9 | 0.45 | 0.45 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
|  |  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sun | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
| LabOccupiedSch |  | Fraction | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
1) | Calculate "composite" exhaust flow schedule, which is function of zone sash control fraction
| ZnExhCtrlFlowSchRef |  | Fraction | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.51 | 0.56 | 0.56 | 0.53 | 0.53 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
| Schedule assigned to: ExhFlowSchRef |  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.52 | 0.52 | 0.52 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  |  | Sun | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.52 | 0.52 | 0.52 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
2) | Calculate ratio of zone ExhFlow:TrmlUnit flow
| VAV Exhaust |  |  | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.51 | 0.56 | 0.56 | 0.53 | 0.53 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.52 | 0.52 | 0.52 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  |  | Sun | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.52 | 0.52 | 0.52 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
3) | Subtract TrmlUnit:PriAirFlowMin from ExhFlow:TrmlUnit flow fraction
|  |  | 0.5 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.06 | 0.06 | 0.03 | 0.03 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.02 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0.02 | 0.02 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.02 | 0.02 | 0.02 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4) | Add 3) to determine TrmlUnit:PriAirFlowMin fraction
| LabTrmlUnitMinAirFracSchRef |  | 0.5 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.51 | 0.56 | 0.56 | 0.53 | 0.53 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
| Schedule assigned to: MinAirFracSchRef |  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.52 | 0.52 | 0.52 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  |  | Sun | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.52 | 0.52 | 0.52 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Calculated flows for graph
| VAV Exhaust |  |  | WD | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8.16 | 8.96 | 8.96 | 8.48 | 8.48 | 8.96 | 8.96 | 8.96 | 8.96 | 8.96 | 8.32 | 8 | 8 | 8 | 8 | 8
|  |  |  | Sat | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8.32 | 8.32 | 8.32 | 8.32 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
|  |  |  | Sun | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8.32 | 8.32 | 8.32 | 8.32 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
| TerminalUnit (Vent) Flow Fraction |  |  | WD | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8.16 | 8.96 | 8.96 | 8.48 | 8.48 | 8.96 | 8.96 | 8.96 | 8.96 | 8.96 | 8.32 | 8 | 8 | 8 | 8 | 8
|  |  |  | Sat | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8.32 | 8.32 | 8.32 | 8.32 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
|  |  |  | Sun | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8.32 | 8.32 | 8.32 | 8.32 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
Schedule Function Options/Inputs
Interpolate between two schedules with fraction
Scaled schedule values by a constant or by the values of another schedule
Union of two or more schedules
Schedule Function Outputs
New schedule
EFLH (Fraction, OnOff)
Max
Min
Note on F22: David Reddy: IN simulation, can't be less than min exhaust
Note on F23: David Reddy: Set to 0 if there is no code minimum ventilation flow for the zone. In this case, ventilation modeled to track exhaust.

## OffSml-Lab_SZVAV25-ab
| Input Value | [6 empty] | Proj:LabExhCAVMinFrac | 0.9
| Calculated Value | [6 empty] | Proj:LabExhVAVManualSashCtrlMinFrac | 0.5
[8 empty] | Proj:LabExhVAVAutoSashCtrlMinFrac | 0.2
Proj: | OffSml-Lab_SZVAV25
|  | SDD Property | Input/Calc
| Exhaust Control |  | VAV
| Zone SF |  | 5502 | ft2
| Zone Height |  | 10 | ft
| Zone Volume |  | 55020 | ft3 |  |  |  | MinVentFlowFrac | 0.25
| Total Fume Hood Length |  | 57 |  |  |  |  | MinExhFlowFrac | 0.25
| Hood Density |  | 10.3599
| Vertical Sash Fume Hood Exhaust Flow |  | 14250 |  | 250 | CFM/LF
| Space Vertical Sash Fume Hood Auto Sash Control Frac |  | 1
| Other Exhaust Flow |  | 422
| Zone Exh Flow Auto Sash Control Frac | ThrmlZn:LabExhFlowAutoSashCtrlFrac | 0.97124
| Occupied (Design) Exhaust Flow, VAV (CFM_eo) |  | 14672 | cfm | 16 | ACH | 2.6667 | CFM/ft2
| Unoccupied (Min) Exhaust Flow, VAV (CFM_vaveu) |  | 3668 | cfm | 4 | ACH | 0.66667 | CFM/ft2
|  | ThrmlZn:LabExhFlowMinSchFrac | 0.2
| Ventilation System OA Fraction |  | 1
| Occupied (Design) Terminal Flow (CFM_to) |  | 14672 | cfm | 16 | ACH | 2.6667 | CFM/ft2
| Unoccupied (Min) Terminal Flow (CFM_tu) |  | 3668 | cfm | 4 | ACH | 0.66667 | CFM/ft2
| Code Unoccupied (Min) Vent Flow (CFM_vumin) |  | 3668 | cfm | 4 | ACH | 0.66667 | CFM/ft2
| LabExhToTrmlUnitFlowMaxFrac | TrmlUnit:LabExhToTrmlUnitFlowMaxFrac | 1 |  |  |  | 0.00018175
|  | TrmlUnit:LabExhToTrmlUnitFlowMinFrac | 0.2
| Modeled Unoccupied Terminal Flow Fraction | TrmlUnit:LabTrmlUnitFlowMinFrac | 0.25
| Modeled Unoccupied Terminal Flow (CFM_vumodel) |  | 3668 | cfm | 4 | ACH
Hour of Day
| Description |  |  | Daily Sch | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
| LabExhaustVAVManualSashCtrl |  | Fraction | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.51 | 0.56 | 0.56 | 0.53 | 0.53 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.52 | 0.52 | 0.52 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  |  | Sun | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.52 | 0.52 | 0.52 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
| LabExhaustVAVAutoSashCtrl |  | Fraction | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.21 | 0.22 | 0.33 | 0.33 | 0.26 | 0.26 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.24 | 0.21 | 0.21 | 0.21 | 0.2 | 0.2
|  |  |  | Sat | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.21 | 0.21 | 0.24 | 0.24 | 0.24 | 0.24 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
|  |  |  | Sun | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.21 | 0.21 | 0.24 | 0.24 | 0.24 | 0.24 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
| LabExhaustCAV |  | Fraction | WD | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sun | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
| LabUnoccExhaustFraction |  | Fraction | WD | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | New for 2025. Enforce exhaust flow schdule to be equal to ratio of occ/unocc
|  |  |  | Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Sun | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
| LabOccupancySch |  | Fraction | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.9 | 0.9 | 0.45 | 0.45 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
|  |  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sun | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
| LabOccupiedSch |  | Fraction | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
1) | Calculate "composite" exhaust flow schedule, which is function of zone sash control fraction
| ExhCtrlFlowSchRef |  | Fraction | WD | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.33662 | 0.33662 | 0.26777 | 0.26777 | 0.33662 | 0.33662 | 0.33662 | 0.33662 | 0.33662 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
| Schedule assigned to: ExhFlowSchRef |  |  | Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Sun | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
2) | Calculate ratio of zone ExhFlow:TrmlUnit flow
|  |  |  | WD | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.33662 | 0.33662 | 0.26777 | 0.26777 | 0.33662 | 0.33662 | 0.33662 | 0.33662 | 0.33662 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Sun | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
3) | Subtract TrmlUnit:PriAirFlowMin from ExhFlow:TrmlUnit flow fraction
| TrmlUnit:LabTrmlUnitMinAirFracAddSchRef |  | 0.25 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.086615 | 0.086615 | 0.017766 | 0.017766 | 0.086615 | 0.086615 | 0.086615 | 0.086615 | 0.086615 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4) | Add 3) to determine TrmlUnit:PriAirFlowMin fraction
| TrmlUnit:LabTrmlUnitMinAirFracSchRef |  | 0.25 | WD | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.33662 | 0.33662 | 0.26777 | 0.26777 | 0.33662 | 0.33662 | 0.33662 | 0.33662 | 0.33662 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
| Schedule assigned to: MinAirFracSchRef |  |  | Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  |  | Sun | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Calculated flows for graph
| VAV Exhaust |  |  | WD | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5.3858 | 5.3858 | 4.2843 | 4.2843 | 5.3858 | 5.3858 | 5.3858 | 5.3858 | 5.3858 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Sat | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Sun | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
| TerminalUnit (Vent) Flow Fraction |  |  | WD | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5.3858 | 5.3858 | 4.2843 | 4.2843 | 5.3858 | 5.3858 | 5.3858 | 5.3858 | 5.3858 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Sat | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Sun | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Schedule Function Options/Inputs
Interpolate between two schedules with fraction
Scaled schedule values by a constant or by the values of another schedule
Union of two or more schedules
Schedule Function Outputs
New schedule
EFLH (Fraction, OnOff)
Max
Min
Note on F22: David Reddy: IN simulation, can't be less than min exhaust
Note on F23: David Reddy: Set to 0 if there is no code minimum ventilation flow for the zone. In this case, ventilation modeled to track exhaust.

## OffLrg-PrkgLab25-ap
| Input Value | [6 empty] | Proj:LabExhCAVMinFrac | 0.9
| Calculated Value | [6 empty] | Proj:LabExhVAVManualSashCtrlMinFrac | 0.5
[8 empty] | Proj:LabExhVAVAutoSashCtrlMinFrac | 0.2
Proj: | OffLrg-PrkgLab25
|  | SDD Property | Input/Calc
| Exhaust Control |  | VAV
| Zone SF |  | 32805.3 | ft2
| Zone Height |  | 9 | ft
| Zone Volume |  | 295247.7 | ft3 |  |  |  | MinVentFlowFrac | 0.25
| Total Fume Hood Length |  | 130 |  |  |  |  | MinExhFlowFrac | 0.25
| Hood Density |  | 4.4031
| Vertical Sash Fume Hood Exhaust Flow |  | 32500 |  | 250 | CFM/LF
| Space Vertical Sash Fume Hood Auto Sash Control Frac |  | 0
| Other Exhaust Flow |  | 305.3
| Zone Exh Flow Auto Sash Control Frac | ThrmlZn:LabExhFlowAutoSashCtrlFrac | 0
| Occupied (Design) Exhaust Flow, VAV (CFM_eo) |  | 32805.3 | cfm | 6.6667 | ACH | 1 | CFM/ft2
| Unoccupied (Min) Exhaust Flow, VAV (CFM_vaveu) |  | 19683.18 | cfm | 4 | ACH | 0.6 | CFM/ft2
|  | ThrmlZn:LabExhFlowMinSchFrac | 0.5
| Ventilation System OA Fraction |  | 1
| Occupied (Design) Terminal Flow (CFM_to) |  | 98415.9 | cfm | 20 | ACH | 3 | CFM/ft2
| Unoccupied (Min) Terminal Flow (CFM_tu) |  | 19683.18 | cfm | 4 | ACH | 0.6 | CFM/ft2
| Code Unoccupied (Min) Vent Flow (CFM_vumin) |  | 19683.18 | cfm | 4 | ACH | 0.6 | CFM/ft2
| LabExhToTrmlUnitFlowMaxFrac | TrmlUnit:LabExhToTrmlUnitFlowMaxFrac | 0.33333 |  |  |  | 1.0161e-05
|  | TrmlUnit:LabExhToTrmlUnitFlowMinFrac | 0.16667
| Modeled Unoccupied Terminal Flow Fraction | TrmlUnit:LabTrmlUnitFlowMinFrac | 0.2
| Modeled Unoccupied Terminal Flow (CFM_vumodel) |  | 19683.18 | cfm | 4 | ACH
Hour of Day
| Description |  |  | Daily Sch | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
| LabExhaustVAVManualSashCtrl |  | Fraction | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.51 | 0.56 | 0.56 | 0.53 | 0.53 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.52 | 0.52 | 0.52 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  |  | Sun | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.52 | 0.52 | 0.52 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
| LabExhaustVAVAutoSashCtrl |  | Fraction | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.21 | 0.22 | 0.33 | 0.33 | 0.26 | 0.26 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.24 | 0.21 | 0.21 | 0.21 | 0.2 | 0.2
|  |  |  | Sat | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.21 | 0.21 | 0.24 | 0.24 | 0.24 | 0.24 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
|  |  |  | Sun | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.21 | 0.21 | 0.24 | 0.24 | 0.24 | 0.24 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
| LabExhaustCAV |  | Fraction | WD | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  |  | Sun | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
| LabUnoccExhaustFraction |  | Fraction | WD | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | New for 2025. Enforce exhaust flow schdule to be equal to ratio of occ/unocc
|  |  |  | Sat | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
|  |  |  | Sun | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
| LabOccupancySch |  | Fraction | WD | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.2 | 0.9 | 0.9 | 0.45 | 0.45 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.3 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05
|  |  |  | Sat | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
|  |  |  | Sun | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3 | 0.3 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
| LabOccupiedSch |  | Fraction | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0
|  |  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
1) | Calculate exhaust flow schedule, which is function of zone sash control fraction
| LabExhaustHoodVAVComposite |  | Fraction | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.51 | 0.56 | 0.56 | 0.53 | 0.53 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.52 | 0.52 | 0.52 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  |  | Sun | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.52 | 0.52 | 0.52 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
2) | Calculate ratio of zone ExhFlow:TrmlUnit flow
|  |  |  | WD | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.17 | 0.18667 | 0.18667 | 0.17667 | 0.17667 | 0.18667 | 0.18667 | 0.18667 | 0.18667 | 0.18667 | 0.17333 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667
|  |  |  | Sat | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.17333 | 0.17333 | 0.17333 | 0.17333 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667
|  |  |  | Sun | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.17333 | 0.17333 | 0.17333 | 0.17333 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667 | 0.16667
3) | Subtract TrmlUnit:PriAirFlowMin from ExhFlow:TrmlUnit flow fraction
| VAV Exhaust |  | 0.2 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4) | Add 3) to TrmlUnit:PriAirFlowMin fraction
| TerminalUnit (Vent) Flow |  | 0.2 | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
|  |  |  | Sat | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
|  |  |  | Sun | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
Calculated flows for graph
| VAV Exhaust |  |  | WD | 3.3333 | 3.3333 | 3.3333 | 3.3333 | 3.3333 | 3.3333 | 3.3333 | 3.3333 | 3.4 | 3.7333 | 3.7333 | 3.5333 | 3.5333 | 3.7333 | 3.7333 | 3.7333 | 3.7333 | 3.7333 | 3.4667 | 3.3333 | 3.3333 | 3.3333 | 3.3333 | 3.3333
|  |  |  | Sat | 3.3333 | 3.3333 | 3.3333 | 3.3333 | 3.3333 | 3.3333 | 3.3333 | 3.3333 | 3.3333 | 3.4667 | 3.4667 | 3.4667 | 3.4667 | 3.3333 | 3.3333 | 3.3333 | 3.3333 | 3.3333 | 3.3333 | 3.3333 | 3.3333 | 3.3333 | 3.3333 | 3.3333
|  |  |  | Sun | 3.3333 | 3.3333 | 3.3333 | 3.3333 | 3.3333 | 3.3333 | 3.3333 | 3.3333 | 3.3333 | 3.4667 | 3.4667 | 3.4667 | 3.4667 | 3.3333 | 3.3333 | 3.3333 | 3.3333 | 3.3333 | 3.3333 | 3.3333 | 3.3333 | 3.3333 | 3.3333 | 3.3333
| TerminalUnit (Vent) Flow Fraction |  |  | WD | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Sat | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  |  |  | Sun | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Schedule Function Options/Inputs
Interpolate between two schedules with fraction
Scaled schedule values by a constant or by the values of another schedule
Union of two or more schedules
Schedule Function Outputs
New schedule
EFLH (Fraction, OnOff)
Max
Min
Note on F22: David Reddy: IN simulation, can't be less than min exhaust
Note on F23: David Reddy: Set to 0 if there is no code minimum ventilation flow for the zone. In this case, ventilation modeled to track exhaust.

## OffSml-Lab_SZVAV22-ap
Input Value
Calculated Value
Proj: | OffSml-Lab_SZVAV25
| Exhaust Control | VAV
| Zone SF | 5502 | ft2 |  |  |  | CAV Exhaust min Frac | 0.9
| Zone Height | 10 | ft |  |  |  | VAV Auto Sash Min Frac | 0.20863
| Zone Volume | 55020 | ft3
| Total Fume Hood Length | 57
| Hood Density | 10.3599
| Vertical Sash Fume Hood Exhaust Flow | 14250 |  | 250 | CFM/LF
| Space Vertical Sash Fume Hood Auto Sash Control Frac | 1
| Other Exhaust Flow | 422
| Zone Exh Flow Auto Sash Control Frac | 0.97124
| Occupied (Design) Exhaust Flow, VAV (CFM_eo) | 14672 | cfm | 16 | ACH
| Unoccupied (Min) Exhaust Flow, VAV (CFM_vaveu) | 3061 | cfm | 3.3381 | ACH
| Ventilation System OA Fraction | 1
| Occupied (Design) Terminal Flow (CFM_to) | 14672 | cfm | 16 | ACH
| Unoccupied (Min) Terminal Flow (CFM_tu) | 3668 | cfm | 4 | ACH | 0.25 | 0.052157
| Code Unoccupied (Min) Vent Flow (CFM_vumin) | 3668 | cfm | 4 | ACH
| Modeled Unoccupied Terminal Flow Fraction,VAV | 0.25
| Modeled Unoccupied Terminal Flow Fraction,CAV | 0.9
| Modeled Unoccupied Terminal Flow (CFM_vumodel) | 3668 | cfm | 4 | ACH
Hour of Day
| Description |  | Daily Sch | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
| LabExhaustVAVManualSashCtrl | Fraction | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.51 | 0.56 | 0.56 | 0.53 | 0.53 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.52 | 0.52 | 0.52 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | Sun | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.52 | 0.52 | 0.52 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
| LabExhaustVAVAutoSashCtrl | Fraction | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.21 | 0.22 | 0.33 | 0.33 | 0.26 | 0.26 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.24 | 0.21 | 0.21 | 0.21 | 0.2 | 0.2
|  |  | Sat | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.21 | 0.21 | 0.24 | 0.24 | 0.24 | 0.24 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
|  |  | Sun | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.21 | 0.21 | 0.24 | 0.24 | 0.24 | 0.24 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
| LabExhaustCAV | Fraction | WD | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  | Sun | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
1) | Calculate exhaust flow schedule, which is function of zone sash control fraction
| LabExhaustHoodVAVComposite | Fraction | WD | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.21834 | 0.22834 | 0.33662 | 0.33662 | 0.26777 | 0.26777 | 0.33662 | 0.33662 | 0.33662 | 0.33662 | 0.33662 | 0.24805 | 0.21834 | 0.21834 | 0.21834 | 0.20863 | 0.20863
|  |  | Sat | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.21834 | 0.21834 | 0.24805 | 0.24805 | 0.24805 | 0.24805 | 0.21834 | 0.21834 | 0.21834 | 0.21834 | 0.21834 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863
|  |  | Sun | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.21834 | 0.21834 | 0.24805 | 0.24805 | 0.24805 | 0.24805 | 0.21834 | 0.21834 | 0.21834 | 0.21834 | 0.21834 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863
2) | Calculate fraction of ExhFlow:TrmlUnit flow
| VAV Exhaust |  | WD | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.21834 | 0.22834 | 0.33662 | 0.33662 | 0.26777 | 0.26777 | 0.33662 | 0.33662 | 0.33662 | 0.33662 | 0.33662 | 0.24805 | 0.21834 | 0.21834 | 0.21834 | 0.20863 | 0.20863
|  |  | Sat | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.21834 | 0.21834 | 0.24805 | 0.24805 | 0.24805 | 0.24805 | 0.21834 | 0.21834 | 0.21834 | 0.21834 | 0.21834 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863
|  |  | Sun | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.21834 | 0.21834 | 0.24805 | 0.24805 | 0.24805 | 0.24805 | 0.21834 | 0.21834 | 0.21834 | 0.21834 | 0.21834 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863
3) | Subtract TrmlUnit:PriAirFlowMin from ExhFlow:TrmlUnit flow fraction
| VAV Exhaust | 0.25 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.086615 | 0.086615 | 0.017766 | 0.017766 | 0.086615 | 0.086615 | 0.086615 | 0.086615 | 0.086615 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4) | Add 3) to TrmlUnit:PriAirFlowMin fraction
| TerminalUnit (Vent) Flow | 0.25 | WD | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.33662 | 0.33662 | 0.26777 | 0.26777 | 0.33662 | 0.33662 | 0.33662 | 0.33662 | 0.33662 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  | Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  | Sun | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Calculated flows for graph
| VAV Exhaust |  | WD | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.4935 | 3.6535 | 5.3858 | 5.3858 | 4.2843 | 4.2843 | 5.3858 | 5.3858 | 5.3858 | 5.3858 | 5.3858 | 3.9689 | 3.4935 | 3.4935 | 3.4935 | 3.3381 | 3.3381
|  |  | Sat | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.4935 | 3.4935 | 3.9689 | 3.9689 | 3.9689 | 3.9689 | 3.4935 | 3.4935 | 3.4935 | 3.4935 | 3.4935 | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.3381
|  |  | Sun | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.4935 | 3.4935 | 3.9689 | 3.9689 | 3.9689 | 3.9689 | 3.4935 | 3.4935 | 3.4935 | 3.4935 | 3.4935 | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.3381
| TerminalUnit (Vent) Flow Fraction |  | WD | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5.3858 | 5.3858 | 4.2843 | 4.2843 | 5.3858 | 5.3858 | 5.3858 | 5.3858 | 5.3858 | 4 | 4 | 4 | 4 | 4 | 4
|  |  | Sat | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  |  | Sun | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Schedule Function Options/Inputs
Interpolate between two schedules with fraction
Scaled schedule values by a constant or by the values of another schedule
Union of two or more schedules
Schedule Function Outputs
New schedule
EFLH (Fraction, OnOff)
Max
Min
Note on E19: David Reddy: IN simulation, can't be less than min exhaust
Note on E20: David Reddy: Set to 0 if there is no code minimum ventilation flow for the zone. In this case, ventilation modeled to track exhaust.

## OffSml-Lab_SZVAV22-ab
Input Value
Calculated Value
Proj: | OffSml-Lab_SZVAV22
| Exhaust Control | VAV
| Zone SF | 5502 | ft2 |  |  |  | CAV Exhaust min Frac | 0.9
| Zone Height | 10 | ft |  |  |  | VAV Auto Sash Min Frac | 0.20863
| Zone Volume | 55020 | ft3
| Total Fume Hood Length | 57
| Hood Density | 10.3599
| Vertical Sash Fume Hood Exhaust Flow | 14250 |  | 250 | CFM/LF
| Space Vertical Sash Fume Hood Auto Sash Control Frac | 1
| Other Exhaust Flow | 422
| Zone Exh Flow Auto Sash Control Frac | 0.97124
| Occupied (Design) Exhaust Flow, VAV (CFM_eo) | 14672 | cfm | 16 | ACH
| Unoccupied (Min) Exhaust Flow, VAV (CFM_vaveu) | 3061 | cfm | 3.3381 | ACH
| Ventilation System OA Fraction | 1
| Occupied (Design) Terminal Flow (CFM_to) | 14672 | cfm | 16 | ACH
| Unoccupied (Min) Terminal Flow (CFM_tu) | 3668 | cfm | 4 | ACH | 0.25 | 0.052157
| Code Unoccupied (Min) Vent Flow (CFM_vumin) | 3668 | cfm | 4 | ACH
| Modeled Unoccupied Terminal Flow Fraction,VAV | 0.25
| Modeled Unoccupied Terminal Flow Fraction,CAV | 0.9
| Modeled Unoccupied Terminal Flow (CFM_vumodel) | 3668 | cfm | 4 | ACH
Hour of Day
| Description |  | Daily Sch | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
| LabExhaustVAVManualSashCtrl | Fraction | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.51 | 0.56 | 0.56 | 0.53 | 0.53 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.52 | 0.52 | 0.52 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | Sun | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.52 | 0.52 | 0.52 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
| LabExhaustVAVAutoSashCtrl | Fraction | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.21 | 0.22 | 0.33 | 0.33 | 0.26 | 0.26 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.24 | 0.21 | 0.21 | 0.21 | 0.2 | 0.2
|  |  | Sat | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.21 | 0.21 | 0.24 | 0.24 | 0.24 | 0.24 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
|  |  | Sun | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.21 | 0.21 | 0.24 | 0.24 | 0.24 | 0.24 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
| LabExhaustCAV | Fraction | WD | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  | Sun | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
1) | Calculate exhaust flow schedule, which is function of zone sash control fraction
| LabExhaustHoodVAVComposite | Fraction | WD | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.21834 | 0.22834 | 0.33662 | 0.33662 | 0.26777 | 0.26777 | 0.33662 | 0.33662 | 0.33662 | 0.33662 | 0.33662 | 0.24805 | 0.21834 | 0.21834 | 0.21834 | 0.20863 | 0.20863
|  |  | Sat | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.21834 | 0.21834 | 0.24805 | 0.24805 | 0.24805 | 0.24805 | 0.21834 | 0.21834 | 0.21834 | 0.21834 | 0.21834 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863
|  |  | Sun | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.21834 | 0.21834 | 0.24805 | 0.24805 | 0.24805 | 0.24805 | 0.21834 | 0.21834 | 0.21834 | 0.21834 | 0.21834 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863
2) | Calculate fraction of ExhFlow:TrmlUnit flow
| VAV Exhaust |  | WD | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.21834 | 0.22834 | 0.33662 | 0.33662 | 0.26777 | 0.26777 | 0.33662 | 0.33662 | 0.33662 | 0.33662 | 0.33662 | 0.24805 | 0.21834 | 0.21834 | 0.21834 | 0.20863 | 0.20863
|  |  | Sat | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.21834 | 0.21834 | 0.24805 | 0.24805 | 0.24805 | 0.24805 | 0.21834 | 0.21834 | 0.21834 | 0.21834 | 0.21834 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863
|  |  | Sun | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.21834 | 0.21834 | 0.24805 | 0.24805 | 0.24805 | 0.24805 | 0.21834 | 0.21834 | 0.21834 | 0.21834 | 0.21834 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863 | 0.20863
3) | Subtract TrmlUnit:PriAirFlowMin from ExhFlow:TrmlUnit flow fraction
| VAV Exhaust | 0.25 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.086615 | 0.086615 | 0.017766 | 0.017766 | 0.086615 | 0.086615 | 0.086615 | 0.086615 | 0.086615 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4) | Add 3) to TrmlUnit:PriAirFlowMin fraction
| TerminalUnit (Vent) Flow | 0.25 | WD | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.33662 | 0.33662 | 0.26777 | 0.26777 | 0.33662 | 0.33662 | 0.33662 | 0.33662 | 0.33662 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  | Sat | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
|  |  | Sun | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Calculated flows for graph
| VAV Exhaust |  | WD | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.4935 | 3.6535 | 5.3858 | 5.3858 | 4.2843 | 4.2843 | 5.3858 | 5.3858 | 5.3858 | 5.3858 | 5.3858 | 3.9689 | 3.4935 | 3.4935 | 3.4935 | 3.3381 | 3.3381
|  |  | Sat | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.4935 | 3.4935 | 3.9689 | 3.9689 | 3.9689 | 3.9689 | 3.4935 | 3.4935 | 3.4935 | 3.4935 | 3.4935 | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.3381
|  |  | Sun | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.4935 | 3.4935 | 3.9689 | 3.9689 | 3.9689 | 3.9689 | 3.4935 | 3.4935 | 3.4935 | 3.4935 | 3.4935 | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.3381 | 3.3381
| TerminalUnit (Vent) Flow Fraction |  | WD | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5.3858 | 5.3858 | 4.2843 | 4.2843 | 5.3858 | 5.3858 | 5.3858 | 5.3858 | 5.3858 | 4 | 4 | 4 | 4 | 4 | 4
|  |  | Sat | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  |  | Sun | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Schedule Function Options/Inputs
Interpolate between two schedules with fraction
Scaled schedule values by a constant or by the values of another schedule
Union of two or more schedules
Schedule Function Outputs
New schedule
EFLH (Fraction, OnOff)
Max
Min
Note on E19: David Reddy: IN simulation, can't be less than min exhaust
Note on E20: David Reddy: Set to 0 if there is no code minimum ventilation flow for the zone. In this case, ventilation modeled to track exhaust.

## Test_Old
Input Value
Calculated Value
| Exhaust Control | VAV
| Zone SF | 1275 | ft2 |  |  |  | CAV Exhaust min Frac | 0.9
| Zone Height | 10 | ft |  |  |  | VAV Auto Sash Min Frac | 0.36105
| Zone Volume | 12750 | ft3
| Total Fume Hood Length | 5
| Hood Density | 3.9216
| Vertical Sash Fume Hood Exhaust Flow | 1250 |  | 250 | CFM/LF
| Space Vertical Sash Fume Hood Auto Sash Control Frac | 0.5
| Other Exhaust Flow | 99.375
| Zone Exh Flow Auto Sash Control Frac | 0.46318
| Occupied (Design) Exhaust Flow, VAV (CFM_eo) | 1349.375 | cfm | 6.35 | ACH
| Unoccupied (Min) Exhaust Flow, VAV (CFM_vaveu) | 487.1875 | cfm | 2.2926 | ACH
| Ventilation System OA Fraction | 1
| Occupied (Design) Terminal Flow (CFM_to) | 1349.375 | cfm | 6.35 | ACH
| Unoccupied (Min) Terminal Flow (CFM_tu) | 1349.375 | cfm | 6.35 | ACH | 1 | 0.36105
| Code Unoccupied (Min) Vent Flow (CFM_vumin) | 1349.375 | cfm | 6.35 | ACH
| Modeled Unoccupied Terminal Flow Fraction,VAV | 1
| Modeled Unoccupied Terminal Flow Fraction,CAV | 0.9
| Modeled Unoccupied Terminal Flow (CFM_vumodel) | 1349.375 | cfm | 6.35 | ACH
Hour of Day
| Description |  | Daily Sch | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
| LabExhaustVAVManualSashCtrl | Fraction | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.51 | 0.56 | 0.56 | 0.53 | 0.53 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.52 | 0.52 | 0.52 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | Sun | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.52 | 0.52 | 0.52 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
| LabExhaustVAVAutoSashCtrl | Fraction | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.21 | 0.22 | 0.33 | 0.33 | 0.26 | 0.26 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.24 | 0.21 | 0.21 | 0.21 | 0.2 | 0.2
|  |  | Sat | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.21 | 0.21 | 0.24 | 0.24 | 0.24 | 0.24 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
|  |  | Sun | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.21 | 0.21 | 0.24 | 0.24 | 0.24 | 0.24 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
| LabExhaustCAV | Fraction | WD | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  | Sun | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
1) | Calculate exhaust flow schedule, which is function of zone sash control fraction
| LabExhaustHoodVAVComposite | Fraction | WD | 0.36105 | 0.36105 | 0.36105 | 0.36105 | 0.36105 | 0.36105 | 0.36105 | 0.36568 | 0.37568 | 0.45347 | 0.45347 | 0.40494 | 0.40494 | 0.45347 | 0.45347 | 0.45347 | 0.45347 | 0.45347 | 0.39031 | 0.36568 | 0.36568 | 0.36568 | 0.36105 | 0.36105
|  |  | Sat | 0.36105 | 0.36105 | 0.36105 | 0.36105 | 0.36105 | 0.36105 | 0.36105 | 0.36568 | 0.36568 | 0.39031 | 0.39031 | 0.39031 | 0.39031 | 0.36568 | 0.36568 | 0.36568 | 0.36568 | 0.36568 | 0.36105 | 0.36105 | 0.36105 | 0.36105 | 0.36105 | 0.36105
|  |  | Sun | 0.36105 | 0.36105 | 0.36105 | 0.36105 | 0.36105 | 0.36105 | 0.36105 | 0.36568 | 0.36568 | 0.39031 | 0.39031 | 0.39031 | 0.39031 | 0.36568 | 0.36568 | 0.36568 | 0.36568 | 0.36568 | 0.36105 | 0.36105 | 0.36105 | 0.36105 | 0.36105 | 0.36105
2) | Calculate fraction of ExhFlow:TrmlUnit flow
| VAV Exhaust |  | WD | 0.36105 | 0.36105 | 0.36105 | 0.36105 | 0.36105 | 0.36105 | 0.36105 | 0.36568 | 0.37568 | 0.45347 | 0.45347 | 0.40494 | 0.40494 | 0.45347 | 0.45347 | 0.45347 | 0.45347 | 0.45347 | 0.39031 | 0.36568 | 0.36568 | 0.36568 | 0.36105 | 0.36105
|  |  | Sat | 0.36105 | 0.36105 | 0.36105 | 0.36105 | 0.36105 | 0.36105 | 0.36105 | 0.36568 | 0.36568 | 0.39031 | 0.39031 | 0.39031 | 0.39031 | 0.36568 | 0.36568 | 0.36568 | 0.36568 | 0.36568 | 0.36105 | 0.36105 | 0.36105 | 0.36105 | 0.36105 | 0.36105
|  |  | Sun | 0.36105 | 0.36105 | 0.36105 | 0.36105 | 0.36105 | 0.36105 | 0.36105 | 0.36568 | 0.36568 | 0.39031 | 0.39031 | 0.39031 | 0.39031 | 0.36568 | 0.36568 | 0.36568 | 0.36568 | 0.36568 | 0.36105 | 0.36105 | 0.36105 | 0.36105 | 0.36105 | 0.36105
3) | Subtract TrmlUnit:PriAirFlowMin from ExhFlow:TrmlUnit flow fraction
| VAV Exhaust | 1 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4) | Add 3) to TrmlUnit:PriAirFlowMin fraction
| TerminalUnit (Vent) Flow | 1 | WD | bar: 1 to Hour of Day 24
Sat | bar: 1 to Hour of Day 24
Sun | bar: 1 to Hour of Day 24
Calculated flows for graph
| VAV Exhaust |  | WD | 2.2926 | 2.2926 | 2.2926 | 2.2926 | 2.2926 | 2.2926 | 2.2926 | 2.3221 | 2.3856 | 2.8795 | 2.8795 | 2.5714 | 2.5714 | 2.8795 | 2.8795 | 2.8795 | 2.8795 | 2.8795 | 2.4785 | 2.3221 | 2.3221 | 2.3221 | 2.2926 | 2.2926
|  |  | Sat | 2.2926 | 2.2926 | 2.2926 | 2.2926 | 2.2926 | 2.2926 | 2.2926 | 2.3221 | 2.3221 | 2.4785 | 2.4785 | 2.4785 | 2.4785 | 2.3221 | 2.3221 | 2.3221 | 2.3221 | 2.3221 | 2.2926 | 2.2926 | 2.2926 | 2.2926 | 2.2926 | 2.2926
|  |  | Sun | 2.2926 | 2.2926 | 2.2926 | 2.2926 | 2.2926 | 2.2926 | 2.2926 | 2.3221 | 2.3221 | 2.4785 | 2.4785 | 2.4785 | 2.4785 | 2.3221 | 2.3221 | 2.3221 | 2.3221 | 2.3221 | 2.2926 | 2.2926 | 2.2926 | 2.2926 | 2.2926 | 2.2926
| TerminalUnit (Vent) Flow Fraction |  | WD | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35
|  |  | Sat | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35
|  |  | Sun | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35 | 6.35
Schedule Function Options/Inputs
Interpolate between two schedules with fraction
Scaled schedule values by a constant or by the values of another schedule
Union of two or more schedules
Schedule Function Outputs
New schedule
EFLH (Fraction, OnOff)
Max
Min
Note on E19: David Reddy: IN simulation, can't be less than min exhaust
Note on E20: David Reddy: Set to 0 if there is no code minimum ventilation flow for the zone. In this case, ventilation modeled to track exhaust.

## LabProto25-CZ12_Core-Bot
Input Value
Calculated Value
| Exhaust Control | VAV
| Zone SF | 10586.7 | ft2 |  |  |  | CAV Exhaust min Frac | 0.9
| Zone Height | 9 | ft |  |  |  | VAV Auto Sash Min Frac | 0.5
| Zone Volume | 95280.3 | ft3
| Total Fume Hood Length | 42
| Hood Density | 4.408
| Vertical Sash Fume Hood Exhaust Flow | 10500 |  | 250 | CFM/LF
| Space Vertical Sash Fume Hood Auto Sash Control Frac | 0
| Other Exhaust Flow | 87.2293
| Zone Exh Flow Auto Sash Control Frac | 0
| Occupied (Design) Exhaust Flow, VAV (CFM_eo) | 10587.2293 | cfm | 6.667 | ACH
| Unoccupied (Min) Exhaust Flow, VAV (CFM_vaveu) | 5293.6147 | cfm | 3.3335 | ACH
| Ventilation System OA Fraction | 1
| Occupied (Design) Terminal Flow (CFM_to) | 10587.2293 | cfm | 6.667 | ACH
| Unoccupied (Min) Terminal Flow (CFM_tu) | 6352.02 | cfm | 4 | ACH | 0.59997 | 0.29999 | 0.6
| Code Unoccupied (Min) Vent Flow (CFM_vumin) | 6352.02 | cfm | 4 | ACH
| Modeled Unoccupied Terminal Flow Fraction,VAV | 0.59997
| Modeled Unoccupied Terminal Flow Fraction,CAV | 0.9
| Modeled Unoccupied Terminal Flow (CFM_vumodel) | 6352.02 | cfm | 4 | ACH
Hour of Day
| Description |  | Daily Sch | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
| LabExhaustVAVManualSashCtrl | Fraction | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.51 | 0.56 | 0.56 | 0.53 | 0.53 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.52 | 0.52 | 0.52 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | Sun | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.52 | 0.52 | 0.52 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
| LabExhaustVAVAutoSashCtrl | Fraction | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.21 | 0.22 | 0.33 | 0.33 | 0.26 | 0.26 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.24 | 0.21 | 0.21 | 0.21 | 0.2 | 0.2
|  |  | Sat | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.21 | 0.21 | 0.24 | 0.24 | 0.24 | 0.24 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
|  |  | Sun | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.21 | 0.21 | 0.24 | 0.24 | 0.24 | 0.24 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
| LabExhaustCAV | Fraction | WD | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  | Sun | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
1) | Calculate exhaust flow schedule, which is function of zone sash control fraction
| LabExhaustHoodVAVComposite | Fraction | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.51 | 0.56 | 0.56 | 0.53 | 0.53 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.52 | 0.52 | 0.52 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | Sun | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.52 | 0.52 | 0.52 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
2) | Calculate fraction of ExhFlow:TrmlUnit flow
| VAV Exhaust |  | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.51 | 0.56 | 0.56 | 0.53 | 0.53 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.52 | 0.52 | 0.52 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | Sun | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.52 | 0.52 | 0.52 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
3) | Subtract TrmlUnit:PriAirFlowMin from ExhFlow:TrmlUnit flow fraction
| VAV Exhaust | 0.59997 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4) | Add 3) to TrmlUnit:PriAirFlowMin fraction
| TerminalUnit (Vent) Flow | 0.59997 | WD | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997
|  |  | Sat | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997
|  |  | Sun | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997 | 0.59997
Calculated flows for graph
| VAV Exhaust |  | WD | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.4002 | 3.7335 | 3.7335 | 3.5335 | 3.5335 | 3.7335 | 3.7335 | 3.7335 | 3.7335 | 3.7335 | 3.4668 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335
|  |  | Sat | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.4668 | 3.4668 | 3.4668 | 3.4668 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335
|  |  | Sun | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.4668 | 3.4668 | 3.4668 | 3.4668 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335
| TerminalUnit (Vent) Flow Fraction |  | WD | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  |  | Sat | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
|  |  | Sun | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Schedule Function Options/Inputs
Interpolate between two schedules with fraction
Scaled schedule values by a constant or by the values of another schedule
Union of two or more schedules
Schedule Function Outputs
New schedule
EFLH (Fraction, OnOff)
Max
Min
Note on E19: David Reddy: IN simulation, can't be less than min exhaust
Note on E20: David Reddy: Set to 0 if there is no code minimum ventilation flow for the zone. In this case, ventilation modeled to track exhaust.

## LabProto25-CZ12_Core-Bot (2)
Input Value
Calculated Value
| Exhaust Control | VAV
| Zone SF | 10586.7 | ft2 |  |  |  | CAV Exhaust min Frac | 0.9
| Zone Height | 9 | ft |  |  |  | VAV Auto Sash Min Frac | 0.5
| Zone Volume | 95280.3 | ft3
| Total Fume Hood Length | 42
| Hood Density | 4.408
| Vertical Sash Fume Hood Exhaust Flow | 10500 |  | 250 | CFM/LF
| Space Vertical Sash Fume Hood Auto Sash Control Frac | 0
| Other Exhaust Flow | 87.2293
| Zone Exh Flow Auto Sash Control Frac | 0
| Occupied (Design) Exhaust Flow, VAV (CFM_eo) | 10587.2293 | cfm | 6.667 | ACH
| Unoccupied (Min) Exhaust Flow, VAV (CFM_vaveu) | 5293.6147 | cfm | 3.3335 | ACH
| Ventilation System OA Fraction | 1
| Occupied (Design) Terminal Flow (CFM_to) | 10587.2293 | cfm | 6.667 | ACH
| Unoccupied (Min) Terminal Flow (CFM_tu) | 9528.03 | cfm | 6 | ACH | 0.89996 | 0.44998
| Code Unoccupied (Min) Vent Flow (CFM_vumin) | 9528.03 | cfm | 6 | ACH
| Modeled Unoccupied Terminal Flow Fraction,VAV | 0.89996
| Modeled Unoccupied Terminal Flow Fraction,CAV | 0.9
| Modeled Unoccupied Terminal Flow (CFM_vumodel) | 9528.03 | cfm | 6 | ACH
Hour of Day
| Description |  | Daily Sch | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
| LabExhaustVAVManualSashCtrl | Fraction | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.51 | 0.56 | 0.56 | 0.53 | 0.53 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.52 | 0.52 | 0.52 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | Sun | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.52 | 0.52 | 0.52 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
| LabExhaustVAVAutoSashCtrl | Fraction | WD | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.21 | 0.22 | 0.33 | 0.33 | 0.26 | 0.26 | 0.33 | 0.33 | 0.33 | 0.33 | 0.33 | 0.24 | 0.21 | 0.21 | 0.21 | 0.2 | 0.2
|  |  | Sat | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.21 | 0.21 | 0.24 | 0.24 | 0.24 | 0.24 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
|  |  | Sun | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.21 | 0.21 | 0.24 | 0.24 | 0.24 | 0.24 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2
| LabExhaustCAV | Fraction | WD | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  | Sun | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
1) | Calculate exhaust flow schedule, which is function of zone sash control fraction
| LabExhaustHoodVAVComposite | Fraction | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.51 | 0.56 | 0.56 | 0.53 | 0.53 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.52 | 0.52 | 0.52 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | Sun | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.52 | 0.52 | 0.52 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
2) | Calculate fraction of ExhFlow:TrmlUnit flow
| VAV Exhaust |  | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.51 | 0.56 | 0.56 | 0.53 | 0.53 | 0.56 | 0.56 | 0.56 | 0.56 | 0.56 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.52 | 0.52 | 0.52 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | Sun | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.52 | 0.52 | 0.52 | 0.52 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
3) | Subtract TrmlUnit:PriAirFlowMin from ExhFlow:TrmlUnit flow fraction
| VAV Exhaust | 0.89996 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4) | Add 3) to TrmlUnit:PriAirFlowMin fraction
| TerminalUnit (Vent) Flow | 0.89996 | WD | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996
|  |  | Sat | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996
|  |  | Sun | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996 | 0.89996
Calculated flows for graph
| VAV Exhaust |  | WD | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.4002 | 3.7335 | 3.7335 | 3.5335 | 3.5335 | 3.7335 | 3.7335 | 3.7335 | 3.7335 | 3.7335 | 3.4668 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335
|  |  | Sat | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.4668 | 3.4668 | 3.4668 | 3.4668 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335
|  |  | Sun | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.4668 | 3.4668 | 3.4668 | 3.4668 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335 | 3.3335
| TerminalUnit (Vent) Flow Fraction |  | WD | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  | Sat | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
|  |  | Sun | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
Schedule Function Options/Inputs
Interpolate between two schedules with fraction
Scaled schedule values by a constant or by the values of another schedule
Union of two or more schedules
Schedule Function Outputs
New schedule
EFLH (Fraction, OnOff)
Max
Min
Note on E19: David Reddy: IN simulation, can't be less than min exhaust
Note on E20: David Reddy: Set to 0 if there is no code minimum ventilation flow for the zone. In this case, ventilation modeled to track exhaust.

## Baseline_old (hidden)
Input Value
Calculated Value
| Sash Control Fraction | 1 |  |  |  | VAV Exhaust | 0.12
| Zone SF | 5502 | ft2 |  |  | CAV Exhaust | 0.9
| Zone Height | 10 | ft
| Zone Volume | 55020 | ft3
| Occupied (Design) Exhaust Flow, VAV (CFM_eo) | 5502 | cfm | 6 | ACH
| Unoccupied (Min) Exhaust Flow, VAV (CFM_vaveu) | 660.24 | cfm | 0.72 | ACH
| Unoccupied (Min) Exhaust Flow, CAV (CFM_caveu) | 4951.8 | cfm | 5.4 | ACH
| Ventilation System OA Fraction | 1
| Occupied (Design) Terminal Flow (CFM_to) | 5502 | cfm | 6 | ACH
| Unoccupied (Min) Terminal Flow (CFM_tu) | 2751 | cfm | 3 | ACH | 0.5 | 0.06
| Code Unoccupied (Min) Vent Flow (CFM_vumin) | 2751 | cfm | 3 | ACH
| Modeled Unoccupied Terminal Flow Fraction,VAV | 0.5
| Modeled Unoccupied Terminal Flow Fraction,CAV | 0.9
| Modeled Unoccupied Terminal Flow (CFM_vumodel) | 2751 | cfm | 3 | ACH
Hour of Day
| Description |  | Daily Sch | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
| LabExhaustHoodVAVNoSashCtrl | Fraction | WD | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.4128 | 0.4718 | 0.37 | 0.37 | 0.4128 | 0.5308 | 0.4718 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37
|  |  | Sat | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37
|  |  | Sun | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37 | 0.37
| LabExhaustHoodVAVSashCtrl | Fraction | WD | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.3062 | 0.3807 | 0.4179 | 0.269 | 0.3062 | 0.3807 | 0.4552 | 0.4179 | 0.3062 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
|  |  | Sat | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
|  |  | Sun | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
| LabExhaustHoodCAV | Fraction | WD | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  | Sun | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
1) | Calculate exhaust flow schedule, which is function of zone sash control fraction
| LabExhaustHoodVAVComposite | Fraction | WD | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.3062 | 0.3807 | 0.4179 | 0.269 | 0.3062 | 0.3807 | 0.4552 | 0.4179 | 0.3062 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
|  |  | Sat | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
|  |  | Sun | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
2) | Calculate fraction of ExhFlow:TrmlUnit flow
| VAV Exhaust |  | WD | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.3062 | 0.3807 | 0.4179 | 0.269 | 0.3062 | 0.3807 | 0.4552 | 0.4179 | 0.3062 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
|  |  | Sat | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
|  |  | Sun | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12
| CAV Exhaust |  | WD | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  | Sun | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
3) | Subtract TrmlUnit:PriAirFlowMin from ExhFlow:TrmlUnit flow fraction
| VAV Exhaust | 0.5 | WD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sat | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  | Sun | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CAV Exhaust |  | WD | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
|  |  | Sat | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
|  |  | Sun | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
4) | Add 3) to TrmlUnit:PriAirFlowMin fraction
| TerminalUnit (Vent) Flow | 0.5 | WD | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | Sat | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | Sun | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
|  |  | WD | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  | Sat | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
|  |  | Sun | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
Calculated flows for graph
| VAV Exhaust |  | WD | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 1.8372 | 2.2842 | 2.5074 | 1.614 | 1.8372 | 2.2842 | 2.7312 | 2.5074 | 1.8372 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72
|  |  | Sat | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72
|  |  | Sun | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72
| TerminalUnit (Vent) Flow Fraction |  | WD | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  | Sat | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
|  |  | Sun | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| CAV Exhaust |  | WD | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4
|  |  | Sat | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4
|  |  | Sun | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4
| TerminalUnit (Vent) Flow Fraction |  | WD | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4
|  |  | Sat | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4
|  |  | Sun | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4
Schedule Function Options/Inputs
Interpolate between two schedules with fraction
Scaled schedule values by a constant or by the values of another schedule
Union of two or more schedules
Schedule Function Outputs
New schedule
EFLH (Fraction, OnOff)
Max
Min
Note on E15: David Reddy: IN simulation, can't be less than min exhaust
Note on E16: David Reddy: Set to 0 if there is no code minimum ventilation flow for the zone. In this case, ventilation modeled to track exhaust.