## UnitaryAC-HPMinEffReq_T24N_new
; | T24 Nonresidential ACM Ruleset
;
; | TABLE NAME:
; |  | UnitaryACHPMinEffReq
;
; | MODIFICATION HISTORY:
; |  | Date | Purpose
; |  | 2019-06-19 | Incorporate 2022 records (copied from 2019) and revise table name removing '2019'
; |  | 2017-12-14 | Copy of 2016 table, modified for 2019 ruleset
; |  | 2019-08-04 | Update <65kBtu/hr table reference and add min EER reqs for Split1Phase HPs
; |  | 2020-08-27 | Updates for Ticket 3217 (Fix for WSHP). Change EER/COP 'NA' values to 0. Add values for VRF. Add notes column
; |  | 2022-02-15 | Update to 2022 standard
; |  | 2022-09-30 | Add columns/rows for <65 kBtu/hr equipment, including SEER2/EER2/HSPF2.
; |  | 2024-10-17 | Add columns/rows for CRAC, including CRACConfig/NSenCOP.
;
; | STANDARDS/ACM REFERENCE(S):
; |  | TABLE 110.2-A - ELECTRICALLY OPERATED UNITARY AIR CONDITIONERS AND CONDENSING UNITS – MINIMUM EFFICIENCY REQUIREMENTS
; |  | TABLE 110.2-B - UNITARY AND APPLIED HEAT PUMPS - MINIMUM EFFICIENCY REQUIREMENTS
; |  | TABLE 110.2-E - PACKAGED TERMINAL AIR CONDITIONER AND PACKAGED TERMINAL HEAT PUMP - MINIMUM EFFICIENCY REQUIREMENTS
; |  | TABLE 110.2-H - Electrically Operated Variable Refrigerant Flow Air-to-Air and Applied Heat Pumps - Minimum Efficiency Requirements
; |  | T20 Appliance Efficiency Standards
;
; | NOTES:
; |  | Adjustments to EER for systems with a heating section other than electric resistance heat performed in rules
; |  | HP COP requirement specified at 47F db/43f wb outdoor air rating point
; |  | Zero values indicate there is no requirement
;
; | SYNTAX EXAMPLES:
; |  | UnitaryACHPMinEffReq:EER(StandardsVersion=Proj:StdsVersion,Category = "AC", SubCategory = "CRAC", CondenserType = "Air", SizeCategory = 80000)
;
; #################################### Start of Table ####################################
TABLE UnitaryACHPMinEffReq
|  | StandardsVersion | Category | SubCategory | Configuration | CondenserType | SizeCategory | SEER | SEER2 | SEERToSEER2Rat | SEERSource | EER | IEER | EER2a | EER2b | EERToEER2Rat | EERSource | NSenCOP | NSenCOPSource | COP47 | COP17 | COPSource | HSPF | HSPF2 | HSPFToHSPF2Rat | Notes
|  | * | AC | CRAC | Floor-Mounted (Downflow) | Air | <80000 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | NA | 2.7 | T24 Std Table 110.2-L | 0 | 0 | NA | 0 | 0 | 0
|  | * | AC | CRAC | Floor-Mounted (Downflow) | Air | <295000 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | NA | 2.58 | T24 Std Table 110.2-L | 0 | 0 | NA | 0 | 0 | 0
|  | * | AC | CRAC | Floor-Mounted (Downflow) | Air | * | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | NA | 2.36 | T24 Std Table 110.2-L | 0 | 0 | NA | 0 | 0 | 0
|  | * | AC | CRAC | Floor-Mounted (Upflow - Ducted) | Air | <80000 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | NA | 2.67 | T24 Std Table 110.2-L | 0 | 0 | NA | 0 | 0 | 0
|  | * | AC | CRAC | Floor-Mounted (Upflow - Ducted) | Air | <295000 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | NA | 2.55 | T24 Std Table 110.2-L | 0 | 0 | NA | 0 | 0 | 0
|  | * | AC | CRAC | Floor-Mounted (Upflow - Ducted) | Air | * | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | NA | 2.33 | T24 Std Table 110.2-L | 0 | 0 | NA | 0 | 0 | 0
|  | * | AC | CRAC | Floor-Mounted (Upflow - Nonducted) | Air | <65000 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | NA | 2.16 | T24 Std Table 110.2-L | 0 | 0 | NA | 0 | 0 | 0
|  | * | AC | CRAC | Floor-Mounted (Upflow - Nonducted) | Air | <240000 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | NA | 2.04 | T24 Std Table 110.2-L | 0 | 0 | NA | 0 | 0 | 0
|  | * | AC | CRAC | Floor-Mounted (Upflow - Nonducted) | Air | * | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | NA | 1.89 | T24 Std Table 110.2-L | 0 | 0 | NA | 0 | 0 | 0
|  | * | AC | CRAC | Floor-Mounted (Horizontal) | Air | <65000 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | NA | 2.65 | T24 Std Table 110.2-L | 0 | 0 | NA | 0 | 0 | 0
|  | * | AC | CRAC | Floor-Mounted (Horizontal) | Air | <240000 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | NA | 2.55 | T24 Std Table 110.2-L | 0 | 0 | NA | 0 | 0 | 0
|  | * | AC | CRAC | Floor-Mounted (Horizontal) | Air | * | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | NA | 2.47 | T24 Std Table 110.2-L | 0 | 0 | NA | 0 | 0 | 0
|  | * | AC | CRAC | Ceiling-Mounted (Free Air Discharge and Ducted Return) | Air | <29000 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | NA | 2.05 | T24 Std Table 110.2-M | 0 | 0 | NA | 0 | 0 | 0
|  | * | AC | CRAC | Ceiling-Mounted (Free Air Discharge and Ducted Return) | Air | <65000 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | NA | 2.02 | T24 Std Table 110.2-M | 0 | 0 | NA | 0 | 0 | 0
|  | * | AC | CRAC | Ceiling-Mounted (Free Air Discharge and Ducted Return) | Air | * | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | NA | 1.92 | T24 Std Table 110.2-M | 0 | 0 | NA | 0 | 0 | 0
|  | * | AC | CRAC | Ceiling-Mounted (Free Air Discharge and Free Air Return) | Air | <29000 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | NA | 2.08 | T24 Std Table 110.2-M | 0 | 0 | NA | 0 | 0 | 0
|  | * | AC | CRAC | Ceiling-Mounted (Free Air Discharge and Free Air Return) | Air | <65000 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | NA | 2.05 | T24 Std Table 110.2-M | 0 | 0 | NA | 0 | 0 | 0
|  | * | AC | CRAC | Ceiling-Mounted (Free Air Discharge and Free Air Return) | Air | * | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | NA | 1.94 | T24 Std Table 110.2-M | 0 | 0 | NA | 0 | 0 | 0
|  | * | AC | CRAC | Ceiling-Mounted (Ducted Discharge and Ducted Return) | Air | <29000 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | NA | 1.86 | T24 Std Table 110.2-M | 0 | 0 | NA | 0 | 0 | 0
|  | * | AC | CRAC | Ceiling-Mounted (Ducted Discharge and Ducted Return) | Air | <65000 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | NA | 1.83 | T24 Std Table 110.2-M | 0 | 0 | NA | 0 | 0 | 0
|  | * | AC | CRAC | Ceiling-Mounted (Ducted Discharge and Ducted Return) | Air | * | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | NA | 1.73 | T24 Std Table 110.2-M | 0 | 0 | NA | 0 | 0 | 0
|  | * | AC | CRAC | Ceiling-Mounted (Ducted Discharge and Free Air Return) | Air | <29000 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | NA | 1.89 | T24 Std Table 110.2-M | 0 | 0 | NA | 0 | 0 | 0
|  | * | AC | CRAC | Ceiling-Mounted (Ducted Discharge and Free Air Return) | Air | <65000 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | NA | 1.86 | T24 Std Table 110.2-M | 0 | 0 | NA | 0 | 0 | 0
|  | * | AC | CRAC | Ceiling-Mounted (Ducted Discharge and Free Air Return) | Air | * | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | NA | 1.75 | T24 Std Table 110.2-M | 0 | 0 | NA | 0 | 0 | 0
|  | * | AC | CRAC | * | Air | <65000 | 0 | 0 | 0 | NA | 11 | 0 | 0 | 0 | 0 | Appl Std Table C-9 | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | * | AC | CRAC | * | Air | <135000 | 0 | 0 | 0 | NA | 10.4 | 0 | 0 | 0 | 0 | Appl Std Table C-9 | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | * | AC | CRAC | * | Air | <240000 | 0 | 0 | 0 | NA | 10.2 | 0 | 0 | 0 | 0 | Appl Std Table C-9 | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | * | AC | CRAC | * | Air | >=240000 | 0 | 0 | 0 | NA | 10.2 | 0 | 0 | 0 | 0 | CBECC Default | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | Compliance2019 | AC | Split1Phase | * | Air | <45000 | 14 | 14.3 | 0.95 | T20 Std Table C-3 | 12.2 | 0 | 11.7 | 9.8 | 0 | T20 Std Table C-3, EER2 from Proctor | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | Compliance2019 | AC | Split1Phase | * | Air | <65000 | 14 | 14.3 | 0.95 | T20 Std Table C-3 | 11.7 | 0 | 11.2 | 9.8 | 0 | T20 Std Table C-3, EER2 from Proctor | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | Compliance2019 | AC | Packaged1Phase | * | Air | <65000 | 14 | 13.4 | 0.96 | T20 Std Table C-3 | 11 | 0 | 10.6 | 0 | 0 | T20 Std Table C-3, EER2 from Proctor | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | Compliance2019 | AC | Split3Phase | * | Air | <65000 | 13 | 13.4 | 0.96 | T20 Std Table C-4 | 0 | 0 | 0 | 0 | 0 | NA | 0 | NA | 0 | 0 | NA | 0 | 0 | 0 | SEER req. covered by separate rule
|  | Compliance2019 | AC | * | * | Air | <65000 | 14 | 13.4 | 0.96 | T20 Std Table C-4 | 0 | 0 | 0 | 0 | 0 | NA | 0 | NA | 0 | 0 | NA | 0 | 0 | 0 | SEER req. covered by separate rule
|  | Compliance2019 | AC | * | * | Air | <135000 | 0 | 0 | 0 | NA | 11.2 | 12.9 | 0 | 0 | 0 | T24 Std Table 110.2-A | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | Compliance2019 | AC | * | * | Air | <240000 | 0 | 0 | 0 | NA | 11 | 12.4 | 0 | 0 | 0 | T24 Std Table 110.2-A | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | Compliance2019 | AC | * | * | Air | <760000 | 0 | 0 | 0 | NA | 10 | 11.6 | 0 | 0 | 0 | T24 Std Table 110.2-A | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | Compliance2019 | AC | * | * | Air | >=760000 | 0 | 0 | 0 | NA | 9.7 | 11.2 | 0 | 0 | 0 | T24 Std Table 110.2-A | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | Compliance2022 | AC | Split1Phase | * | Air | <45000 | 15 | 14.3 | 0.95 | T20 Std Table C-3 | 12.2 | 0 | 11.7 | 9.8 | 0 | T20 Std Table C-3, EER2 from Proctor | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | Compliance2022 | AC | Split1Phase | * | Air | <65000 | 15 | 14.3 | 0.95 | T20 Std Table C-3 | 11.7 | 0 | 11.2 | 9.8 | 0 | T20 Std Table C-3, EER2 from Proctor | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | Compliance2022 | AC | Packaged1Phase | * | Air | <65000 | 14 | 13.4 | 0.96 | T20 Std Table C-3 | 11 | 0 | 10.6 | 0 | 0 | T20 Std Table C-3, EER2 from Proctor | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | Compliance2022 | AC | Split3Phase | * | Air | <65000 | 13 | 13.4 | 0.96 | T20 Std Table C-4 | 0 | 0 | 0 | 0 | 0 | NA | 0 | NA | 0 | 0 | NA | 0 | 0 | 0 | SEER req. covered by separate rule
|  | Compliance2022 | AC | * | * | Air | <65000 | 14 | 13.4 | 0.96 | T20 Std Table C-4 | 0 | 0 | 0 | 0 | 0 | NA | 0 | NA | 0 | 0 | NA | 0 | 0 | 0 | SEER req. covered by separate rule
|  | Compliance2022 | AC | * | * | Air | <135000 | 0 | 0 | 0 | NA | 11.2 | 14.8 | 0 | 0 | 0 | T24 Std Table 110.2-A | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | Compliance2022 | AC | * | * | Air | <240000 | 0 | 0 | 0 | NA | 11 | 14.2 | 0 | 0 | 0 | T24 Std Table 110.2-A | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | Compliance2022 | AC | * | * | Air | <760000 | 0 | 0 | 0 | NA | 10 | 13.2 | 0 | 0 | 0 | T24 Std Table 110.2-A | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | Compliance2022 | AC | * | * | Air | >=760000 | 0 | 0 | 0 | NA | 9.7 | 12.5 | 0 | 0 | 0 | T24 Std Table 110.2-A | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | Compliance2025 | AC | Split1Phase | * | Air | <45000 | 15 | 14.3 | 0.95 | T20 Std Table C-3 | 12.2 | 0 | 11.7 | 9.8 | 0 | T20 Std Table C-3, EER2 from Proctor | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | Compliance2025 | AC | Split1Phase | * | Air | <65000 | 15 | 14.3 | 0.95 | T20 Std Table C-3 | 11.7 | 0 | 11.2 | 9.8 | 0 | T20 Std Table C-3, EER2 from Proctor | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | Compliance2025 | AC | Packaged1Phase | * | Air | <65000 | 14 | 13.4 | 0.96 | T20 Std Table C-3 | 11 | 0 | 10.6 | 0 | 0 | T20 Std Table C-3, EER2 from Proctor | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | Compliance2025 | AC | Split3Phase | * | Air | <65000 | 13 | 13.4 | 0.96 | T20 Std Table C-4 | 0 | 0 | 0 | 0 | 0 | NA | 0 | NA | 0 | 0 | NA | 0 | 0 | 0 | SEER req. covered by separate rule
|  | Compliance2025 | AC | * | * | Air | <65000 | 14 | 13.4 | 0.96 | T20 Std Table C-4 | 0 | 0 | 0 | 0 | 0 | NA | 0 | NA | 0 | 0 | NA | 0 | 0 | 0 | SEER req. covered by separate rule
|  | Compliance2025 | AC | * | * | Air | <135000 | 0 | 0 | 0 | NA | 11.2 | 14.8 | 0 | 0 | 0 | T24 Std Table 110.2-A | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | Compliance2025 | AC | * | * | Air | <240000 | 0 | 0 | 0 | NA | 11 | 14.2 | 0 | 0 | 0 | T24 Std Table 110.2-A | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | Compliance2025 | AC | * | * | Air | <760000 | 0 | 0 | 0 | NA | 10 | 13.2 | 0 | 0 | 0 | T24 Std Table 110.2-A | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | Compliance2025 | AC | * | * | Air | >=760000 | 0 | 0 | 0 | NA | 9.7 | 12.5 | 0 | 0 | 0 | T24 Std Table 110.2-A | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | * | AC | * | * | WaterSource | <17000 | 0 | 0 | 0 | NA | 12.1 | 0 | 0 | 0 | 0 | Appl Std Table C-5 | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | * | AC | * | * | WaterSource | <65000 | 0 | 0 | 0 | NA | 12.1 | 0 | 0 | 0 | 0 | Appl Std Table C-5 | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | * | AC | * | * | WaterSource | <135000 | 0 | 0 | 0 | NA | 12.1 | 13.9 | 0 | 0 | 0 | T24 Std Table 110.2-A | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | * | AC | * | * | WaterSource | <240000 | 0 | 0 | 0 | NA | 12.5 | 13.9 | 0 | 0 | 0 | T24 Std Table 110.2-A | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | * | AC | * | * | WaterSource | <760000 | 0 | 0 | 0 | NA | 12.4 | 13.6 | 0 | 0 | 0 | T24 Std Table 110.2-A | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | * | AC | * | * | WaterSource | >=760000 | 0 | 0 | 0 | NA | 12.2 | 13.5 | 0 | 0 | 0 | T24 Std Table 110.2-A | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | * | AC | * | * | EvaporativelyCooled | <65000 | 0 | 0 | 0 | NA | 12.1 | 0 | 0 | 0 | 0 | Appl Std Table C-4 | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | * | AC | * | * | EvaporativelyCooled | <135000 | 0 | 0 | 0 | NA | 12.1 | 12.3 | 0 | 0 | 0 | T24 Std Table 110.2-A | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | * | AC | * | * | EvaporativelyCooled | <240000 | 0 | 0 | 0 | NA | 12 | 12.2 | 0 | 0 | 0 | T24 Std Table 110.2-A | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | * | AC | * | * | EvaporativelyCooled | <760000 | 0 | 0 | 0 | NA | 11.9 | 12.1 | 0 | 0 | 0 | T24 Std Table 110.2-A | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | * | AC | * | * | EvaporativelyCooled | >=760000 | 0 | 0 | 0 | NA | 11.7 | 11.9 | 0 | 0 | 0 | T24 Std Table 110.2-A | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | Compliance2019 | HP | Split1Phase | * | Air | <65000 | 14 | 14.3 | 0.95 | NA | 0 | 0 | 0 | 0 | 0 | T20 Std Table C-3 | 0 | NA | 0 | 0 | NA | 8.2 | 7.5 | 0.85 |  | https://govt.westlaw.com/calregs/Document/IC95DA848BDAD489294F06754177B0C50?viewType=FullText&originationContext=documenttoc&transitionType=CategoryPageItem&contextData=(sc.Default)&bhcp=1
|  | Compliance2019 | HP | Split3Phase | * | Air | <65000 | 14 | 13.4 | 0.96 | NA | 0 | 0 | 0 | 0 | 0 | T20 Std Table C-3 | 0 | NA | 0 | 0 | NA | 8.2 | 7.5 | 0.84 |  | https://govt.westlaw.com/calregs/Document/IC95DA848BDAD489294F06754177B0C50?viewType=FullText&originationContext=documenttoc&transitionType=CategoryPageItem&contextData=(sc.Default)&bhcp=1
|  | Compliance2019 | HP | * | * | Air | <65000 | 14 | 13.4 | 0.96 | T20 Table C-4 | 0 | 0 | 0 | 0 | 0 | NA | 0 | NA | 0 | 0 | NA | 8 | 6.7 | 0.84
|  | Compliance2019 | HP | * | * | Air | <135000 | 0 | 0 | 0 | NA | 11 | 12.2 | 0 | 0 | 0 | T24 Std Table 110.2-B | 0 | NA | 3.3 | 2.25 | T24 Std Table 110.2-B | 0 | 0 | 0
|  | Compliance2019 | HP | * | * | Air | <240000 | 0 | 0 | 0 | NA | 10.6 | 11.6 | 0 | 0 | 0 | T24 Std Table 110.2-B | 0 | NA | 3.2 | 2.05 | T24 Std Table 110.2-B | 0 | 0 | 0
|  | Compliance2019 | HP | * | * | Air | >=240000 | 0 | 0 | 0 | NA | 9.5 | 10.6 | 0 | 0 | 0 | T24 Std Table 110.2-B | 0 | NA | 3.2 | 2.05 | T24 Std Table 110.2-B | 0 | 0 | 0
|  | Compliance2022 | HP | Split1Phase | * | Air | <65000 | 15 | 14.3 | 0.95 | NA | 0 | 0 | 0 | 0 | 0 | T20 Std Table C-3 | 0 | NA | 0 | 0 | NA | 8.8 | 7.5 | 0.85 |  | https://govt.westlaw.com/calregs/Document/IC95DA848BDAD489294F06754177B0C50?viewType=FullText&originationContext=documenttoc&transitionType=CategoryPageItem&contextData=(sc.Default)&bhcp=1
|  | Compliance2022 | HP | Split3Phase | * | Air | <65000 | 14 | 13.4 | 0.96 | NA | 0 | 0 | 0 | 0 | 0 | T20 Std Table C-3 | 0 | NA | 0 | 0 | NA | 8.2 | 7.5 | 0.84 |  | https://govt.westlaw.com/calregs/Document/IC95DA848BDAD489294F06754177B0C50?viewType=FullText&originationContext=documenttoc&transitionType=CategoryPageItem&contextData=(sc.Default)&bhcp=1
|  | Compliance2022 | HP | * | * | Air | <65000 | 14 | 13.4 | 0.96 | T20 Table C-4 | 0 | 0 | 0 | 0 | 0 | NA | 0 | NA | 0 | 0 | NA | 8 | 6.7 | 0.84
|  | Compliance2022 | HP | * | * | Air | <135000 | 0 | 0 | 0 | NA | 11 | 14.1 | 0 | 0 | 0 | T24 Std Table 110.2-B | 0 | NA | 3.4 | 2.25 | T24 Std Table 110.2-B | 0 | 0 | 0
|  | Compliance2022 | HP | * | * | Air | <240000 | 0 | 0 | 0 | NA | 10.6 | 13.5 | 0 | 0 | 0 | T24 Std Table 110.2-B | 0 | NA | 3.3 | 2.05 | T24 Std Table 110.2-B | 0 | 0 | 0
|  | Compliance2022 | HP | * | * | Air | >=240000 | 0 | 0 | 0 | NA | 9.5 | 12.5 | 0 | 0 | 0 | T24 Std Table 110.2-B | 0 | NA | 3.3 | 2.05 | T24 Std Table 110.2-B | 0 | 0 | 0
|  | Compliance2025 | HP | Split1Phase | * | Air | <65000 | 15 | 14.3 | 0.95 | NA | 0 | 0 | 0 | 0 | 0 | T20 Std Table C-3 | 0 | NA | 0 | 0 | NA | 8.8 | 7.5 | 0.85 |  | https://govt.westlaw.com/calregs/Document/IC95DA848BDAD489294F06754177B0C50?viewType=FullText&originationContext=documenttoc&transitionType=CategoryPageItem&contextData=(sc.Default)&bhcp=1
|  | Compliance2025 | HP | Split3Phase | * | Air | <65000 | 14 | 13.4 | 0.96 | NA | 0 | 0 | 0 | 0 | 0 | T20 Std Table C-3 | 0 | NA | 0 | 0 | NA | 8.2 | 7.5 | 0.84 |  | https://govt.westlaw.com/calregs/Document/IC95DA848BDAD489294F06754177B0C50?viewType=FullText&originationContext=documenttoc&transitionType=CategoryPageItem&contextData=(sc.Default)&bhcp=1
|  | Compliance2025 | HP | * | * | Air | <65000 | 14 | 13.4 | 0.96 | T20 Table C-4 | 0 | 0 | 0 | 0 | 0 | NA | 0 | NA | 0 | 0 | NA | 8 | 6.7 | 0.84
|  | Compliance2025 | HP | * | * | Air | <135000 | 0 | 0 | 0 | NA | 11 | 14.1 | 0 | 0 | 0 | T24 Std Table 110.2-B | 0 | NA | 3.4 | 2.25 | 10 CFR 431.97 Table 1 + T24 Std Table 110.2-B | 0 | 0 | 0
|  | Compliance2025 | HP | * | * | Air | <240000 | 0 | 0 | 0 | NA | 10.6 | 13.5 | 0 | 0 | 0 | T24 Std Table 110.2-B | 0 | NA | 3.3 | 2.05 | 10 CFR 431.97 Table 1 + T24 Std Table 110.2-B | 0 | 0 | 0
|  | Compliance2025 | HP | * | * | Air | >=240000 | 0 | 0 | 0 | NA | 9.5 | 12.5 | 0 | 0 | 0 | T24 Std Table 110.2-B | 0 | NA | 3.2 | 2.05 | T24 Std Table 110.2-B | 0 | 0 | 0
|  | * | HP | * | * | WaterSource | <17000 | 0 | 0 | 0 | NA | 11.2 | 0 | 0 | 0 | 0 | Appl Std Table C-4 | 0 | NA | 4.2 | 0 | Appl Std Table C-4 | 0 | 0 | 0
|  | * | HP | * | * | WaterSource | <65000 | 0 | 0 | 0 | NA | 12 | 0 | 0 | 0 | 0 | Appl Std Table C-4 | 0 | NA | 4.2 | 0 | Appl Std Table C-4 | 0 | 0 | 0
|  | * | HP | * | * | WaterSource | <135000 | 0 | 0 | 0 | NA | 13 | 0 | 0 | 0 | 0 | T24 Std Table 110.2-B | 0 | NA | 4.3 | 0 | T24 Std Table 110.2-B | 0 | 0 | 0
|  | * | HP | * | * | WaterSource | <240000 | 0 | 0 | 0 | NA | 12.3 | 0 | 0 | 0 | 0 | Appl Std Table C-4 | 0 | NA | 2.9 | 0 | Appl Std Table C-4 | 0 | 0 | 0
|  | * | HP | * | * | WaterSource | <760000 | 0 | 0 | 0 | NA | 12.2 | 0 | 0 | 0 | 0 | Appl Std Table C-4 | 0 | NA | 0 | 0 | Appl Std Table C-4 | 0 | 0 | 0
|  | * | HP | * | * | WaterSource | >=760000 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | NA | 0 | NA | 0 | 0 | NA | 0 | 0 | 0 | No min eff req
|  | * | HP | * | * | GroundwaterSource | <135000 | 0 | 0 | 0 | NA | 18 | 0 | 0 | 0 | 0 | T24 Std Table 110.2-B | 0 | NA | 3.7 | 0 | T24 Std Table 110.2-B | 0 | 0 | 0
|  | * | HP | * | * | GroundwaterSource | >=135000 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | NA | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | * | HP | * | * | GroundSource | <135000 | 0 | 0 | 0 | NA | 14.1 | 0 | 0 | 0 | 0 | T24 Std Table 110.2-B | 0 | NA | 3.2 | 0 | T24 Std Table 110.2-B | 0 | 0 | 0
|  | * | HP | * | * | GroundSource | >=135000 | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | NA | 0 | NA | 0 | 0 | NA | 0 | 0 | 0 | No min eff req
|  | Compliance2019 | SPVAC | * | * | Air | <65000 | 0 | 0 | 0 | NA | 11 | 0 | 0 | 0 | 0 | T24 Std Table 110.2-E | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | Compliance2022 | SPVAC | * | * | Air | <65000 | 0 | 0 | 0 | NA | 11 | 0 | 0 | 0 | 0 | T24 Std Table 110.2-E | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | Compliance2025 | SPVAC | * | * | Air | <65000 | 0 | 0 | 0 | NA | 11 | 0 | 0 | 0 | 0 | 10 CFR 431.97 Table 10 | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | * | SPVAC | * | * | Air | <65000 | 0 | 0 | 0 | NA | 11 | 0 | 0 | 0 | 0 | 10 CFR 431.97 Table 10 | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | * | SPVAC | * | * | Air | <240000 | 0 | 0 | 0 | NA | 10 | 0 | 0 | 0 | 0 | 10 CFR 431.97 Table 10 | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | * | SPVAC | * | * | Air | * | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | NA | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | Compliance2019 | SPVHP | * | * | Air | <65000 | 0 | 0 | 0 | NA | 11 | 0 | 0 | 0 | 0 | T24 Std Table 110.2-E | 0 | NA | 3.3 | 0 | T24 Std Table 110.2-E | 0 | 0 | 0 | No min COP at 17F
|  | Compliance2022 | SPVHP | * | * | Air | <65000 | 0 | 0 | 0 | NA | 11 | 0 | 0 | 0 | 0 | T24 Std Table 110.2-E | 0 | NA | 3.3 | 0 | T24 Std Table 110.2-E | 0 | 0 | 0 | No min COP at 17F
|  | Compliance2025 | SPVHP | * | * | Air | <65000 | 0 | 0 | 0 | NA | 11 | 0 | 0 | 0 | 0 | 10 CFR 431.97 Table 10 | 0 | NA | 3.3 | 0 | 10 CFR 431.97 Table 10 | 0 | 0 | 0 | No min COP at 17F
|  | * | SPVHP | * | * | Air | <65000 | 0 | 0 | 0 | NA | 11 | 0 | 0 | 0 | 0 | 10 CFR 431.97 Table 10 | 0 | NA | 3.3 | 0 | 10 CFR 431.97 Table 10 | 0 | 0 | 0 | No min COP at 17F
|  | * | SPVHP | * | * | Air | <240000 | 0 | 0 | 0 | NA | 10 | 0 | 0 | 0 | 0 | 10 CFR 431.97 Table 10 | 0 | NA | 3 | 0 | 10 CFR 431.97 Table 10 | 0 | 0 | 0 | No min COP at 17F
|  | * | SPVHP | * | * | Air | * | 0 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | NA | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | Compliance2022 | VRF | AC | * | Air | <65000 | 13 | 12.9 | 0 | NA | 0 | 0 | 0 | 0 | 0 | NA | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | Compliance2025 | VRF | AC | * | Air | <65000 | 13 | 13.4 | 0 | T24 Std Table 110.2-F | 0 | 0 | 0 | 0 | 0 | NA | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | Compliance2025 | VRF | AC | * | Air | <135000 | 0 | 0 | 0 | NA | 10.5 | 15.5 | 0 | 0 | 0 | T24 Std Table 110.2-F | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | Compliance2025 | VRF | AC | * | Air | <240000 | 0 | 0 | 0 | NA | 10.3 | 14.9 | 0 | 0 | 0 | T24 Std Table 110.2-F | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | Compliance2025 | VRF | AC | * | Air | >=240000 | 0 | 0 | 0 | NA | 9.5 | 13.9 | 0 | 0 | 0 | T24 Std Table 110.2-F | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | * | VRF | AC | * | Air | <65000 | 13 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | T24 Std Table 110.2-H | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | * | VRF | AC | * | Air | <135000 | 0 | 0 | 0 | NA | 11.2 | 15.5 | 0 | 0 | 0 | T24 Std Table 110.2-G | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | * | VRF | AC | * | Air | <240000 | 0 | 0 | 0 | NA | 11 | 14.9 | 0 | 0 | 0 | T24 Std Table 110.2-G | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | * | VRF | AC | * | Air | >=240000 | 0 | 0 | 0 | NA | 10 | 13.9 | 0 | 0 | 0 | T24 Std Table 110.2-G | 0 | NA | 0 | 0 | NA | 0 | 0 | 0
|  | Compliance2022 | VRF | HP | * | Air | <65000 | 13 | 12.9 | 0 | NA | 0 | 0 | 0 | 0 | 0 | T24 Std Table 110.2-H | 0 | NA | 0 | 0 | NA | 7.7 | 6.5 | 0
|  | Compliance2025 | VRF | HP | * | Air | <65000 | 13 | 13.4 | 0 | T24 Std Table 110.2-G | 0 | 0 | 0 | 0 | 0 | T24 Std Table 110.2-H | 0 | NA | 0 | 0 | NA | 7.7 | 7.5 | 0
|  | Compliance2025 | VRF | HP | * | Air | <135000 | 0 | 0 | 0 | NA | 10.3 | 14.6 | 0 | 0 | 0 | T24 Std Table 110.2-G | 0 | NA | 3.3 | 2.25 | T24 Std Table 110.2-G | 0 | 0 | 0
|  | Compliance2025 | VRF | HP | * | Air | <240000 | 0 | 0 | 0 | NA | 9.9 | 13.9 | 0 | 0 | 0 | T24 Std Table 110.2-G | 0 | NA | 3.2 | 2.05 | T24 Std Table 110.2-G | 0 | 0 | 0
|  | Compliance2025 | VRF | HP | * | Air | >=240000 | 0 | 0 | 0 | NA | 9.1 | 12.7 | 0 | 0 | 0 | T24 Std Table 110.2-G | 0 | NA | 3.2 | 2.05 | T24 Std Table 110.2-G | 0 | 0 | 0
|  | * | VRF | HP | * | Air | <65000 | 13 | 0 | 0 | NA | 0 | 0 | 0 | 0 | 0 | T24 Std Table 110.2-H | 0 | NA | 0 | 0 | NA | 7.7 | 0 | 0
|  | * | VRF | HP | * | Air | <135000 | 0 | 0 | 0 | NA | 11 | 14.6 | 0 | 0 | 0 | T24 Std Table 110.2-H | 0 | NA | 3.3 | 2.25 | T24 Std Table 110.2-H | 0 | 0 | 0
|  | * | VRF | HP | * | Air | <240000 | 0 | 0 | 0 | NA | 10.6 | 13.9 | 0 | 0 | 0 | T24 Std Table 110.2-H | 0 | NA | 3.2 | 2.05 | T24 Std Table 110.2-H | 0 | 0 | 0
|  | * | VRF | HP | * | Air | >=240000 | 0 | 0 | 0 | NA | 9.5 | 12.7 | 0 | 0 | 0 | T24 Std Table 110.2-H | 0 | NA | 3.2 | 2.05 | T24 Std Table 110.2-H | 0 | 0 | 0
|  | Compliance2019 | VRF | HP | * | WaterSource | <65000 | 0 | 0 | 0 | NA | 12 | 15.8 | 0 | 0 | 0 | T24 Std Table 110.2-H | 0 | NA | 4.3 | 0 | T24 Std Table 110.2-H | 0 | 0 | 0
|  | Compliance2019 | VRF | HP | * | WaterSource | <135000 | 0 | 0 | 0 | NA | 12 | 15.8 | 0 | 0 | 0 | T24 Std Table 110.2-H | 0 | NA | 4.3 | 0 | T24 Std Table 110.2-H | 0 | 0 | 0
|  | Compliance2019 | VRF | HP | * | WaterSource | <240000 | 0 | 0 | 0 | NA | 10 | 13.8 | 0 | 0 | 0 | T24 Std Table 110.2-H | 0 | NA | 4 | 0 | T24 Std Table 110.2-H | 0 | 0 | 0
|  | Compliance2022 | VRF | HP | * | WaterSource | <65000 | 0 | 0 | 0 | NA | 12 | 16 | 0 | 0 | 0 | T24 Std Table 110.2-H | 0 | NA | 4.3 | 0 | T24 Std Table 110.2-H | 0 | 0 | 0
|  | Compliance2022 | VRF | HP | * | WaterSource | <135000 | 0 | 0 | 0 | NA | 12 | 16 | 0 | 0 | 0 | T24 Std Table 110.2-H | 0 | NA | 4.3 | 0 | T24 Std Table 110.2-H | 0 | 0 | 0
|  | Compliance2022 | VRF | HP | * | WaterSource | <240000 | 0 | 0 | 0 | NA | 10 | 14 | 0 | 0 | 0 | T24 Std Table 110.2-H | 0 | NA | 4 | 0 | T24 Std Table 110.2-H | 0 | 0 | 0
|  | Compliance2025 | VRF | HP | * | WaterSource | <65000 | 0 | 0 | 0 | NA | 12 | 16 | 0 | 0 | 0 | T24 Std Table 110.2-H | 0 | NA | 4.3 | 0 | T24 Std Table 110.2-H | 0 | 0 | 0
|  | Compliance2025 | VRF | HP | * | WaterSource | <135000 | 0 | 0 | 0 | NA | 12 | 16 | 0 | 0 | 0 | T24 Std Table 110.2-H | 0 | NA | 4.3 | 0 | T24 Std Table 110.2-H | 0 | 0 | 0
|  | Compliance2025 | VRF | HP | * | WaterSource | <240000 | 0 | 0 | 0 | NA | 10 | 14 | 0 | 0 | 0 | T24 Std Table 110.2-H | 0 | NA | 4 | 0 | T24 Std Table 110.2-H | 0 | 0 | 0
|  | * | VRF | HP | * | WaterSource | >=240000 | 0 | 0 | 0 | NA | 10 | 12 | 0 | 0 | 0 | T24 Std Table 110.2-H | 0 | NA | 3.9 | 0 | T24 Std Table 110.2-H | 0 | 0 | 0
|  | * | VRF | HP | * | GroundwaterSource | <135000 | 0 | 0 | 0 | NA | 16.2 | 0 | 0 | 0 | 0 | T24 Std Table 110.2-H | 0 | NA | 3.6 | 0 | T24 Std Table 110.2-H | 0 | 0 | 0
|  | * | VRF | HP | * | GroundwaterSource | >=135000 | 0 | 0 | 0 | NA | 13.8 | 0 | 0 | 0 | 0 | T24 Std Table 110.2-H | 0 | NA | 3.3 | 0 | T24 Std Table 110.2-H | 0 | 0 | 0
|  | * | VRF | HP | * | GroundSource | <135000 | 0 | 0 | 0 | NA | 13.4 | 0 | 0 | 0 | 0 | T24 Std Table 110.2-H | 0 | NA | 3.1 | 0 | T24 Std Table 110.2-H | 0 | 0 | 0
|  | * | VRF | HP | * | GroundSource | >=135000 | 0 | 0 | 0 | NA | 11 | 0 | 0 | 0 | 0 | T24 Std Table 110.2-H | 0 | NA | 2.8 | 0 | T24 Std Table 110.2-H | 0 | 0 | 0
ENDTABLE
Note on O33: David Reddy: For Split 1 phase with SEER2 < 15.2
Note on P33: David Reddy: For Split 1 phase with SEER2 >= 15.2
Note on Q33: David Reddy: Not used, coded into rules
Note on J74: David Reddy: Federal SEER2 not yet defined. ASHRAE 90.1-2019 is 13.4, but that is more stringent than federal
Note on K74: David Reddy: Use same value as packaged per email from Abram on 10/12
Note on J83: David Reddy: Federal SEER2 not yet defined. ASHRAE 90.1-2019 is 13.4, but that is more stringent than federal
Note on K83: David Reddy: Use same value as packaged per email from Abram on 10/12
Note on Z107: David Reddy: Use same value as packaged per email from Abram on 10/12
Note on Z113: David Reddy: Use same value as packaged per email from Abram on 10/12

## UnitaryAC-HPMinEffReq_T24N_2016 (hidden)
; | CEC 2013 Nonresidential ACM Ruleset
;
; | TABLE NAME:
; |  | UnitaryACHPMinEffReq
;
; | MODIFICATION HISTORY:
; |  | Date | Name | Purpose
; |  | 2013-08-25 | D. Reddy | Initial ruleset setup
; |  | 2015-07-21 | D. Reddy | Modify to support 2016 (and future) efficiency requirements based on Proj:StdsVersion
;
; | STANDARDS/ACM REFERENCE(S):
; |  | TABLE 110.2-A - ELECTRICALLY OPERATED UNITARY AIR CONDITIONERS AND CONDENSING UNITS – MINIMUM EFFICIENCY REQUIREMENTS
; |  | TABLE 110.2-B - UNITARY AND APPLIED HEAT PUMPS, MINIMUM EFFICIENCY REQUIREMENTS
;
; | NOTES:
; |  | Adjustments to EER for systems with a heating section other than electric resistance heat performed in rules
; |  | HP COP requirement specified at 47F db/43f wb outdoor air rating point
;
; | SYNTAX EXAMPLES:
; |  | UnitaryACHPMinEffReq:EER(StandardsVersion=Proj:StdsVersion,Category = "AC", SubCategory = "CRAC", CondenserType = "Air", SizeCategory = 80000)
;
; #################################### Start of Table ####################################
TABLE UnitaryACHPMinEffReq
|  | StandardsVersion | Category | SubCategory | CondenserType | SizeCategory | EER | IEER | EERSource | COP47 | COP17 | COPSource
|  | * | AC | Split1Phase | Air | <45000 | 12.2 | NA | Appl Std Table C-2 | NA | NA | NA
|  | * | AC | Split1Phase | Air | <65000 | 11.7 | NA | Appl Std Table C-2 | NA | NA | NA
|  | * | AC | Packaged1Phase | Air | <65000 | 11 | NA | Appl Std Table C-2 | NA | NA | NA
|  | * | AC | * | Air | <65000 | NA | NA | Appl Std Table C-2 | NA | NA | NA
|  | Compliance2016 | AC | * | Air | <135000 | 11.2 | 12.9 | T24 Std Table 110.2-A | NA | NA | NA
|  | * | AC | * | Air | <135000 | 11.2 | 11.4 | T24 Std Table 110.2-A | NA | NA | NA
|  | Compliance2016 | AC | * | Air | <240000 | 11 | 12.4 | T24 Std Table 110.2-A | NA | NA | NA
|  | * | AC | * | Air | <240000 | 11 | 11.2 | T24 Std Table 110.2-A | NA | NA | NA
|  | Compliance2016 | AC | * | Air | <760000 | 10 | 11.6 | T24 Std Table 110.2-A | NA | NA | NA
|  | * | AC | * | Air | <760000 | 10 | 10.1 | T24 Std Table 110.2-A | NA | NA | NA
|  | Compliance2016 | AC | * | Air | >=760000 | 9.7 | 11.2 | T24 Std Table 110.2-A | NA | NA | NA
|  | * | AC | * | Air | >=760000 | 9.7 | 9.8 | T24 Std Table 110.2-A | NA | NA | NA
|  | * | AC | * | WaterSource | <17000 | 12.1 | NA | Appl Std Table C-5 | NA | NA | NA
|  | * | AC | * | WaterSource | <65000 | 12.1 | NA | Appl Std Table C-5 | NA | NA | NA
|  | Compliance2016 | AC | * | WaterSource | <135000 | 12.1 | 13.9 | T24 Std Table 110.2-A | NA | NA | NA
|  | * | AC | * | WaterSource | <135000 | 12.1 | 12.3 | T24 Std Table 110.2-A | NA | NA | NA
|  | Compliance2016 | AC | * | WaterSource | <240000 | 12.5 | 13.9 | T24 Std Table 110.2-A | NA | NA | NA
|  | * | AC | * | WaterSource | <240000 | 12.5 | 12.5 | T24 Std Table 110.2-A | NA | NA | NA
|  | Compliance2016 | AC | * | WaterSource | <760000 | 12.4 | 13.6 | T24 Std Table 110.2-A | NA | NA | NA
|  | * | AC | * | WaterSource | <760000 | 12.4 | 12.6 | T24 Std Table 110.2-A | NA | NA | NA
|  | Compliance2016 | AC | * | WaterSource | >=760000 | 12.2 | 13.5 | T24 Std Table 110.2-A | NA | NA | NA
|  | * | AC | * | WaterSource | >=760000 | 12.2 | 12.4 | T24 Std Table 110.2-A | NA | NA | NA
|  | * | AC | * | EvaporativelyCooled | <65000 | 12.1 | NA | Appl Std Table C-4 | NA | NA | NA
|  | * | AC | * | EvaporativelyCooled | <135000 | 12.1 | 12.3 | T24 Std Table 110.2-A | NA | NA | NA
|  | * | AC | * | EvaporativelyCooled | <240000 | 12 | 12.2 | T24 Std Table 110.2-A | NA | NA | NA
|  | * | AC | * | EvaporativelyCooled | <760000 | 11.9 | 12.1 | T24 Std Table 110.2-A | NA | NA | NA
|  | * | AC | * | EvaporativelyCooled | >=760000 | 11.7 | 11.9 | T24 Std Table 110.2-A | NA | NA | NA
|  | * | HP | * | Air | <65000 | NA | NA | Appl Std Table C-2 | NA | NA | Appl Std Table C-2
|  | Compliance2016 | HP | * | Air | <135000 | 11 | 12.2 | T24 Std Table 110.2-B | 3.3 | 2.25 | T24 Std Table 110.2-B
|  | * | HP | * | Air | <135000 | 11 | 11.2 | T24 Std Table 110.2-B | 3.3 | 2.25 | T24 Std Table 110.2-B
|  | Compliance2016 | HP | * | Air | <240000 | 10.6 | 11.6 | T24 Std Table 110.2-B | 3.2 | 2.05 | T24 Std Table 110.2-B
|  | * | HP | * | Air | <240000 | 10.6 | 10.7 | T24 Std Table 110.2-B | 3.2 | 2.05 | T24 Std Table 110.2-B
|  | Compliance2016 | HP | * | Air | >=240000 | 9.5 | 10.6 | T24 Std Table 110.2-B | 3.2 | 2.05 | T24 Std Table 110.2-B
|  | * | HP | * | Air | >=240000 | 9.5 | 9.6 | T24 Std Table 110.2-B | 3.2 | 2.05 | T24 Std Table 110.2-B
|  | * | HP | * | WaterSource | <17000 | 11.2 | NA | Appl Std Table C-4 | 4.2 | NA | Appl Std Table C-4
|  | * | HP | * | WaterSource | <65000 | 12 | NA | Appl Std Table C-4 | 4.2 | NA | Appl Std Table C-4
|  | Compliance2016 | HP | * | WaterSource | <135000 | 13 | NA | T24 Std Table 110.2-B | 4.3 | NA | T24 Std Table 110.2-B
|  | * | HP | * | WaterSource | <135000 | 12 | NA | T24 Std Table 110.2-B | 4.2 | NA | T24 Std Table 110.2-B
|  | Compliance2016 | HP | * | WaterSource | <240000 | 12.3 | NA | Appl Std Table C-4 | 2.9 | NA | Appl Std Table C-4
|  | * | HP | * | WaterSource | <240000 | 12.3 | NA | Appl Std Table C-4 | 2.9 | NA | Appl Std Table C-4
|  | * | HP | * | WaterSource | <760000 | 12.2 | NA | Appl Std Table C-4 | NA | NA | Appl Std Table C-4
|  | Compliance2016 | HP | * | GroundwaterSource | <135000 | 18 | NA | T24 Std Table 110.2-B | 3.7 | NA | T24 Std Table 110.2-B
|  | * | HP | * | GroundwaterSource | <135000 | 16.2 | NA | T24 Std Table 110.2-B | 3.6 | NA | T24 Std Table 110.2-B
|  | * | HP | * | GroundwaterSource | >=135000 | NA | NA | NA | NA | NA | NA
|  | Compliance2016 | HP | * | GroundSource | <135000 | 14.1 | NA | T24 Std Table 110.2-B | 3.2 | NA | T24 Std Table 110.2-B
|  | * | HP | * | GroundSource | <135000 | 13.4 | NA | T24 Std Table 110.2-B | 3.1 | NA | T24 Std Table 110.2-B
|  | * | HP | * | GroundSource | >=135000 | NA | NA | NA | NA | NA | NA
|  | * | AC | CRAC | Air | <65000 | 11 | NA | Appl Std Table C-9 | NA | NA | NA
|  | * | AC | CRAC | Air | <135000 | 10.4 | NA | Appl Std Table C-9 | NA | NA | NA
|  | * | AC | CRAC | Air | <240000 | 10.2 | NA | Appl Std Table C-9 | NA | NA | NA
|  | * | AC | CRAC | Air | >=240000 | 10.2 | NA | CBECC Default | NA | NA | NA
ENDTABLE

## UnitaryAC-HPMinEffReq_T24N_old (hidden)
; | T24 Nonresidential ACM Ruleset
;
; | TABLE NAME:
; |  | UnitaryACHPMinEffReq
;
; | MODIFICATION HISTORY:
; |  | Date | Purpose
; |  | 2019-06-19 | Incorporate 2022 records (copied from 2019) and revise table name removing '2019'
; |  | 2017-12-14 | Copy of 2016 table, modified for 2019 ruleset
; |  | 2019-08-04 | Update <65kBtu/hr table reference and add min EER reqs for Split1Phase HPs
; |  | 2020-08-27 | Updates for Ticket 3217 (Fix for WSHP). Change EER/COP 'NA' values to 0. Add values for VRF. Add notes column
; |  | 2022-02-15 | Update to 2022 standard
;
; | STANDARDS/ACM REFERENCE(S):
; |  | TABLE 110.2-A - ELECTRICALLY OPERATED UNITARY AIR CONDITIONERS AND CONDENSING UNITS – MINIMUM EFFICIENCY REQUIREMENTS
; |  | TABLE 110.2-B - UNITARY AND APPLIED HEAT PUMPS - MINIMUM EFFICIENCY REQUIREMENTS
; |  | TABLE 110.2-E - PACKAGED TERMINAL AIR CONDITIONER AND PACKAGED TERMINAL HEAT PUMP - MINIMUM EFFICIENCY REQUIREMENTS
; |  | T20 Appliance Efficiency Standards
;
; | NOTES:
; |  | Adjustments to EER for systems with a heating section other than electric resistance heat performed in rules
; |  | HP COP requirement specified at 47F db/43f wb outdoor air rating point
; |  | Zero values indicate there is no requirement
;
; | SYNTAX EXAMPLES:
; |  | UnitaryACHPMinEffReq:EER(StandardsVersion=Proj:StdsVersion,Category = "AC", SubCategory = "CRAC", CondenserType = "Air", SizeCategory = 80000)
;
; #################################### Start of Table ####################################
TABLE UnitaryACHPMinEffReq
|  | StandardsVersion | Category | SubCategory | CondenserType | SizeCategory | EER | IEER | EERSource | COP47 | COP17 | COPSource | Notes
|  | Compliance2022 | SPVAC | * | Air | <65000 | 11 | 0 | T24 Std Table 110.2-E | 0 | 0 | NA
|  | Compliance2019 | SPVAC | * | Air | <65000 | 11 | 0 | T24 Std Table 110.2-E | 0 | 0 | NA
|  | * | SPVAC | * | Air | <65000 | 10 | 0 | T24 Std Table 110.2-E | 0 | 0 | NA
|  | * | SPVAC | * | Air | * | 10 | 0 | T24 Std Table 110.2-E | 0 | 0 | NA
|  | * | AC | Split1Phase | Air | <45000 | 12.2 | 0 | Appl Std Table C-3 | 0 | 0 | NA
|  | * | AC | Split1Phase | Air | <65000 | 11.7 | 0 | Appl Std Table C-3 | 0 | 0 | NA
|  | * | AC | Packaged1Phase | Air | <65000 | 11 | 0 | Appl Std Table C-3 | 0 | 0 | NA
|  | * | AC | * | Air | <65000 | 0 | 0 | NA | 0 | 0 | NA | SEER req. covered by separate rule
|  | Compliance2022 | AC | * | Air | <135000 | 11.2 | 14.8 | T24 Std Table 110.2-A | 0 | 0 | NA
|  | Compliance2019 | AC | * | Air | <135000 | 11.2 | 12.9 | T24 Std Table 110.2-A | 0 | 0 | NA
|  | Compliance2022 | AC | * | Air | <240000 | 11 | 14.2 | T24 Std Table 110.2-A | 0 | 0 | NA
|  | Compliance2019 | AC | * | Air | <240000 | 11 | 12.4 | T24 Std Table 110.2-A | 0 | 0 | NA
|  | Compliance2022 | AC | * | Air | <760000 | 10 | 13.2 | T24 Std Table 110.2-A | 0 | 0 | NA
|  | Compliance2019 | AC | * | Air | <760000 | 10 | 11.6 | T24 Std Table 110.2-A | 0 | 0 | NA
|  | Compliance2022 | AC | * | Air | >=760000 | 9.7 | 12.5 | T24 Std Table 110.2-A | 0 | 0 | NA
|  | Compliance2019 | AC | * | Air | >=760000 | 9.7 | 11.2 | T24 Std Table 110.2-A | 0 | 0 | NA
|  | * | AC | * | WaterSource | <17000 | 12.1 | 0 | Appl Std Table C-5 | 0 | 0 | NA
|  | * | AC | * | WaterSource | <65000 | 12.1 | 0 | Appl Std Table C-5 | 0 | 0 | NA
|  | * | AC | * | WaterSource | <135000 | 12.1 | 13.9 | T24 Std Table 110.2-A | 0 | 0 | NA
|  | * | AC | * | WaterSource | <240000 | 12.5 | 13.9 | T24 Std Table 110.2-A | 0 | 0 | NA
|  | * | AC | * | WaterSource | <760000 | 12.4 | 13.6 | T24 Std Table 110.2-A | 0 | 0 | NA
|  | * | AC | * | WaterSource | >=760000 | 12.2 | 13.5 | T24 Std Table 110.2-A | 0 | 0 | NA
|  | * | AC | * | EvaporativelyCooled | <65000 | 12.1 | 0 | Appl Std Table C-4 | 0 | 0 | NA
|  | * | AC | * | EvaporativelyCooled | <135000 | 12.1 | 12.3 | T24 Std Table 110.2-A | 0 | 0 | NA
|  | * | AC | * | EvaporativelyCooled | <240000 | 12 | 12.2 | T24 Std Table 110.2-A | 0 | 0 | NA
|  | * | AC | * | EvaporativelyCooled | <760000 | 11.9 | 12.1 | T24 Std Table 110.2-A | 0 | 0 | NA
|  | * | AC | * | EvaporativelyCooled | >=760000 | 11.7 | 11.9 | T24 Std Table 110.2-A | 0 | 0 | NA
|  | Compliance2022 | SPVHP | * | Air | <65000 | 11 | 0 | T24 Std Table 110.2-E | 3.3 | 0 | T24 Std Table 110.2-E | No min COP at 17F
|  | Compliance2019 | SPVHP | * | Air | <65000 | 11 | 0 | T24 Std Table 110.2-E | 3.3 | 0 | T24 Std Table 110.2-E | No min COP at 17F
|  | * | SPVHP | * | Air | <65000 | 10 | 0 | T24 Std Table 110.2-E | 3 | 0 | T24 Std Table 110.2-E | No min COP at 17F
|  | * | SPVHP | * | Air | * | 10 | 0 | T24 Std Table 110.2-E | 3 | 0 | T24 Std Table 110.2-E | No min COP at 17F
|  | * | HP | Split1Phase | Air | <45000 | 0 | 0 | T20 Std Table C-3 | 0 | 0 | NA | SEER/HSPF req. covered by separate rule | https://govt.westlaw.com/calregs/Document/IC95DA848BDAD489294F06754177B0C50?viewType=FullText&originationContext=documenttoc&transitionType=CategoryPageItem&contextData=(sc.Default)&bhcp=1
|  | * | HP | Split1Phase | Air | <65000 | 0 | 0 | T20 Std Table C-3 | 0 | 0 | NA | SEER/HSPF req. covered by separate rule | https://govt.westlaw.com/calregs/Document/IC95DA848BDAD489294F06754177B0C50?viewType=FullText&originationContext=documenttoc&transitionType=CategoryPageItem&contextData=(sc.Default)&bhcp=1
|  | * | HP | * | Air | <65000 | 0 | 0 | NA | 0 | 0 | NA | SEER/HSPF req. covered by separate rule
|  | Compliance2022 | HP | * | Air | <135000 | 11 | 14.1 | T24 Std Table 110.2-B | 3.4 | 2.25 | T24 Std Table 110.2-B
|  | Compliance2019 | HP | * | Air | <135000 | 11 | 12.2 | T24 Std Table 110.2-B | 3.3 | 2.25 | T24 Std Table 110.2-B
|  | Compliance2022 | HP | * | Air | <240000 | 10.6 | 13.5 | T24 Std Table 110.2-B | 3.3 | 2.05 | T24 Std Table 110.2-B
|  | Compliance2019 | HP | * | Air | <240000 | 10.6 | 11.6 | T24 Std Table 110.2-B | 3.2 | 2.05 | T24 Std Table 110.2-B
|  | Compliance2022 | HP | * | Air | >=240000 | 9.5 | 12.5 | T24 Std Table 110.2-B | 3.3 | 2.05 | T24 Std Table 110.2-B
|  | Compliance2019 | HP | * | Air | >=240000 | 9.5 | 10.6 | T24 Std Table 110.2-B | 3.2 | 2.05 | T24 Std Table 110.2-B
|  | * | HP | * | WaterSource | <17000 | 11.2 | 0 | Appl Std Table C-4 | 4.2 | 0 | Appl Std Table C-4
|  | * | HP | * | WaterSource | <65000 | 12 | 0 | Appl Std Table C-4 | 4.2 | 0 | Appl Std Table C-4
|  | * | HP | * | WaterSource | <135000 | 13 | 0 | T24 Std Table 110.2-B | 4.3 | 0 | T24 Std Table 110.2-B
|  | * | HP | * | WaterSource | <240000 | 12.3 | 0 | Appl Std Table C-4 | 2.9 | 0 | Appl Std Table C-4
|  | * | HP | * | WaterSource | <760000 | 12.2 | 0 | Appl Std Table C-4 | 0 | 0 | Appl Std Table C-4
|  | * | HP | * | WaterSource | >=760000 | 0 | 0 | NA | 0 | 0 | NA | No min eff req
|  | * | HP | * | GroundwaterSource | <135000 | 18 | 0 | T24 Std Table 110.2-B | 3.7 | 0 | T24 Std Table 110.2-B
|  | * | HP | * | GroundwaterSource | >=135000 | 0 | 0 | NA | 0 | 0 | NA
|  | * | HP | * | GroundSource | <135000 | 14.1 | 0 | T24 Std Table 110.2-B | 3.2 | 0 | T24 Std Table 110.2-B
|  | * | HP | * | GroundSource | >=135000 | 0 | 0 | NA | 0 | 0 | NA | No min eff req
|  | * | AC | CRAC | Air | <65000 | 11 | 0 | Appl Std Table C-9 | 0 | 0 | NA
|  | * | AC | CRAC | Air | <135000 | 10.4 | 0 | Appl Std Table C-9 | 0 | 0 | NA
|  | * | AC | CRAC | Air | <240000 | 10.2 | 0 | Appl Std Table C-9 | 0 | 0 | NA
|  | * | AC | CRAC | Air | >=240000 | 10.2 | 0 | CBECC Default | 0 | 0 | NA
|  | * | VRF | AC | Air | <65000 | 0 | 0 | T24 Std Table 110.2-H | 0 | 0 | NA | SEER req. covered by separate rule
|  | * | VRF | AC | Air | <135000 | 11.2 | 0 | T24 Std Table 110.2-H | 0 | 0 | NA
|  | * | VRF | AC | Air | <240000 | 11 | 0 | T24 Std Table 110.2-H | 0 | 0 | NA
|  | * | VRF | AC | Air | >=240000 | 10 | 0 | T24 Std Table 110.2-H | 0 | 0 | NA
|  | * | VRF | HP | Air | <65000 | 0 | 0 | T24 Std Table 110.2-I | 0 | 0 | NA | SEER/HSPF req. covered by separate rule
|  | * | VRF | HP | Air | <135000 | 11 | 14.6 | T24 Std Table 110.2-I | 3.3 | 2.25 | T24 Std Table 110.2-I
|  | * | VRF | HP | Air | <240000 | 10.6 | 13.9 | T24 Std Table 110.2-I | 3.2 | 2.05 | T24 Std Table 110.2-I
|  | * | VRF | HP | Air | >=240000 | 9.5 | 12.7 | T24 Std Table 110.2-I | 3.2 | 2.05 | T24 Std Table 110.2-I
|  | Compliance2022 | VRF | HP | WaterSource | <65000 | 12 | 16 | T24 Std Table 110.2-I | 4.3 | 0 | T24 Std Table 110.2-I
|  | Compliance2019 | VRF | HP | WaterSource | <65000 | 12 | 15.8 | T24 Std Table 110.2-I | 4.3 | 0 | T24 Std Table 110.2-I
|  | Compliance2022 | VRF | HP | WaterSource | <135000 | 12 | 16 | T24 Std Table 110.2-I | 4.3 | 0 | T24 Std Table 110.2-I
|  | Compliance2019 | VRF | HP | WaterSource | <135000 | 12 | 15.8 | T24 Std Table 110.2-I | 4.3 | 0 | T24 Std Table 110.2-I
|  | Compliance2022 | VRF | HP | WaterSource | <240000 | 10 | 14 | T24 Std Table 110.2-I | 4 | 0 | T24 Std Table 110.2-I
|  | Compliance2019 | VRF | HP | WaterSource | <240000 | 10 | 13.8 | T24 Std Table 110.2-I | 4 | 0 | T24 Std Table 110.2-I
|  | * | VRF | HP | WaterSource | >=240000 | 10 | 12 | T24 Std Table 110.2-I | 3.9 | 0 | T24 Std Table 110.2-I
|  | * | VRF | HP | GroundwaterSource | <135000 | 16.2 | 0 | T24 Std Table 110.2-I | 3.6 | 0 | T24 Std Table 110.2-I
|  | * | VRF | HP | GroundwaterSource | >=135000 | 13.8 | 0 | T24 Std Table 110.2-I | 3.3 | 0 | T24 Std Table 110.2-I
|  | * | VRF | HP | GroundSource | <135000 | 13.4 | 0 | T24 Std Table 110.2-I | 3.1 | 0 | T24 Std Table 110.2-I
|  | * | VRF | HP | GroundSource | >=135000 | 11 | 0 | T24 Std Table 110.2-I | 2.8 | 0 | T24 Std Table 110.2-I
ENDTABLE